## Nodes
Node | Voltage (Derived) | Sheet_Name | Relevant TO | latitude | longitude | Minor Flop Zone | Major Flop Zone | DESNZ T-Zone | User Defined Zone | Type | Indoor/Outdoor | Site Name
ABBA1- | 132 | B-2-1a | SHET | [8 empty] | ABERDEEN BAY WINDFARM
ABED1- | 132 | B-2-2a | SHET | [8 empty] | ABERARDER ONSHORE WIND FARM
ABHA11 | 132 | B-3-1c, B-4-1c | NGET | 50.4717 | -3.7309 | F6 | F | T9 |  | Teed Transformers | Outdoor | ABHAM
ABHA12 | 132 | B-3-1c, B-4-1c | NGET | 50.4717 | -3.7309 | F6 | F | T9 |  | Teed Transformers | Outdoor | ABHAM
ABHA4A | 400 | B-2-1c, B-3-1c | NGET | 50.4717 | -3.7309 | F6 | F | T9 |  | Teed Transformers | Outdoor | ABHAM
ABHA4B | 400 | B-2-1c, B-3-1c | NGET | 50.4717 | -3.7309 | F6 | F | T9 |  | Teed Transformers | Outdoor | ABHAM
ABNE1Q | 132 | B-2-1a, B-3-1a | SHET | 56.34 | -3.297 | T4 | T | T1 |  |  |  | ABERNETHY
ABNE1R | 132 | B-2-1a, B-3-1a | SHET | 56.34 | -3.297 | T4 | T | T1 |  |  |  | ABERNETHY
ABNE3- | 33 | B-3-1a | SHET | 56.34 | -3.297 | T4 | T | T1 |  |  |  | ABERNETHY
ABTH11 | 132 | B-3-1c, B-4-1c | NGET | 51.3883 | -3.4032 | H2 | H | T8 |  | Double busbar | Indoor | ABERTHAW
ABTH12 | 132 | B-3-1c | NGET | 51.3883 | -3.4032 | H2 | H | T8 |  | Double busbar | Indoor | ABERTHAW
ABTH13 | 132 | B-3-1c | NGET | 51.3883 | -3.4032 | H2 | H | T8 |  | Double busbar | Indoor | ABERTHAW
ABTH21 | 275 | B-2-1c, B-3-1c | NGET | 51.3883 | -3.4032 | H2 | H | T8 |  | Double busbar | Indoor | ABERTHAW
ACHE1- | 132 | B-2-2a, B-3-2a | SHET | [8 empty] | ACHANY EXTENSION
ACHE3- | 33 | B-3-2a | SHET | [8 empty] | ACHANY EXTENSION
AIGN1- | 132 | B-2-2a, B-3-2a | SHET | 57.4287 | -4.5772 |  |  | T1 |  |  |  | AIGAS NORTH
AIGN1A | 132 | B-2-2a | SHET | 57.4287 | -4.5772 |  |  | T1 |  |  |  | AIGAS NORTH
AIGN5- | 11 | B-3-2a | SHET | 57.4287 | -4.5772 |  |  | T1 |  |  |  | AIGAS NORTH
AIKE3A | 33 | B-3-1b | SPT | 55.9085 | -2.4867 |  |  | T2 |  |  |  | AIKENGALL
AIKE3B | 33 | B-3-1b | SPT | 55.9085 | -2.4867 |  |  | T2 |  |  |  | AIKENGALL
ALDW21 | 275 | B-2-1c, B-3-1c | NGET | 53.4455 | -1.3206 | P3 | P | T4 |  | Four Switch Mesh | Outdoor | ALDWARKE
ALDW31 | 33 | B-3-1c | NGET | 53.4455 | -1.3206 | P3 | P | T4 |  | Four Switch Mesh | Outdoor | ALDWARKE
ALDW32 | 33 | B-3-1c | NGET | 53.4455 | -1.3206 | P3 | P | T4 |  | Four Switch Mesh | Outdoor | ALDWARKE
ALNE1Q | 132 | B-2-1a, B-3-1a | SHET | 57.7082 | -4.2754 | T5 | T | T1 |  |  |  | ALNESS GSP
ALNE1R | 132 | B-2-1a, B-3-1a | SHET | 57.7082 | -4.2754 | T5 | T | T1 |  |  |  | ALNESS GSP
ALNE3J | 33 | B-3-1a | SHET | 57.7082 | -4.2754 | T5 | T | T1 |  |  |  | ALNESS GSP
ALST31 | 33 | B-3-1c | NGET | 51.547 | -2.9786 | H2 | H | T8 |  |  |  | ALPHA STEEL
ALST32 | 33 | B-3-1c | NGET | 51.547 | -2.9786 | H2 | H | T8 |  |  |  | ALPHA STEEL
ALVE11 | 132 | B-3-2c, B-4-1c | NGET | 51.0059 | -4.1365 | F6 | F | T9 |  | Teed Transformers | Outdoor | ALVERDISCOTT
ALVE41 | 400 | B-2-2c, B-3-2c | NGET | 51.0059 | -4.1365 | F6 | F | T9 |  | Teed Transformers | Outdoor | ALVERDISCOTT
ALVE4A | 400 | B-2-2c | NGET | 51.0059 | -4.1365 | F6 | F | T9 |  | Teed Transformers | Outdoor | ALVERDISCOTT
ALYT2A | 275 | B-2-1a, B-3-2a | SHET | 56.609 | -3.1651 |  |  | T1 |  |  |  | ALYTH
ALYT2B | 275 | B-2-1a, B-3-2a | SHET | 56.609 | -3.1651 |  |  | T1 |  |  |  | ALYTH
ALYT4J | 400 | B-2-2a, B-3-2a, B-4-2a | SHET | 56.609 | -3.1651 |  |  | T1 |  |  |  | ALYTH
ALYT4K | 400 | B-2-2a, B-3-2a | SHET | 56.609 | -3.1651 |  |  | T1 |  |  |  | ALYTH
AMEM11 | 132 | B-3-1c | NGET | 51.6652 | -0.65634 | A6 | A | T11 |  | Double busbar | Outdoor | AMERSHAM MAIN
AMEM4A | 400 | B-2-1c, B-2-2c, B-3-1c | NGET | 51.6652 | -0.65634 | A6 | A | T11 |  | Double busbar | Outdoor | AMERSHAM MAIN
AMEM4B | 400 | B-2-1c, B-2-2c, B-3-1c | NGET | 51.6652 | -0.65634 | A6 | A | T11 |  | Double busbar | Outdoor | AMERSHAM MAIN
AMUL1E | 132 | B-2-1a | SHET | [8 empty] | AMULREE
AMUL1F | 132 | B-2-1a | SHET | [8 empty] | AMULREE
AMUL1G | 132 | B-2-1a | SHET | [8 empty] | AMULREE
AMUL1H | 132 | B-2-1a | SHET | [8 empty] | AMULREE
ANSN2- | 275 | B-2-2a, B-3-2a | SHET | 56.198 | -5.1456 |  |  | T1 |  |  |  | AN SUIDHE NORTH
ANSN3- | 33 | B-3-2a | SHET | 56.198 | -5.1456 |  |  | T1 |  |  |  | AN SUIDHE NORTH
ARBR1Q | 132 | B-2-1a, B-3-2a | SHET | 56.5642 | -2.6202 | T4 | T | T1 |  |  |  | ARBROATH
ARBR1R | 132 | B-2-1a, B-3-2a | SHET | 56.5642 | -2.6202 | T4 | T | T1 |  |  |  | ARBROATH
ARBR3- | 33 | B-3-2a | SHET | 56.5642 | -2.6202 | T4 | T | T1 |  |  |  | ARBROATH
ARCR2- | 275 | B-2-2b, B-3-2b, B-4-2b | SPT | 56.5144 | -3.0428 |  |  | T1 |  |  |  | ARECLEOCH REPOWERING
ARCR3A | 33 | B-3-2b | SPT | 56.5144 | -3.0428 |  |  | T1 |  |  |  | ARECLEOCH REPOWERING
ARCR3B | 33 | B-3-2b | SPT | 56.5144 | -3.0428 |  |  | T1 |  |  |  | ARECLEOCH REPOWERING
ARDK1- | 132 | B-2-1a, B-3-1a | SHET | 56.2772 | -4.9218 | T3 | T | T1 |  |  |  | ARDKINGLAS WIND
ARDK3K | 33 | B-3-1a | SHET | 56.2772 | -4.9218 | T3 | T | T1 |  |  |  | ARDKINGLAS WIND
AREC1- | 132 | B-2-1b, B-3-1b | SPT | 55.0843 | -4.851 |  |  | T2 |  |  |  | ARECLEOCH
AREC3- | 33 | B-2-1b, B-3-1b | SPT | 55.0843 | -4.851 |  |  | T2 |  |  |  | ARECLEOCH
AREC3A | 33 | B-3-1b | SPT | 55.0843 | -4.851 |  |  | T2 |  |  |  | ARECLEOCH
AREC3B | 33 | B-3-1b | SPT | 55.0843 | -4.851 |  |  | T2 |  |  |  | ARECLEOCH
AREX1- | 132 | B-2-2b, B-3-2b | SPT | 56.5144 | -3.0428 |  |  | T1 |  |  |  | ARECLEOCH EXTENSION
AREX1A | 132 | B-2-2b | SPT | 56.5144 | -3.0428 |  |  | T1 |  |  |  | ARECLEOCH EXTENSION
AREX3- | 33 | B-3-2b | SPT | 56.5144 | -3.0428 |  |  | T1 |  |  |  | ARECLEOCH EXTENSION
ARMA1- | 132 | B-2-2a | SHET | 55.8941 | -3.6966 |  |  | T2 |  |  |  | ARMADALE
ARMO1J | 132 | B-2-2a, B-3-1a | SHET | 57.5544 | -6.6447 | T1 | T | T1 |  |  |  | ARDMORE
ARMO3- | 33 | B-3-1a | SHET | 57.5544 | -6.6447 | T1 | T | T1 |  |  |  | ARDMORE
ASBS1- | 132 | B-3-2a | SHET | 56.609 | -3.1651 |  |  | T1 |  |  |  | ALYTH SOLAR AND BATTERY STORAGE
ASBS4B | 400 | B-2-2a, B-3-2a | SHET | 56.609 | -3.1651 |  |  | T1 |  |  |  | ALYTH SOLAR AND BATTERY STORAGE
AUCH2- | 275 | B-2-1b | SPT | 55.0707 | -4.9801 |  |  | T2 |  |  |  | AUCHENCROSH
AUCW1- | 132 | B-2-1b | SPT | 55.3422 | -4.6844 |  |  | T2 |  |  |  | AUCHENWYND
AXMI11 | 132 | B-3-1c | NGET | 50.7865 | -2.9246 | E1 | E | T9 |  | Single Switch Mesh | Outdoor | AXMINSTER
AXMI41 | 400 | B-2-1c, B-3-1c | NGET | 50.7865 | -2.9246 | E1 | E | T9 |  | Single Switch Mesh | Outdoor | AXMINSTER
AYR-2Q | 275 | B-2-2b, B-3-1b | SPT | 55.4575 | -4.5881 |  |  | T2 |  |  |  | AYR
AYR-2R | 275 | B-2-2b, B-3-1b | SPT | 55.4575 | -4.5881 |  |  | T2 |  |  |  | AYR
AYR-3- | 33 | B-3-1b | SPT | 55.4575 | -4.5881 |  |  | T2 |  |  |  | AYR
AYRS4- | 400 | B-2-2b | SPT | 55.4575 | -4.5881 |  |  | T2 |  |  |  | AYRSHIRE GRID COLLECTOR
BAGA1Q | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.9002 | -3.6734 | S5 | S | T2 |  |  |  | BATHGATE
BAGA1R | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.9002 | -3.6734 | S5 | S | T2 |  |  |  | BATHGATE
BAGA3- | 33 | B-3-1b | SPT | 55.9002 | -3.6734 | S5 | S | T2 |  |  |  | BATHGATE
BAGB21 | 275 | B-2-1c | NGET | 51.617 | -3.8325 | H1 | H | T8 |  | Double busbar | Indoor | BAGLAN BAY
BAGP2- | 275 | B-2-2a | SHET | 57.0854 | -2.3465 |  |  | T1 |  |  |  | BAILLIE GREENER GRID PARK
BAGP2J | 275 | B-2-2a | SHET | 57.0854 | -2.3465 |  |  | T1 |  |  |  | BAILLIE GREENER GRID PARK
BAGP2K | 275 | B-2-2a | SHET | 57.0854 | -2.3465 |  |  | T1 |  |  |  | BAILLIE GREENER GRID PARK
BAIN1Q | 132 | B-2-1b, B-3-1b | SPT | 56.0143 | -3.7688 | S5 | S | T2 |  |  |  | BAINSFORD
BAIN1R | 132 | B-2-1b, B-3-1b | SPT | 56.0143 | -3.7688 | S5 | S | T2 |  |  |  | BAINSFORD
BAIN3- | 33 | B-3-1b | SPT | 56.0143 | -3.7688 | S5 | S | T2 |  |  |  | BAINSFORD
BANN4J | 400 | B-2-2a, B-3-2a | SHET | [8 empty] | BANNISKIRK
BANN4K | 400 | B-2-2a, B-3-2a | SHET | [8 empty] | BANNISKIRK
BARK11 | 132 | B-3-1c | NGET | 51.5226 | 0.11536 | A1 | A | T11 |  | Double busbar | Indoor | BARKING
BARK21 | 275 | B-2-1c, B-3-1c | NGET | 51.5226 | 0.11536 | A1 | A | T11 |  | Double busbar | Indoor | BARKING
BARK22 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 51.5226 | 0.11536 | A1 | A | T11 |  | Double busbar | Indoor | BARKING
BARK41 | 400 | B-2-1c, B-2-2c, B-3-1c | NGET | 51.5226 | 0.11536 | A1 | A | T11 |  | Double busbar | Indoor | BARKING
BARW31 | 33 | B-3-1c | NGET | 51.5202 | 0.11548 | A1 | A | T11 |  |  |  | BARKING WEST
BARW32 | 33 | B-3-1c | NGET | 51.5202 | 0.11548 | A1 | A | T11 |  |  |  | BARKING WEST
BEAT4- | 400 | B-2-1a | SHET | [8 empty] | BEATRICE ONSHORE
BEAU1J | 132 | B-2-1a, B-2-2a, B-3-1a, B-3-2a, B-4-1a | SHET | 57.4699 | -4.49 | T1 | T | T1 |  |  |  | BEAULY
BEAU1K | 132 | B-2-1a, B-2-2a, B-3-1a, B-4-1a | SHET | 57.4699 | -4.49 | T1 | T | T1 |  |  |  | BEAULY
BEAU1L | 132 | B-2-1a | SHET | 57.4699 | -4.49 | T1 | T | T1 |  |  |  | BEAULY
BEAU1M | 132 | B-2-1a | SHET | 57.4699 | -4.49 | T1 | T | T1 |  |  |  | BEAULY
BEAU1N | 132 | B-2-1a | SHET | 57.4699 | -4.49 | T1 | T | T1 |  |  |  | BEAULY
BEAU1P | 132 | B-2-1a, B-3-1a | SHET | 57.4699 | -4.49 | T1 | T | T1 |  |  |  | BEAULY
BEAU1Q | 132 | B-2-1a, B-3-1a | SHET | 57.4699 | -4.49 | T1 | T | T1 |  |  |  | BEAULY
BEAU1R | 132 | B-2-1a | SHET | 57.4699 | -4.49 | T1 | T | T1 |  |  |  | BEAULY
BEAU1S | 132 | B-2-1a | SHET | 57.4699 | -4.49 | T1 | T | T1 |  |  |  | BEAULY
BEAU1T | 132 | B-2-1a | SHET | 57.4699 | -4.49 | T1 | T | T1 |  |  |  | BEAULY
BEAU2J | 275 | B-2-1a, B-2-2a, B-3-1a, B-3-2a, B-4-1a | SHET | 57.4699 | -4.49 | T1 | T | T1 |  |  |  | BEAULY
BEAU2K | 275 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.4699 | -4.49 | T1 | T | T1 |  |  |  | BEAULY
BEAU3- | 33 | B-3-1a | SHET | 57.4699 | -4.49 | T1 | T | T1 |  |  |  | BEAULY
BEAU3U | 33 | B-4-1a | SHET | 57.4699 | -4.49 | T1 | T | T1 |  |  |  | BEAULY
BEAU3V | 33 | B-4-1a | SHET | 57.4699 | -4.49 | T1 | T | T1 |  |  |  | BEAULY
BEAU4- | 400 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.4699 | -4.49 | T1 | T | T1 |  |  |  | BEAULY
BEDD11 | 132 | B-3-1c | NGET | 51.3726 | -0.12647 | A8 | A | T11 |  | Double busbar | Outdoor | BEDDINGTON
BEDD12 | 132 | B-3-1c | NGET | 51.3726 | -0.12647 | A8 | A | T11 |  | Double busbar | Outdoor | BEDDINGTON
BEDD21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 51.3726 | -0.12647 | A8 | A | T11 |  | Double busbar | Outdoor | BEDDINGTON
BEDD22 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 51.3726 | -0.12647 | A8 | A | T11 |  | Double busbar | Outdoor | BEDDINGTON
BEDD23 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 51.3726 | -0.12647 | A8 | A | T11 |  | Double busbar | Outdoor | BEDDINGTON
BEDD4A | 400 | B-2-1c, B-3-1c | NGET | 51.3726 | -0.12647 | A8 | A | T11 |  | Double busbar | Outdoor | BEDDINGTON
BEDD4B | 400 | B-2-1c, B-3-1c | NGET | 51.3726 | -0.12647 | A8 | A | T11 |  | Double busbar | Outdoor | BEDDINGTON
BEDT1A | 132 | B-3-1c | NGET | 51.373 | -0.12795 | A8 | A | T11 |  |  |  | BEDDINGTON TEE
BEDT1B | 132 | B-3-1c | NGET | 51.373 | -0.12795 | A8 | A | T11 |  |  |  | BEDDINGTON TEE
BEIN11 | 132 | B-2-1a, B-3-1a | SHET | 57.1539 | -4.8701 |  |  | T1 |  |  |  | BEINNEUN WIND FARM
BEIN31 | 33 | B-3-1a | SHET | 57.1539 | -4.8701 |  |  | T1 |  |  |  | BEINNEUN WIND FARM
BENB1- | 132 | B-2-2b, B-3-2b | SPT | [8 empty] | BENBRACK WIND FARM
BENB1T | 132 | B-2-2b | SPT | [8 empty] | BENBRACK WIND FARM
BENB3- | 33 | B-3-2b | SPT | [8 empty] | BENBRACK WIND FARM
BENR11 | 132 | B-3-2c | NGET | 51.4658 | -0.098387 | A4 | A | T11 |  |  |  | BENGEWORTH ROAD
BENR41 | 400 | B-2-2c, B-3-2c | NGET | 51.4658 | -0.098387 | A4 | A | T11 |  |  |  | BENGEWORTH ROAD
BERB2Q | 275 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.5041 | -3.6001 | T1 | T | T1 |  |  |  | BERRY BURN
BERB3- | 33 | B-3-1a | SHET | 57.5041 | -3.6001 | T1 | T | T1 |  |  |  | BERRY BURN
BERW1Q | 132 | B-2-1b, B-3-1b | SPT | 55.7777 | -2.0777 | S6 | S | T2 |  |  |  | BERWICK
BERW1R | 132 | B-2-1b, B-3-1b | SPT | 55.7777 | -2.0777 | S6 | S | T2 |  |  |  | BERWICK
BERW3- | 33 | B-3-1b | SPT | 55.7777 | -2.0777 | S6 | S | T2 |  |  |  | BERWICK
BESW11 | 132 | B-3-1c, B-4-1c | NGET | 52.3859 | -1.6155 | L3 | L | T5 |  | Four Switch Mesh | Outdoor | BERKSWELL
BESW12 | 132 | B-3-1c, B-4-1c | NGET | 52.3859 | -1.6155 | L3 | L | T5 |  | Four Switch Mesh | Outdoor | BERKSWELL
BESW21 | 275 | B-2-1c, B-3-1c | NGET | 52.3859 | -1.6155 | L3 | L | T5 |  | Four Switch Mesh | Outdoor | BERKSWELL
BEWF1- | 132 | B-2-2a, B-3-2a | SHET | [8 empty] | BEAW FIELD
BEWF3- | 33 | B-3-2a | SHET | [8 empty] | BEAW FIELD
BHLA11 | 132 | B-2-1a, B-3-1a | SHET | 57.2446 | -4.704 |  |  | T1 |  |  |  | BHLARAIDH WIND FARM
BHLA31 | 33 | B-3-1a | SHET | 57.2446 | -4.704 |  |  | T1 |  |  |  | BHLARAIDH WIND FARM
BICF11 | 132 | B-3-1c | NGET | 52.9308 | -0.22118 | K4 | K | T5 |  | Teed Transformers | Outdoor | BICKER FEN
BICF41 | 400 | B-2-1c, B-3-1c | NGET | 52.9308 | -0.22118 | K4 | K | T5 |  | Teed Transformers | Outdoor | BICKER FEN
BIGG11 | 132 | B-3-1c | NGET | 52.0814 | -0.26357 | J4 | J | T6 |  |  |  | BIGGLESWADE
BIGG41 | 400 | B-2-1c, B-3-1c | NGET | 52.0814 | -0.26357 | J4 | J | T6 |  |  |  | BIGGLESWADE
BIHI1Q | 132 | B-2-1a | SHET | [8 empty] | BIRKHILL
BIHI1R | 132 | B-2-1a | SHET | [8 empty] | BIRKHILL
BING4- | 400 | B-2-2a, B-3-2a | SHET | [8 empty] | BINGALLY
BIRK11 | 132 | B-3-1c | NGET | 53.3657 | -3.0627 | N3 | N | T4 |  | Four Switch Mesh | Outdoor | BIRKENHEAD
BIRK21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 53.3657 | -3.0627 | N3 | N | T4 |  | Four Switch Mesh | Outdoor | BIRKENHEAD
BISW11 | 132 | B-3-1c, B-4-1c | NGET | 52.3121 | -2.2417 | L2 | L | T5 |  | Four Switch Mesh | Outdoor | BISHOPS WOOD
BISW21 | 275 | B-2-1c, B-3-1c | NGET | 52.3121 | -2.2417 | L2 | L | T5 |  | Four Switch Mesh | Outdoor | BISHOPS WOOD
BLAH1- | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 57.5218 | -2.9515 |  |  | T1 |  |  |  | BLACKHILL
BLAH3A | 33 | B-3-1b | SPT | 57.5218 | -2.9515 |  |  | T1 |  |  |  | BLACKHILL
BLAH3B | 33 | B-2-2b, B-3-1b | SPT | 57.5218 | -2.9515 |  |  | T1 |  |  |  | BLACKHILL
BLBS3- | 33 | B-3-2a | SHET | 57.5251 | -2.9484 |  |  | T1 |  |  |  | BLACKHILLOCK BATTERY STORAGE
BLBS4- | 400 | B-3-2a | SHET | 57.5251 | -2.9484 |  |  | T1 |  |  |  | BLACKHILLOCK BATTERY STORAGE
BLCW1- | 132 | B-2-2b, B-3-1b | SPT | 55.1291 | -4.0572 |  |  | T2 |  |  |  | BLACKCRAIG
BLCW3- | 33 | B-2-2b, B-3-1b | SPT | 55.1291 | -4.0572 |  |  | T2 |  |  |  | BLACKCRAIG
BLEX1- | 132 | B-2-2a, B-3-2a | SHET | 57.2446 | -4.704 |  |  | T1 |  |  |  | BHLARAIDH EXTENSION
BLEX1A | 132 | B-2-2a | SHET | 57.2446 | -4.704 |  |  | T1 |  |  |  | BHLARAIDH EXTENSION
BLEX1B | 132 | B-2-2a | SHET | 57.2446 | -4.704 |  |  | T1 |  |  |  | BHLARAIDH EXTENSION
BLEX3- | 33 | B-3-2a | SHET | 57.2446 | -4.704 |  |  | T1 |  |  |  | BHLARAIDH EXTENSION
BLGH1- | 132 | B-2-2a | SHET | [8 empty] | BLARGHOUR
BLHI1J | 132 | B-2-1a, B-2-2a, B-3-1a, B-3-2a | SHET | 57.5251 | -2.9484 |  |  | T1 |  |  |  | BLACKHILLOCK
BLHI1K | 132 | B-2-1a, B-3-1a | SHET | 57.5251 | -2.9484 |  |  | T1 |  |  |  | BLACKHILLOCK
BLHI2A | 275 | B-2-2a, B-3-2a | SHET | 57.5251 | -2.9484 |  |  | T1 |  |  |  | BLACKHILLOCK
BLHI2B | 275 | B-2-2a, B-3-2a | SHET | 57.5251 | -2.9484 |  |  | T1 |  |  |  | BLACKHILLOCK
BLHI2J | 275 | B-2-1a, B-2-2a, B-3-1a, B-3-2a | SHET | 57.5251 | -2.9484 |  |  | T1 |  |  |  | BLACKHILLOCK
BLHI2K | 275 | B-2-1a, B-2-2a, B-3-1a, B-3-2a | SHET | 57.5251 | -2.9484 |  |  | T1 |  |  |  | BLACKHILLOCK
BLHI4- | 400 | B-2-1a, B-3-1a | SHET | 57.5251 | -2.9484 |  |  | T1 |  |  |  | BLACKHILLOCK
BLHI4R | 400 | B-2-1a | SHET | 57.5251 | -2.9484 |  |  | T1 |  |  |  | BLACKHILLOCK
BLKL1- | 132 | B-2-1b, B-3-1b | SPT | [8 empty] | BLACKLAW
BLKL3A | 33 | B-3-1b | SPT | [8 empty] | BLACKLAW
BLKL3B | 33 | B-3-1b | SPT | [8 empty] | BLACKLAW
BLKS3- | 33 | B-2-2b | SPT | 55.1291 | -4.0572 |  |  | T2 |  |  |  | BLACKCRAIG SOUTH
BLLX1- | 132 | B-2-1b, B-3-1b | SPT | 55.7926 | -3.7379 |  |  | T2 |  |  |  | BLACKLAW EXTENSION
BLLX3- | 33 | B-3-1b | SPT | 55.7926 | -3.7379 |  |  | T2 |  |  |  | BLACKLAW EXTENSION
BLYT1A | 132 | B-3-1c | NGET | 55.1412 | -1.5306 | Q6 | Q | T3 |  | Double busbar | Indoor | BLYTH
BLYT1B | 132 | B-3-1c | NGET | 55.1412 | -1.5306 | Q6 | Q | T3 |  | Double busbar | Indoor | BLYTH
BLYT21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 55.1412 | -1.5306 | Q6 | Q | T3 |  | Double busbar | Indoor | BLYTH
BLYT22 | 275 | B-2-1c | NGET | 55.1412 | -1.5306 | Q6 | Q | T3 |  | Double busbar | Indoor | BLYTH
BLYT23 | 275 | B-2-1c | NGET | 55.1412 | -1.5306 | Q6 | Q | T3 |  | Double busbar | Indoor | BLYTH
BLYT41 | 400 | B-2-1c, B-3-1c | NGET | 55.1412 | -1.5306 | Q6 | Q | T3 |  | Double busbar | Indoor | BLYTH
BLYT61 | 66 | B-3-1c | NGET | 55.1412 | -1.5306 | Q6 | Q | T3 |  | Double busbar | Indoor | BLYTH
BOAG1L | 132 | B-2-1a | SHET | 57.2541 | -3.7317 | T1 | T | T1 |  |  |  | BOAT OF GARTEN
BOAG1M | 132 | B-2-1a | SHET | 57.2541 | -3.7317 | T1 | T | T1 |  |  |  | BOAT OF GARTEN
BOAG1P | 132 | B-2-1a | SHET | 57.2541 | -3.7317 | T1 | T | T1 |  |  |  | BOAT OF GARTEN
BOAG1Q | 132 | B-2-1a, B-3-1a | SHET | 57.2541 | -3.7317 | T1 | T | T1 |  |  |  | BOAT OF GARTEN
BOAG1R | 132 | B-2-1a, B-3-1a | SHET | 57.2541 | -3.7317 | T1 | T | T1 |  |  |  | BOAT OF GARTEN
BOAG3- | 33 | B-3-1a | SHET | 57.2541 | -3.7317 | T1 | T | T1 |  |  |  | BOAT OF GARTEN
BODE41 | 400 | B-2-2c, B-3-1c | NGET | 53.2501 | -3.4761 | M6 | M | T4 |  | Double busbar | Outdoor | BODELWYDDAN
BOLN11 | 132 | B-3-1c, B-4-1c | NGET | 50.9752 | -0.23508 | B1 | B | T11 |  | Double busbar | Outdoor | BOLNEY
BOLN12 | 132 | B-3-1c, B-4-1c | NGET | 50.9752 | -0.23508 | B1 | B | T11 |  | Double busbar | Outdoor | BOLNEY
BOLN41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 50.9752 | -0.23508 | B1 | B | T11 |  | Double busbar | Outdoor | BOLNEY
BONB4- | 400 | B-2-1a, B-2-2b | SHET, SPT | 56.0078 | -3.8607 |  |  | T2 |  |  |  | BONNYBRIDGE BORDER NODE
BONB4A | 400 | B-2-2a, B-2-2b | SHET, SPT | 56.0078 | -3.8607 |  |  | T2 |  |  |  | BONNYBRIDGE BORDER NODE
BONN1- | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 56.0078 | -3.8607 | S5 | S | T2 |  |  |  | BONNYBRIDGE
BONN2A | 275 | B-2-1b, B-3-1b | SPT | 56.0078 | -3.8607 | S5 | S | T2 |  |  |  | BONNYBRIDGE
BONN2B | 275 | B-2-1b, B-3-1b | SPT | 56.0078 | -3.8607 | S5 | S | T2 |  |  |  | BONNYBRIDGE
BONN3- | 33 | B-3-1b | SPT | 56.0078 | -3.8607 | S5 | S | T2 |  |  |  | BONNYBRIDGE
BONN3U | 33 | B-4-1b | SPT | 56.0078 | -3.8607 | S5 | S | T2 |  |  |  | BONNYBRIDGE
BONN3V | 33 | B-4-1b | SPT | 56.0078 | -3.8607 | S5 | S | T2 |  |  |  | BONNYBRIDGE
BOTW11 | 132 | B-3-1c | NGET | 50.8845 | -1.2321 | B2 | B | T10 |  | Single Switch Mesh | Outdoor | BOTLEY WOOD
BOTW41 | 400 | B-2-1c, B-3-1c | NGET | 50.8845 | -1.2321 | B2 | B | T10 |  | Single Switch Mesh | Outdoor | BOTLEY WOOD
BPGR3J | 33 | B-3-1b | SPT | 51.5604 | -3.7546 |  |  | T8 |  |  |  | BP GRANGEMOUTH
BPGR3K | 33 | B-3-1b | SPT | 51.5604 | -3.7546 |  |  | T8 |  |  |  | BP GRANGEMOUTH
BRAI11 | 132 | B-3-1c | NGET | 51.8649 | 0.57634 | J8 | J | T6 |  | Teed Transformers | Outdoor | BRAINTREE
BRAI4A | 400 | B-2-1c, B-2-2c, B-3-1c | NGET | 51.8649 | 0.57634 | J8 | J | T6 |  | Teed Transformers | Outdoor | BRAINTREE
BRAI4B | 400 | B-2-1c, B-2-2c, B-3-1c | NGET | 51.8649 | 0.57634 | J8 | J | T6 |  | Teed Transformers | Outdoor | BRAINTREE
BRAP1- | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.8813 | -4.3815 | S6 | S | T2 |  |  |  | BRAEHEAD PARK
BRAP3- | 33 | B-3-1b | SPT | 55.8813 | -4.3815 | S6 | S | T2 |  |  |  | BRAEHEAD PARK
BRAW11 | 132 | B-3-1c, B-4-1c | NGET | 53.8105 | -1.8653 | P1 | P | T4 |  | Four Switch Mesh | Outdoor | BRADFORD WEST
BRAW12 | 132 | B-3-1c | NGET | 53.8105 | -1.8653 | P1 | P | T4 |  | Four Switch Mesh | Outdoor | BRADFORD WEST
BRAW21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 53.8105 | -1.8653 | P1 | P | T4 |  | Four Switch Mesh | Outdoor | BRADFORD WEST
BRAW4A | 400 | B-2-1c, B-3-1c | NGET | 53.8105 | -1.8653 | P1 | P | T4 |  | Four Switch Mesh | Outdoor | BRADFORD WEST
BRCW1A | 132 | B-3-2a | SHET | 56.2613 | -3.9471 |  |  | T1 |  |  |  | BRACO WEST
BRCW1B | 132 | B-3-2a | SHET | 56.2613 | -3.9471 |  |  | T1 |  |  |  | BRACO WEST
BRCW3- | 33 | B-3-2a | SHET | 56.2613 | -3.9471 |  |  | T1 |  |  |  | BRACO WEST
BREC1Q | 132 | B-2-1a, B-2-2a | SHET | 56.7401 | -2.6287 |  |  | T1 |  |  |  | BRECHIN
BREC1R | 132 | B-2-1a | SHET | 56.7401 | -2.6287 |  |  | T1 |  |  |  | BRECHIN
BRED11 | 132 | B-3-1c | NGET | 53.4145 | -2.1289 | N2 | N | T4 |  | Four Switch Mesh | Outdoor | BREDBURY
BRED21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 53.4145 | -2.1289 | N2 | N | T4 |  | Four Switch Mesh | Outdoor | BREDBURY
BREE1- | 132 | B-2-2b | SPT | [8 empty] | BREEZY HILL
BRFO11 | 132 | B-3-1c, B-4-1c | NGET | 52.0713 | 1.0621 | J5 | J | T7 |  | Double busbar | Outdoor | BRAMFORD
BRFO12 | 132 | B-3-1c | NGET | 52.0713 | 1.0621 | J5 | J | T7 |  | Double busbar | Outdoor | BRAMFORD
BRFO41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c, B-4-2c | NGET | 52.0713 | 1.0621 | J5 | J | T7 |  | Double busbar | Outdoor | BRAMFORD
BRID1Q | 132 | B-2-1a, B-3-1a | SHET | 56.7202 | -2.557 | T4 | T | T1 |  |  |  | BRIDGE OF DUN
BRID1R | 132 | B-2-1a, B-3-1a | SHET | 56.7202 | -2.557 | T4 | T | T1 |  |  |  | BRIDGE OF DUN
BRID3- | 33 | B-3-1a | SHET | 56.7202 | -2.557 | T4 | T | T1 |  |  |  | BRIDGE OF DUN
BRIM11 | 132 | B-3-1c, B-3-2c | NGET | 51.6635 | -0.02494 | A3 | A | T11 |  | Double busbar | Outdoor | BRIMSDOWN
BRIM2A | 275 | B-2-2c, B-3-1c | NGET | 51.6635 | -0.02494 | A3 | A | T11 |  | Double busbar | Outdoor | BRIMSDOWN
BRIM2B | 275 | B-2-2c, B-3-1c | NGET | 51.6635 | -0.02494 | A3 | A | T11 |  | Double busbar | Outdoor | BRIMSDOWN
BRIM4C | 400 | B-2-2c, B-3-2c | NGET | 51.6635 | -0.02494 | A3 | A | T11 |  | Double busbar | Outdoor | BRIMSDOWN
BRIM4D | 400 | B-2-2c, B-3-2c | NGET | 51.6635 | -0.02494 | A3 | A | T11 |  | Double busbar | Outdoor | BRIMSDOWN
BRIN21 | 275 | B-2-1c, B-3-1c | NGET | 53.4015 | -1.352 | P3 | P | T4 |  | Double busbar | Outdoor | BRINSWORTH
BRIN22 | 275 | B-2-1c, B-3-1c | NGET | 53.4015 | -1.352 | P3 | P | T4 |  | Double busbar | Outdoor | BRINSWORTH
BRIN41 | 400 | B-2-1c, B-2-2c, B-3-1c | NGET | 53.4015 | -1.352 | P3 | P | T4 |  | Double busbar | Outdoor | BRINSWORTH
BRLE11 | 132 | B-3-1c | NGET | 51.3361 | -1.0773 | B4 | B | T10 |  | Double busbar | Outdoor | BRAMLEY
BRLE12 | 132 | B-3-1c | NGET | 51.3361 | -1.0773 | B4 | B | T10 |  | Double busbar | Outdoor | BRAMLEY
BRLE13 | 132 | B-3-1c | NGET | 51.3361 | -1.0773 | B4 | B | T10 |  | Double busbar | Outdoor | BRAMLEY
BRLE14 | 132 | B-3-1c | NGET | 51.3361 | -1.0773 | B4 | B | T10 |  | Double busbar | Outdoor | BRAMLEY
BRLE1A | 132 | B-3-1c | NGET | 51.3361 | -1.0773 | B4 | B | T10 |  | Double busbar | Outdoor | BRAMLEY
BRLE1B | 132 | B-3-1c | NGET | 51.3361 | -1.0773 | B4 | B | T10 |  | Double busbar | Outdoor | BRAMLEY
BRLE41 | 400 | B-2-1c, B-2-2c, B-3-1c | NGET | 51.3361 | -1.0773 | B4 | B | T10 |  | Double busbar | Outdoor | BRAMLEY
BRNX4- | 400 | B-2-2b | SPT | 55.9485 | -2.4168 | S6 | S | T2 |  |  |  | BRANXTON
BRNX4A | 400 | B-2-2b | SPT | 55.9485 | -2.4168 | S6 | S | T2 |  |  |  | BRANXTON
BRNX4Q | 400 | B-2-2b | SPT | 55.9485 | -2.4168 | S6 | S | T2 |  |  |  | BRANXTON
BRNX4R | 400 | B-2-2b | SPT | 55.9485 | -2.4168 | S6 | S | T2 |  |  |  | BRANXTON
BROA1- | 132 | B-2-2a, B-3-2a | SHET | 53.8029 | -1.7526 | T1 | T | T1 |  |  |  | BROADFORD
BROA1A | 132 | B-2-2a, B-4-2a | SHET | 53.8029 | -1.7526 | T1 | T | T1 |  |  |  | BROADFORD
BROA1B | 132 | B-2-2a, B-4-2a | SHET | 53.8029 | -1.7526 | T1 | T | T1 |  |  |  | BROADFORD
BROA1C | 132 | B-2-2a | SHET | 53.8029 | -1.7526 | T1 | T | T1 |  |  |  | BROADFORD
BROA1D | 132 | B-2-2a | SHET | 53.8029 | -1.7526 | T1 | T | T1 |  |  |  | BROADFORD
BROA1J | 132 | B-2-2a | SHET | 53.8029 | -1.7526 | T1 | T | T1 |  |  |  | BROADFORD
BROA1K | 132 | B-2-2a | SHET | 53.8029 | -1.7526 | T1 | T | T1 |  |  |  | BROADFORD
BROA3- | 33 | B-3-2a | SHET | 53.8029 | -1.7526 | T1 | T | T1 |  |  |  | BROADFORD
BROC1- | 132 | B-2-2b | SPT | 51.9219 | -2.5903 |  |  | T5 |  |  |  | BROKEN CROSS
BROR1- | 132 | B-2-1a, B-3-1a | SHET | 58.0202 | -3.8755 | T5 | T | T1 |  |  |  | BRORA
BROR1Q | 132 | B-2-1a | SHET | 58.0202 | -3.8755 | T5 | T | T1 |  |  |  | BRORA
BROR3- | 33 | B-3-1a | SHET | 58.0202 | -3.8755 | T5 | T | T1 |  |  |  | BRORA
BROT1- | 132 | B-2-1b, B-2-2b | SPT | 51.9219 | -2.5903 |  |  | T5 |  |  |  | BROKEN CROSS TEE
BROX1Q | 132 | B-2-1b, B-3-1b | SPT | 55.9196 | -3.4545 | S6 | S | T2 |  |  |  | BROXBURN
BROX1R | 132 | B-2-1b, B-3-1b | SPT | 55.9196 | -3.4545 | S6 | S | T2 |  |  |  | BROXBURN
BROX3- | 33 | B-3-1b | SPT | 55.9196 | -3.4545 | S6 | S | T2 |  |  |  | BROXBURN
BRWA11 | 132 | B-3-1c, B-4-1c | NGET | 51.1173 | -2.969 | E7 | E | T9 |  | Teed Transformers | Outdoor | BRIDGWATER
BRWA41 | 400 | B-2-1c, B-3-1c | NGET | 51.1173 | -2.969 | E7 | E | T9 |  | Teed Transformers | Outdoor | BRIDGWATER
BRWA42 | 400 | B-2-1c, B-3-1c | NGET | 51.1173 | -2.969 | E7 | E | T9 |  | Teed Transformers | Outdoor | BRIDGWATER
BRWA4A | 400 | B-2-1c | NGET | 51.1173 | -2.969 | E7 | E | T9 |  | Teed Transformers | Outdoor | BRIDGWATER
BRWA4B | 400 | B-2-1c | NGET | 51.1173 | -2.969 | E7 | E | T9 |  | Teed Transformers | Outdoor | BRIDGWATER
BULL41 | 400 | B-2-1c | NGET | 51.7659 | 0.53743 | J8 | J | T11 |  |  |  | BULLS LODGE
BUMU1Q | 132 | B-2-1a, B-3-1a | SHET | 56.3969 | -3.4885 | T4 | T | T1 |  |  |  | BURGHMUIR
BUMU1R | 132 | B-2-1a, B-3-1a | SHET | 56.3969 | -3.4885 | T4 | T | T1 |  |  |  | BURGHMUIR
BUMU3- | 33 | B-3-1a | SHET | 56.3969 | -3.4885 | T4 | T | T1 |  |  |  | BURGHMUIR
BURW11 | 132 | B-3-1c | NGET | 52.2801 | 0.31212 | J7 | J | T6 |  | Four Switch Mesh | Outdoor | BURWELL MAIN
BURW41 | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 52.2801 | 0.31212 | J7 | J | T6 |  | Four Switch Mesh | Outdoor | BURWELL MAIN
BUSB2- | 275 | B-2-1b, B-2-2b | SPT | 55.7745 | -4.2638 |  |  | T2 |  |  |  | BUSBY
BUSH11 | 132 | B-3-1c, B-4-1c | NGET | 52.6362 | -2.1148 | L2 | L | T5 |  | Four Switch Mesh | Outdoor | BUSHBURY
BUSH21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 52.6362 | -2.1148 | L2 | L | T5 |  | Four Switch Mesh | Outdoor | BUSHBURY
BUST11 | 132 | B-3-1c | NGET | 52.5529 | -1.964 | L3 | L | T5 |  | Double busbar | Outdoor | BUSTLEHOLME
BUST21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 52.5529 | -1.964 | L3 | L | T5 |  | Double busbar | Outdoor | BUSTLEHOLME
BUST4A | 400 | B-2-1c, B-3-1c | NGET | 52.5529 | -1.964 | L3 | L | T5 |  | Double busbar | Outdoor | BUSTLEHOLME
BUST4B | 400 | B-2-1c, B-3-1c | NGET | 52.5529 | -1.964 | L3 | L | T5 |  | Double busbar | Outdoor | BUSTLEHOLME
CAAD1Q | 132 | B-2-2a, B-3-1a | SHET | 55.5903 | -5.5034 | T3 | T | T1 |  |  |  | CARRADALE
CAAD1R | 132 | B-2-1a, B-3-1a | SHET | 55.5903 | -5.5034 | T3 | T | T1 |  |  |  | CARRADALE
CAAD3- | 33 | B-3-1a | SHET | 55.5903 | -5.5034 | T3 | T | T1 |  |  |  | CARRADALE
CAAD3J | 33 | B-3-1a | SHET | 55.5903 | -5.5034 | T3 | T | T1 |  |  |  | CARRADALE
CAFA1Q | 132 | B-2-2b, B-3-1b | SPT | 55.1434 | -4.1896 | S6 | S | T2 |  |  |  | CARSFAD
CAFA5R | 11 | B-3-1b | SPT | 55.1434 | -4.1896 | S6 | S | T2 |  |  |  | CARSFAD
CAID2- | 275 | B-2-2a, B-3-2a | SHET | [8 empty] | CAIRN DUHIE WIND FARM
CAID3- | 33 | B-3-2a | SHET | [8 empty] | CAIRN DUHIE WIND FARM
CAIN2- | 275 | B-2-1a, B-3-1a | SHET | 57.4525 | -2.8497 |  |  | T1 |  |  |  | CAIRNFORD
CAIN3J | 33 | B-3-1a | SHET | 57.4525 | -2.8497 |  |  | T1 |  |  |  | CAIRNFORD
CAMA11 | 132 | B-2-1c | NGET | 51.4745 | -2.6103 | G5 | G | T8 |  |  |  | CAMBRIDGE ARMS
CAMA12 | 132 | B-2-1c | NGET | 51.4745 | -2.6103 | G5 | G | T8 |  |  |  | CAMBRIDGE ARMS
CAML61 | 66 | B-3-1c | NGET | 53.7295 | -1.0008 | P4 | P | T4 |  |  |  | CAMBLESFORTH
CANT13 | 132 | B-3-1c | NGET | 51.2923 | 1.0941 | C7 | C | T11 |  | Four Switch Mesh | Outdoor | CANTERBURY NORTH
CANT14 | 132 | B-3-1c | NGET | 51.2923 | 1.0941 | C7 | C | T11 |  | Four Switch Mesh | Outdoor | CANTERBURY NORTH
CANT41 | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 51.2923 | 1.0941 | C7 | C | T11 |  | Four Switch Mesh | Outdoor | CANTERBURY NORTH
CAPE11 | 132 | B-3-1c | NGET | 53.2688 | -2.9492 | N3 | N | T4 |  | Teed Transformers | Outdoor | CAPENHURST
CAPE1A | 132 | B-2-1c, B-3-1c | NGET | 53.2688 | -2.9492 | N3 | N | T4 |  | Teed Transformers | Outdoor | CAPENHURST
CAPE1B | 132 | B-2-1c, B-3-1c | NGET | 53.2688 | -2.9492 | N3 | N | T4 |  | Teed Transformers | Outdoor | CAPENHURST
CAPE21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 53.2688 | -2.9492 | N3 | N | T4 |  | Teed Transformers | Outdoor | CAPENHURST
CAPE4A | 400 | B-2-1c, B-3-1c | NGET | 53.2688 | -2.9492 | N3 | N | T4 |  | Teed Transformers | Outdoor | CAPENHURST
CAPE4B | 400 | B-2-1c, B-3-1c | NGET | 53.2688 | -2.9492 | N3 | N | T4 |  | Teed Transformers | Outdoor | CAPENHURST
CARE11 | 132 | B-3-1c | NGET | 51.4948 | -3.1454 | H2 | H | T8 |  | Single Switch Mesh | Outdoor | CARDIFF EAST
CARE21 | 275 | B-2-1c, B-3-1c | NGET | 51.4948 | -3.1454 | H2 | H | T8 |  | Single Switch Mesh | Outdoor | CARDIFF EAST
CARR11 | 132 | B-3-1c | NGET | 53.4363 | -2.4072 | N2 | N | T4 |  | Double busbar | Indoor | CARRINGTON
CARR12 | 132 | B-3-1c | NGET | 53.4363 | -2.4072 | N2 | N | T4 |  | Double busbar | Indoor | CARRINGTON
CARR21 | 275 | B-2-1c, B-3-1c | NGET | 53.4363 | -2.4072 | N2 | N | T4 |  | Double busbar | Indoor | CARRINGTON
CARR41 | 400 | B-2-1c, B-2-2c, B-3-1c | NGET | 53.4363 | -2.4072 | N2 | N | T4 |  | Double busbar | Indoor | CARRINGTON
CARR4A | 400 | B-2-2c, B-3-1c | NGET | 53.4363 | -2.4072 | N2 | N | T4 |  | Double busbar | Indoor | CARRINGTON
CARR4B | 400 | B-2-1c, B-3-1c | NGET | 53.4363 | -2.4072 | N2 | N | T4 |  | Double busbar | Indoor | CARRINGTON
CASS1Q | 132 | B-2-1a, B-3-1a | SHET | 58.1874 | -4.7297 | T5 | T | T1 |  |  |  | CASSLEY
CASS3- | 33 | B-3-1a | SHET | 58.1874 | -4.7297 | T5 | T | T1 |  |  |  | CASSLEY
CATY1Q | 132 | B-2-1b, B-3-1b | SPT | 55.858 | -4.197 | S6 | S | T2 |  |  |  | CARNTYNE
CATY1R | 132 | B-2-1b, B-3-1b | SPT | 55.858 | -4.197 | S6 | S | T2 |  |  |  | CARNTYNE
CATY3- | 33 | B-3-1b | SPT | 55.858 | -4.197 | S6 | S | T2 |  |  |  | CARNTYNE
CCSS1- | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.5824 | -3.9259 |  |  | T2 |  |  |  | CUMBERHEAD COLLECTOR
CCSS3- | 33 | B-2-2b, B-3-1b | SPT | 55.5824 | -3.9259 |  |  | T2 |  |  |  | CUMBERHEAD COLLECTOR
CEAN1Q | 132 | B-2-1a, B-3-1a | SHET | 57.1541 | -4.9369 | T1 | T | T1 |  |  |  | CEANNACROC
CEAN5- | 11 | B-3-1a | SHET | 57.1541 | -4.9369 | T1 | T | T1 |  |  |  | CEANNACROC
CELL11 | 132 | B-3-1c, B-4-1c | NGET | 53.0409 | -2.0826 | L5 | L | T5 |  | Double busbar | Outdoor | CELLARHEAD
CELL12 | 132 | B-3-1c, B-4-1c | NGET | 53.0409 | -2.0826 | L5 | L | T5 |  | Double busbar | Outdoor | CELLARHEAD
CELL41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 53.0409 | -2.0826 | L5 | L | T5 |  | Double busbar | Outdoor | CELLARHEAD
CELL42 | 400 | B-2-2c | NGET | 53.0409 | -2.0826 | L5 | L | T5 |  | Double busbar | Outdoor | CELLARHEAD
CELL43 | 400 | B-2-2c | NGET | 53.0409 | -2.0826 | L5 | L | T5 |  | Double busbar | Outdoor | CELLARHEAD
CHAP1- | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.0167 | -3.231 | S6 | S | T2 |  |  |  | CHAPELCROSS
CHAP3- | 33 | B-3-1b | SPT | 55.0167 | -3.231 | S6 | S | T2 |  |  |  | CHAPELCROSS
CHAR1- | 132 | B-2-1a, B-3-1a | SHET | 56.4732 | -3.0455 | T4 | T | T1 |  |  |  | CHARLESTON
CHAR1R | 132 | B-2-1a, B-3-1a | SHET | 56.4732 | -3.0455 | T4 | T | T1 |  |  |  | CHARLESTON
CHAR1S | 132 | B-2-1a, B-2-2a | SHET | 56.4732 | -3.0455 | T4 | T | T1 |  |  |  | CHARLESTON
CHAR1T | 132 | B-2-1a, B-2-2a | SHET | 56.4732 | -3.0455 | T4 | T | T1 |  |  |  | CHARLESTON
CHAR3- | 33 | B-3-1a | SHET | 56.4732 | -3.0455 | T4 | T | T1 |  |  |  | CHARLESTON
CHAS2Q | 275 | B-2-1b, B-3-1b | SPT | 51.1312 | -2.7535 | S6 | S | T2 |  |  |  | CHARLOTTE STREET
CHAS2R | 275 | B-2-1b, B-3-1b | SPT | 51.1312 | -2.7535 | S6 | S | T2 |  |  |  | CHARLOTTE STREET
CHAS3A | 33 | B-3-1b | SPT | 51.1312 | -2.7535 | S6 | S | T2 |  |  |  | CHARLOTTE STREET
CHAS3C | 33 | B-3-1b | SPT | 51.1312 | -2.7535 | S6 | S | T2 |  |  |  | CHARLOTTE STREET
CHIC11 | 132 | B-3-1c | NGET | 50.6246 | -2.4865 | E1 | E | T9 |  | Double busbar | Outdoor | CHICKERELL
CHIC41 | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 50.6246 | -2.4865 | E1 | E | T9 |  | Double busbar | Outdoor | CHICKERELL
CHIC4A | 400 | B-2-1c, B-4-1c | NGET | 50.6246 | -2.4865 | E1 | E | T9 |  | Double busbar | Outdoor | CHICKERELL
CHIL41 | 400 | B-2-1c | NGET | 50.8217 | -1.3286 | B2 | B | T10 |  |  |  | CHILLING
CHLS1- | 132 | B-2-2a | SHET | [8 empty] | CHLEANSAID
CHMO1- | 132 | B-2-2b | SPT | [8 empty] | CHIRMORIE
CHMO1T | 132 | B-2-2b | SPT | [8 empty] | CHIRMORIE
CHSI11 | 132 | B-3-1c | NGET | 51.3441 | -0.32271 | A8 | A | T11 |  | Four Switch Mesh | Outdoor | CHESSINGTON
CHSI1A | 132 | B-3-1c | NGET | 51.3441 | -0.32271 | A8 | A | T11 |  | Four Switch Mesh | Outdoor | CHESSINGTON
CHSI1B | 132 | B-3-1c | NGET | 51.3441 | -0.32271 | A8 | A | T11 |  | Four Switch Mesh | Outdoor | CHESSINGTON
CHSI21 | 275 | B-2-1c, B-3-1c | NGET | 51.3441 | -0.32271 | A8 | A | T11 |  | Four Switch Mesh | Outdoor | CHESSINGTON
CHTE11 | 132 | B-3-2c | NGET | 53.2246 | -1.3889 | P3 | P | T4 |  | Four Switch Mesh | Outdoor | CHESTERFIELD
CHTE12 | 132 | B-3-2c | NGET | 53.2246 | -1.3889 | P3 | P | T4 |  | Four Switch Mesh | Outdoor | CHESTERFIELD
CHTE21 | 275 | B-3-2c, B-4-1c | NGET | 53.2246 | -1.3889 | P3 | P | T4 |  | Four Switch Mesh | Outdoor | CHESTERFIELD
CHTE41 | 400 | B-2-2c, B-3-2c, B-4-2c | NGET | 53.2246 | -1.3889 | P3 | P | T4 |  | Four Switch Mesh | Outdoor | CHESTERFIELD
CHUE4A | 400 | B-2-1c | NGET | 51.4908 | 0.3119 | A1 | A | T11 |  |  |  | CHAFFORD HUNDRED EAST
CHUE4B | 400 | B-2-1c | NGET | 51.4908 | 0.3119 | A1 | A | T11 |  |  |  | CHAFFORD HUNDRED EAST
CILF2A | 275 | B-2-1c, B-3-1c | NGET | 51.6359 | -3.3002 | H6 | H | T8 |  | Double busbar | Outdoor | CILFYNYDD
CILF2B | 275 | B-2-1c, B-3-1c | NGET | 51.6359 | -3.3002 | H6 | H | T8 |  | Double busbar | Outdoor | CILFYNYDD
CILF41 | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 51.6359 | -3.3002 | H6 | H | T8 |  | Double busbar | Outdoor | CILFYNYDD
CITR11 | 132 | B-3-1c | NGET | 51.5302 | -0.095741 | A7 | A | T11 |  | Double busbar | Indoor | CITY ROAD
CITR12 | 132 | B-3-1c | NGET | 51.5302 | -0.095741 | A7 | A | T11 |  | Double busbar | Indoor | CITY ROAD
CITR41 | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 51.5302 | -0.095741 | A7 | A | T11 |  | Double busbar | Indoor | CITY ROAD
CLAC1Q | 132 | B-2-1a, B-3-1a | SHET | 56.2774 | -4.9217 | T3 | T | T1 |  |  |  | CLACHAN
CLAC5J | 11 | B-3-1a | SHET | 56.2774 | -4.9217 | T3 | T | T1 |  |  |  | CLACHAN
CLAU1- | 132 | B-2-2b, B-3-2b | SPT | [8 empty] | CLAUCHRIE
CLAU3- | 33 | B-3-2b | SPT | [8 empty] | CLAUCHRIE
CLAW1- | 132 | B-2-2b | SPT | [8 empty] | CLAWFIN
CLAY1Q | 132 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.1404 | -2.0992 | T2 | T | T1 |  |  |  | CLAYHILLS
CLAY1R | 132 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.1404 | -2.0992 | T2 | T | T1 |  |  |  | CLAYHILLS
CLAY3- | 33 | B-3-1a | SHET | 57.1404 | -2.0992 | T2 | T | T1 |  |  |  | CLAYHILLS
CLEH41 | 400 | B-2-1c | NGET | 51.3382 | 0.94034 | C8 | C | T11 |  | Double busbar | Indoor | CLEVE HILL
CLFO1- | 132 | B-2-2b, B-3-2b | SPT | [8 empty] | CLOICH FOREST
CLFO3- | 33 | B-3-2b | SPT | [8 empty] | CLOICH FOREST
CLGO1- | 132 | B-3-2a | SHET | [8 empty] | CLASH GOUR WIND FARM
CLGO2- | 275 | B-2-2a, B-3-2a | SHET | [8 empty] | CLASH GOUR WIND FARM
CLGO2A | 275 | B-2-2a, B-3-2a | SHET | [8 empty] | CLASH GOUR WIND FARM
CLOI1- | 132 | B-3-2a | SHET | [8 empty] | CLOICHE WIND FARM
CLOI1A | 132 | B-2-2a | SHET | [8 empty] | CLOICHE WIND FARM
CLOI3- | 33 | B-3-2a | SHET | [8 empty] | CLOICHE WIND FARM
CLUN1Q | 132 | B-2-1a, B-3-1a | SHET | 56.7174 | -3.7838 |  |  | T1 |  |  |  | CLUNIE
CLUN1R | 132 | B-2-1a, B-3-1a | SHET | 56.7174 | -3.7838 |  |  | T1 |  |  |  | CLUNIE
CLUN1S | 132 | B-2-1a, B-2-2a | SHET | 56.7174 | -3.7838 |  |  | T1 |  |  |  | CLUNIE
CLUN1T | 132 | B-2-1a, B-2-2a | SHET | 56.7174 | -3.7838 |  |  | T1 |  |  |  | CLUNIE
CLUN5J | 11 | B-3-1a | SHET | 56.7174 | -3.7838 |  |  | T1 |  |  |  | CLUNIE
CLUN5K | 11 | B-3-1a | SHET | 56.7174 | -3.7838 |  |  | T1 |  |  |  | CLUNIE
CLYM2- | 275 | B-2-1b, B-3-1b, B-3-2b | SPT | 55.8223 | -4.1472 | S6 | S | T2 |  |  |  | CLYDE'S MILL
CLYM3A | 33 | B-3-1b | SPT | 55.8223 | -4.1472 | S6 | S | T2 |  |  |  | CLYDE'S MILL
CLYM3B | 33 | B-3-1b | SPT | 55.8223 | -4.1472 | S6 | S | T2 |  |  |  | CLYDE'S MILL
CLYM4- | 400 | B-2-2b, B-3-2b | SPT | 55.8223 | -4.1472 | S6 | S | T2 |  |  |  | CLYDE'S MILL
CLYN2Q | 275 | B-2-1b, B-3-1b | SPT | [8 empty] | CLYDE NORTH
CLYN3A | 33 | B-3-1b | SPT | [8 empty] | CLYDE NORTH
CLYN3B | 33 | B-3-1b | SPT | [8 empty] | CLYDE NORTH
CLYN3C | 33 | B-3-1b | SPT | [8 empty] | CLYDE NORTH
CLYN3D | 33 | B-3-1b | SPT | [8 empty] | CLYDE NORTH
CLYS2R | 275 | B-2-1b, B-3-1b | SPT | [8 empty] | CLYDE SOUTH
CLYS3A | 33 | B-2-2b, B-3-1b | SPT | [8 empty] | CLYDE SOUTH
CLYS3B | 33 | B-2-1b, B-2-2b | SPT | [8 empty] | CLYDE SOUTH
CLYS3X | 33 | B-2-1b, B-3-1b | SPT | [8 empty] | CLYDE SOUTH
CMBS4A | 400 | B-2-2a, B-3-2a | SHET | 57.9436 | -4.4143 |  |  | T1 |  |  |  | CAMBUSHINNIE
CMBS4B | 400 | B-2-2a, B-3-2a | SHET | 57.9436 | -4.4143 |  |  | T1 |  |  |  | CAMBUSHINNIE
COAB4- | 400 | B-2-2b | SPT | 55.6163 | -3.8684 |  |  | T2 |  |  |  | COALBURN BATTERY STORAGE FACILITY
COAL1- | 132 | B-2-1b | SPT | 55.6163 | -3.8684 |  |  | T2 |  |  |  | COALBURN
COAL1A | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.6163 | -3.8684 |  |  | T2 |  |  |  | COALBURN
COAL1B | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.6163 | -3.8684 |  |  | T2 |  |  |  | COALBURN
COAL3U | 33 | B-4-1b | SPT | 55.6163 | -3.8684 |  |  | T2 |  |  |  | COALBURN
COAL3V | 33 | B-4-1b | SPT | 55.6163 | -3.8684 |  |  | T2 |  |  |  | COALBURN
COAL4- | 400 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.6163 | -3.8684 |  |  | T2 |  |  |  | COALBURN
COAN4- | 400 | B-2-2b | SPT | 55.6163 | -3.8684 |  |  | T2 |  |  |  | COALBURN NORTH
COAT2Q | 275 | B-2-1b, B-3-1b | SPT | 55.851 | -4.0125 | S6 | S | T2 |  |  |  | COATBRIDGE
COAT2R | 275 | B-2-1b, B-3-1b | SPT | 55.851 | -4.0125 | S6 | S | T2 |  |  |  | COATBRIDGE
COAT3- | 33 | B-3-1b | SPT | 55.851 | -4.0125 | S6 | S | T2 |  |  |  | COATBRIDGE
COBA3- | 33 | B-3-2b | SPT | 55.6163 | -3.8684 |  |  | T2 |  |  |  | COALBURN BATTERY STORAGE TWO
COBA4- | 400 | B-2-2b, B-3-2b | SPT | 55.6163 | -3.8684 |  |  | T2 |  |  |  | COALBURN BATTERY STORAGE TWO
COCK2- | 275 | B-2-1b, B-3-1b, B-4-1b | SPT | 55.9673 | -2.968 | S6 | S | T2 |  |  |  | COCKENZIE
COCK3- | 33 | B-3-1b | SPT | 55.9673 | -2.968 | S6 | S | T2 |  |  |  | COCKENZIE
COCK4Q | 400 | B-2-2b, B-3-1b | SPT | 55.9673 | -2.968 | S6 | S | T2 |  |  |  | COCKENZIE
COCK4R | 400 | B-2-2b, B-3-1b | SPT | 55.9673 | -2.968 | S6 | S | T2 |  |  |  | COCKENZIE
COGA1- | 132 | B-2-1a, B-3-1a | SHET | 57.1924 | -4.4017 |  |  | T1 |  |  |  | CORRIEGARTH WIND FARM
COGA1C | 132 | B-2-1a | SHET | 57.1924 | -4.4017 |  |  | T1 |  |  |  | CORRIEGARTH WIND FARM
COGA3- | 33 | B-3-1a | SHET | 57.1924 | -4.4017 |  |  | T1 |  |  |  | CORRIEGARTH WIND FARM
COGL4J | 400 | B-2-2a | SHET | [8 empty] | COIRE GLAS PUMPED STORAGE
COGL4K | 400 | B-2-2a | SHET | [8 empty] | COIRE GLAS PUMPED STORAGE
CONN1J | 132 | B-2-2a, B-3-2a | SHET | 58.5131 | -3.8801 |  |  | T1 |  |  |  | CONNAGILL
CONN1K | 132 | B-2-2a, B-3-2a | SHET | 58.5131 | -3.8801 |  |  | T1 |  |  |  | CONNAGILL
CONN2J | 275 | B-2-2a, B-3-2a | SHET | 58.5131 | -3.8801 |  |  | T1 |  |  |  | CONNAGILL
CONN2K | 275 | B-2-2a, B-3-2a | SHET | 58.5131 | -3.8801 |  |  | T1 |  |  |  | CONNAGILL
CONQ11 | 132 | B-3-1c | NGET | 53.2299 | -3.0739 | M5 | M | T4 |  | Double busbar | Indoor | CONNAHS QUAY
CONQ12 | 132 | B-3-1c | NGET | 53.2299 | -3.0739 | M5 | M | T4 |  | Double busbar | Indoor | CONNAHS QUAY
CONQ13 | 132 | B-3-1c | NGET | 53.2299 | -3.0739 | M5 | M | T4 |  | Double busbar | Indoor | CONNAHS QUAY
CONQ41 | 400 | B-2-1c, B-2-2c, B-3-1c | NGET | 53.2299 | -3.0739 | M5 | M | T4 |  | Double busbar | Indoor | CONNAHS QUAY
CORI1J | 132 | B-2-1a, B-3-1a | SHET | 57.6339 | -4.7703 |  |  | T1 |  |  |  | CORRIEMOILLIE
CORI1K | 132 | B-2-1a | SHET | 57.6339 | -4.7703 |  |  | T1 |  |  |  | CORRIEMOILLIE
CORI1P | 132 | B-2-1a | SHET | 57.6339 | -4.7703 |  |  | T1 |  |  |  | CORRIEMOILLIE
CORI1Q | 132 | B-2-1a | SHET | 57.6339 | -4.7703 |  |  | T1 |  |  |  | CORRIEMOILLIE
CORI3- | 33 | B-3-1a | SHET | 57.6339 | -4.7703 |  |  | T1 |  |  |  | CORRIEMOILLIE
CORI3J | 33 | B-3-1a | SHET | 57.6339 | -4.7703 |  |  | T1 |  |  |  | CORRIEMOILLIE
COSO41 | 400 | B-2-1c | NGET | 51.5129 | 0.5067 | C5 | C | T11 |  | Double busbar | Outdoor | CORYTON SOUTH
COST1- | 132 | B-2-2a, B-3-2a | SHET | [8 empty] | COSTA HEAD
COST1A | 132 | B-2-2a | SHET | [8 empty] | COSTA HEAD
COST3- | 33 | B-3-2a | SHET | [8 empty] | COSTA HEAD
COTT41 | 400 | B-2-1c, B-2-2c, B-4-2c | NGET | 53.3007 | -0.78123 | K5 | K | T5 |  | Double busbar | Outdoor | COTTAM
COTT42 | 400 | B-2-1c, B-2-2c | NGET | 53.3007 | -0.78123 | K5 | K | T5 |  | Double busbar | Outdoor | COTTAM
COTT43 | 400 | B-2-2c | NGET | 53.3007 | -0.78123 | K5 | K | T5 |  | Double busbar | Outdoor | COTTAM
COUA1Q | 132 | B-2-1a, B-3-1a | SHET | 56.5383 | -3.2744 | T4 | T | T1 |  |  |  | COUPAR ANGUS
COUA1R | 132 | B-2-1a, B-3-1a | SHET | 56.5383 | -3.2744 | T4 | T | T1 |  |  |  | COUPAR ANGUS
COUA3- | 33 | B-3-1a | SHET | 56.5383 | -3.2744 | T4 | T | T1 |  |  |  | COUPAR ANGUS
COVE11 | 132 | B-3-1c, B-4-1c | NGET | 52.4565 | -1.4638 | L3 | L | T5 |  | Four Switch Mesh | Outdoor | COVENTRY
COVE12 | 132 | B-3-1c, B-4-1c | NGET | 52.4565 | -1.4638 | L3 | L | T5 |  | Four Switch Mesh | Outdoor | COVENTRY
COVE21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 52.4565 | -1.4638 | L3 | L | T5 |  | Four Switch Mesh | Outdoor | COVENTRY
COWL11 | 132 | B-3-1c, B-4-1c | NGET | 51.7115 | -1.1905 | D6 | D | T8 |  | Double busbar | Outdoor | COWLEY
COWL12 | 132 | B-3-1c | NGET | 51.7115 | -1.1905 | D6 | D | T8 |  | Double busbar | Outdoor | COWLEY
COWL41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 51.7115 | -1.1905 | D6 | D | T8 |  | Double busbar | Outdoor | COWLEY
COWT2A | 275 | B-2-1c | NGET | 51.4635 | -3.4483 | H1 | H | T8 |  |  |  | COWBRIDGE TEE
COYL1- | 132 | B-2-1b, B-3-1b | SPT | 55.4473 | -4.4334 | S6 | S | T2 |  |  |  | COYLTON
COYL2- | 275 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.4473 | -4.4334 | S6 | S | T2 |  |  |  | COYLTON
COYL3- | 33 | B-3-1b | SPT | 55.4473 | -4.4334 | S6 | S | T2 |  |  |  | COYLTON
COYT1T | 132 | B-2-1b | SPT | 55.4473 | -4.4334 |  |  | T2 |  |  |  | COYLTON TEE
COYW2S | 275 | B-2-1b, B-2-2b | SPT | 55.4473 | -4.4334 |  |  | T2 |  |  |  | COYLTON WEST
COYW2T | 275 | B-2-1b, B-2-2b | SPT | 55.4473 | -4.4334 |  |  | T2 |  |  |  | COYLTON WEST
CRAI1- | 132 | B-2-1a, B-3-1a | SHET | 57.1314 | -2.1552 | T2 | T | T1 |  |  |  | CRAIGIEBUCKLER
CRAI1P | 132 | B-2-1a | SHET | 57.1314 | -2.1552 | T2 | T | T1 |  |  |  | CRAIGIEBUCKLER
CRAI1Q | 132 | B-2-1a, B-3-1a | SHET | 57.1314 | -2.1552 | T2 | T | T1 |  |  |  | CRAIGIEBUCKLER
CRAI1R | 132 | B-2-1a | SHET | 57.1314 | -2.1552 | T2 | T | T1 |  |  |  | CRAIGIEBUCKLER
CRAI3- | 33 | B-3-1a | SHET | 57.1314 | -2.1552 | T2 | T | T1 |  |  |  | CRAIGIEBUCKLER
CRAS2- | 275 | B-2-2a, B-3-2a | SHET | 56.1315 | -5.2656 |  |  | T1 |  |  |  | CRARAE SOUTH
CRAS3- | 33 | B-3-2a | SHET | 56.1315 | -5.2656 |  |  | T1 |  |  |  | CRARAE SOUTH
CRCK2- | 275 | B-2-2b, B-3-2b | SPT | 54.7128 | -5.8457 |  |  | T2 |  |  |  | CARRICK
CRCK3- | 33 | B-3-2b | SPT | 54.7128 | -5.8457 |  |  | T2 |  |  |  | CARRICK
CRDH1J | 132 | B-2-2a, B-3-2a | SHET | [8 empty] | CREAG DHUBH
CRDH1K | 132 | B-2-2a, B-3-2a | SHET | [8 empty] | CREAG DHUBH
CRDH2J | 275 | B-2-2a, B-3-2a | SHET | [8 empty] | CREAG DHUBH
CRDH2K | 275 | B-2-2a, B-3-2a | SHET | [8 empty] | CREAG DHUBH
CRDY3A | 33 | B-2-2b | SPT | 51.9219 | -2.5903 |  |  | T5 |  |  |  | CROSSDYKES
CRDY3B | 33 | B-2-2b | SPT | 51.9219 | -2.5903 |  |  | T5 |  |  |  | CROSSDYKES
CREA1- | 132 | B-2-1a, B-3-1a | SHET | 58.2109 | -4.5044 |  |  | T1 |  |  |  | CREAG RIABHACH WINDFARM
CREA1A | 132 | B-2-1a | SHET | 58.2109 | -4.5044 |  |  | T1 |  |  |  | CREAG RIABHACH WINDFARM
CREA1B | 132 | B-2-1a | SHET | 58.2109 | -4.5044 |  |  | T1 |  |  |  | CREAG RIABHACH WINDFARM
CREA3- | 33 | B-3-1a | SHET | 58.2109 | -4.5044 |  |  | T1 |  |  |  | CREAG RIABHACH WINDFARM
CREB11 | 132 | B-3-1c | NGET | 53.8007 | -0.41528 | P8 | P | T4 |  | Double busbar | Outdoor | CREYKE BECK
CREB12 | 132 | B-3-1c | NGET | 53.8007 | -0.41528 | P8 | P | T4 |  | Double busbar | Outdoor | CREYKE BECK
CREB2A | 275 | B-2-1c, B-3-1c | NGET | 53.8007 | -0.41528 | P8 | P | T4 |  | Double busbar | Outdoor | CREYKE BECK
CREB2B | 275 | B-2-1c, B-3-1c | NGET | 53.8007 | -0.41528 | P8 | P | T4 |  | Double busbar | Outdoor | CREYKE BECK
CREB41 | 400 | B-2-1c, B-2-2c, B-3-1c | NGET | 53.8007 | -0.41528 | P8 | P | T4 |  | Double busbar | Outdoor | CREYKE BECK
CREB42 | 400 | B-2-2c | NGET | 53.8007 | -0.41528 | P8 | P | T4 |  | Double busbar | Outdoor | CREYKE BECK
CRMU2J | 275 | B-2-2a, B-3-2a | SHET | [8 empty] | CRAIG MURRAIL
CRMU2K | 275 | B-2-2a, B-3-2a | SHET | [8 empty] | CRAIG MURRAIL
CRMU3- | 33 | B-3-2a | SHET | [8 empty] | CRAIG MURRAIL
CROO1Q | 132 | B-2-2b, B-3-1b | SPT | 55.8212 | -4.3656 |  |  | T2 |  |  |  | CROOKSTON
CROO1R | 132 | B-2-2b, B-3-1b | SPT | 55.8212 | -4.3656 |  |  | T2 |  |  |  | CROOKSTON
CROO3J | 33 | B-3-1b | SPT | 55.8212 | -4.3656 |  |  | T2 |  |  |  | CROOKSTON
CROO3K | 33 | B-3-1b | SPT | 55.8212 | -4.3656 |  |  | T2 |  |  |  | CROOKSTON
CRSN1Q | 132 | B-2-2a, B-3-2a | SHET | 51.9219 | -2.5903 |  |  | T5 |  |  |  | CROSSAIG NORTH
CRSN1R | 132 | B-2-2a, B-3-2a | SHET | 51.9219 | -2.5903 |  |  | T5 |  |  |  | CROSSAIG NORTH
CRSN2Q | 275 | B-2-2a, B-3-2a | SHET | 51.9219 | -2.5903 |  |  | T5 |  |  |  | CROSSAIG NORTH
CRSN2R | 275 | B-2-2a, B-3-2a | SHET | 51.9219 | -2.5903 |  |  | T5 |  |  |  | CROSSAIG NORTH
CRSS1J | 132 | B-2-1a, B-2-2a, B-3-1a, B-3-2a | SHET | 55.6976 | -5.4589 |  |  | T1 |  |  |  | CROSSAIG
CRSS1K | 132 | B-2-1a, B-2-2a, B-3-2a | SHET | 55.6976 | -5.4589 |  |  | T1 |  |  |  | CROSSAIG
CRSS1X | 132 | B-3-2a | SHET | 55.6976 | -5.4589 |  |  | T1 |  |  |  | CROSSAIG
CRSS1Y | 132 | B-3-2a | SHET | 55.6976 | -5.4589 |  |  | T1 |  |  |  | CROSSAIG
CRSS2A | 275 | B-2-1a, B-3-2a | SHET | 55.6976 | -5.4589 |  |  | T1 |  |  |  | CROSSAIG
CRSS2B | 275 | B-2-1a, B-3-2a | SHET | 55.6976 | -5.4589 |  |  | T1 |  |  |  | CROSSAIG
CRSS2C | 275 | B-2-1a | SHET | 55.6976 | -5.4589 |  |  | T1 |  |  |  | CROSSAIG
CRSS2D | 275 | B-2-1a | SHET | 55.6976 | -5.4589 |  |  | T1 |  |  |  | CROSSAIG
CRSS3- | 33 | B-3-1a | SHET | 55.6976 | -5.4589 |  |  | T1 |  |  |  | CROSSAIG
CRSS3W | 33 | B-4-1a | SHET | 55.6976 | -5.4589 |  |  | T1 |  |  |  | CROSSAIG
CRSS3X | 33 | B-4-1a | SHET | 55.6976 | -5.4589 |  |  | T1 |  |  |  | CROSSAIG
CRUA2Q | 275 | B-2-1b | SPT | 56.4026 | -5.1131 |  |  | T1 |  |  |  | CRUACHAN
CRUA2R | 275 | B-2-1b | SPT | 56.4026 | -5.1131 |  |  | T1 |  |  |  | CRUACHAN
CRYR1- | 132 | B-3-1b | SPT | 55.9144 | -2.5409 |  |  | T2 |  |  |  | CRYSTAL RIG
CRYR1A | 132 | B-2-1b, B-3-1b | SPT | 55.9144 | -2.5409 |  |  | T2 |  |  |  | CRYSTAL RIG
CRYR31 | 33 | B-3-1b | SPT | 55.9144 | -2.5409 |  |  | T2 |  |  |  | CRYSTAL RIG
CRYR32 | 33 | B-3-1b | SPT | 55.9144 | -2.5409 |  |  | T2 |  |  |  | CRYSTAL RIG
CRYR3V | 33 | B-4-1b | SPT | 55.9144 | -2.5409 |  |  | T2 |  |  |  | CRYSTAL RIG
CRYR4- | 400 | B-2-2b, B-3-1b | SPT | 55.9144 | -2.5409 |  |  | T2 |  |  |  | CRYSTAL RIG
CULJ31 | 33 | B-3-1c | NGET | 51.6612 | -1.2283 | D6 | D | T8 |  | Teed Transformers | Outdoor | CULHAM JET
CULJ32 | 33 | B-3-1c | NGET | 51.6612 | -1.2283 | D6 | D | T8 |  | Teed Transformers | Outdoor | CULHAM JET
CULJ33 | 33 | B-3-1c | NGET | 51.6612 | -1.2283 | D6 | D | T8 |  | Teed Transformers | Outdoor | CULHAM JET
CULJ4A | 400 | B-2-1c, B-3-1c | NGET | 51.6612 | -1.2283 | D6 | D | T8 |  | Teed Transformers | Outdoor | CULHAM JET
CULL1A | 132 | B-2-2a, B-3-2a | SHET | 57.4257 | -4.7026 |  |  | T1 |  |  |  | CULLIGRAN
CULL1Q | 132 | B-2-1a, B-2-2a | SHET | 57.4257 | -4.7026 |  |  | T1 |  |  |  | CULLIGRAN
CULL5- | 11 | B-3-2a | SHET | 57.4257 | -4.7026 |  |  | T1 |  |  |  | CULLIGRAN
CUMB1Q | 132 | B-2-1b, B-3-1b | SPT | 55.9468 | -3.9632 | S5 | S | T2 |  |  |  | CUMBERNAULD
CUMB1R | 132 | B-2-1b, B-3-1b | SPT | 55.9468 | -3.9632 | S5 | S | T2 |  |  |  | CUMBERNAULD
CUMB3- | 33 | B-3-1b | SPT | 55.9468 | -3.9632 | S5 | S | T2 |  |  |  | CUMBERNAULD
CUMH3- | 33 | B-2-2b | SPT | [8 empty] | CUMBERHEAD WF SUBSTATION
CUMW1- | 132 | B-2-2b, B-3-2b | SPT | [8 empty] | CUMBERHEAD WEST
CUMW3- | 33 | B-3-2b | SPT | [8 empty] | CUMBERHEAD WEST
CUPA1Q | 132 | B-2-1b, B-3-1b | SPT | 56.3136 | -3.0367 | S5 | S | T2 |  |  |  | CUPAR
CUPA1R | 132 | B-2-1b, B-3-1b | SPT | 56.3136 | -3.0367 | S5 | S | T2 |  |  |  | CUPAR
CUPA3- | 33 | B-3-1b | SPT | 56.3136 | -3.0367 | S5 | S | T2 |  |  |  | CUPAR
CURR1A | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.9036 | -3.3097 | S6 | S | T2 |  |  |  | CURRIE
CURR1B | 132 | B-2-1b, B-3-1b | SPT | 55.9036 | -3.3097 | S6 | S | T2 |  |  |  | CURRIE
CURR2- | 275 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.9036 | -3.3097 | S6 | S | T2 |  |  |  | CURRIE
CURR3W | 33 | B-4-1b | SPT | 55.9036 | -3.3097 | S6 | S | T2 |  |  |  | CURRIE
CURR5- | 11 | B-3-1b | SPT | 55.9036 | -3.3097 | S6 | S | T2 |  |  |  | CURRIE
DAAS2- | 275 | B-2-2a, B-3-1a | SHET | 57.5569 | -3.421 |  |  | T1 |  |  |  | DALLAS SUBSTATION
DAAS3- | 33 | B-3-1a | SHET | 57.5569 | -3.421 |  |  | T1 |  |  |  | DALLAS SUBSTATION
DAER1- | 132 | B-2-2b, B-3-2b | SPT | [8 empty] | DAER WINDFARM
DAER3- | 33 | B-3-2b | SPT | [8 empty] | DAER WINDFARM
DAIN41 | 400 | B-2-1c, B-2-2c | NGET | 53.4257 | -2.3791 | N6 | N | T4 |  | Double busbar | Outdoor | DAINES
DALB2A | 275 | B-2-2a, B-2-2b | SHET, SPT | 56.4193 | -5.0133 |  |  | T1 |  |  |  | DALMALLY BORDER NODE
DALB2B | 275 | B-2-2a, B-2-2b | SHET, SPT | 56.4193 | -5.0133 |  |  | T1 |  |  |  | DALMALLY BORDER NODE
DALL2- | 275 | B-2-1b, B-2-2b | SPT | 56.4193 | -5.0133 | T1 | T | T1 |  |  |  | DALMALLY
DALM1- | 132 | B-2-1b, B-3-1b | SPT | 55.8357 | -4.2028 | S6 | S | T2 |  |  |  | DALMARNOCK
DALM2Q | 275 | B-2-1b, B-3-1b | SPT | 55.8357 | -4.2028 | S6 | S | T2 |  |  |  | DALMARNOCK
DALM2R | 275 | B-2-1b, B-3-1b | SPT | 55.8357 | -4.2028 | S6 | S | T2 |  |  |  | DALMARNOCK
DALM3- | 33 | B-3-1b | SPT | 55.8357 | -4.2028 | S6 | S | T2 |  |  |  | DALMARNOCK
DAMC41 | 400 | B-2-1c | NGET | 51.4244 | 0.59866 | C2 | C | T11 |  |  |  | DAMHEAD CREEK
DEAW1- | 132 | B-2-2a, B-3-2a | SHET | [8 empty] | DEANIE WEST
DEAW1A | 132 | B-2-2a | SHET | [8 empty] | DEANIE WEST
DEAW5- | 11 | B-3-2a | SHET | [8 empty] | DEANIE WEST
DEBS2- | 275 | B-2-2b, B-3-2b | SPT | [8 empty] | DEVILLA BATTERY STORAGE FACILITY
DEBS3A | 33 | B-3-2b | SPT | [8 empty] | DEVILLA BATTERY STORAGE FACILITY
DEBS3B | 33 | B-3-2b | SPT | [8 empty] | DEVILLA BATTERY STORAGE FACILITY
DEBS3C | 33 | B-3-2b | SPT | [8 empty] | DEVILLA BATTERY STORAGE FACILITY
DEBS3D | 33 | B-3-2b | SPT | [8 empty] | DEVILLA BATTERY STORAGE FACILITY
DEBS3E | 33 | B-3-2b | SPT | [8 empty] | DEVILLA BATTERY STORAGE FACILITY
DELL1- | 132 | B-2-2a | SHET | 55.848 | -4.244 |  |  | T2 |  |  |  | DELL
DELL1A | 132 | B-2-2a | SHET | 55.848 | -4.244 |  |  | T2 |  |  |  | DELL
DELL1B | 132 | B-2-2a | SHET | 55.848 | -4.244 |  |  | T2 |  |  |  | DELL
DENN1- | 132 | B-2-1b, B-3-1b | SPT | 56.0411 | -3.8904 |  |  | T2 |  |  |  | DENNY NORTH
DENN2- | 275 | B-2-1b, B-2-2b, B-3-1b, B-3-2b | SPT | 56.0411 | -3.8904 |  |  | T2 |  |  |  | DENNY NORTH
DENN2T | 275 | B-2-2b | SPT | 56.0411 | -3.8904 |  |  | T2 |  |  |  | DENNY NORTH
DENN4- | 400 | B-2-2b, B-3-1b, B-3-2b | SPT | 56.0411 | -3.8904 |  |  | T2 |  |  |  | DENNY NORTH
DENS1Q | 132 | B-2-1a | SHET | [8 empty] | DENSIDE
DENS1R | 132 | B-2-1a | SHET | [8 empty] | DENSIDE
DESA1Q | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.3195 | -4.4703 |  |  | T2 |  |  |  | DERSALLOCH
DESA3- | 33 | B-3-1b | SPT | 55.3195 | -4.4703 |  |  | T2 |  |  |  | DERSALLOCH
DEVM1- | 132 | B-2-2b, B-3-1b | SPT | 55.915 | -4.7082 | S6 | S | T2 |  |  |  | DEVOL MOOR
DEVM3- | 33 | B-3-1b | SPT | 55.915 | -4.7082 | S6 | S | T2 |  |  |  | DEVOL MOOR
DEVM4- | 400 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.915 | -4.7082 | S6 | S | T2 |  |  |  | DEVOL MOOR
DEVO1- | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 56.1375 | -3.7805 | S5 | S | T2 |  |  |  | DEVONSIDE
DEVO3- | 33 | B-3-1b | SPT | 56.1375 | -3.7805 | S5 | S | T2 |  |  |  | DEVONSIDE
DEWP2Q | 275 | B-2-1b, B-3-1b | SPT | 55.9473 | -3.2105 | S6 | S | T2 |  |  |  | DEWAR PLACE
DEWP2R | 275 | B-2-1b, B-3-1b | SPT | 55.9473 | -3.2105 | S6 | S | T2 |  |  |  | DEWAR PLACE
DEWP3- | 33 | B-3-1b, B-4-1b | SPT | 55.9473 | -3.2105 | S6 | S | T2 |  |  |  | DEWAR PLACE
DIDC41 | 400 | B-2-1c, B-3-1c | NGET | 51.6256 | -1.2592 | D6 | D | T8 |  | Double busbar | Outdoor | DIDCOT
DINO41 | 400 | B-2-1c, B-2-2c | NGET | 53.1215 | -4.1001 | M6 | M | T4 |  | Single Switch Mesh | Indoor | DINORWIG
DISS4A | 400 | B-2-1c, B-2-2c | NGET | 52.3736 | 1.1235 | J7 | J | T7 |  |  |  | DISS
DISS4B | 400 | B-2-1c | NGET | 52.3736 | 1.1235 | J7 | J | T7 |  |  |  | DISS
DLCH1A | 132 | B-2-1a, B-2-2a | SHET | 58.0528 | -4.4033 |  |  | T1 |  |  |  | DALCHORK
DLCH1B | 132 | B-2-1a, B-2-2a | SHET | 58.0528 | -4.4033 |  |  | T1 |  |  |  | DALCHORK
DONO1- | 132 | B-2-2b, B-3-1b | SPT | 55.5917 | -3.8332 |  |  | T2 |  |  |  | DOUGLAS NORTH COLLECTOR
DONO3A | 33 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.5917 | -3.8332 |  |  | T2 |  |  |  | DOUGLAS NORTH COLLECTOR
DORE11 | 132 | B-2-1a, B-3-1a | SHET | 57.3785 | -3.0992 |  |  | T1 |  |  |  | DORENELL WIND FARM
DORE12 | 132 | B-2-1a, B-3-1a | SHET | 57.3785 | -3.0992 |  |  | T1 |  |  |  | DORENELL WIND FARM
DORE31 | 33 | B-3-1a | SHET | 57.3785 | -3.0992 |  |  | T1 |  |  |  | DORENELL WIND FARM
DORE32 | 33 | B-3-1a | SHET | 57.3785 | -3.0992 |  |  | T1 |  |  |  | DORENELL WIND FARM
DOUN1- | 132 | B-2-2a, B-3-1a, B-3-2a | SHET | 58.5752 | -3.7542 | T5 | T | T1 |  |  |  | DOUNREAY
DOUN2- | 275 | B-2-1a, B-2-2a, B-3-1a, B-3-2a | SHET | 58.5752 | -3.7542 | T5 | T | T1 |  |  |  | DOUNREAY
DOUN2A | 275 | B-2-2a, B-3-2a | SHET | 58.5752 | -3.7542 | T5 | T | T1 |  |  |  | DOUNREAY
DOUN2B | 275 | B-2-2a | SHET | 58.5752 | -3.7542 | T5 | T | T1 |  |  |  | DOUNREAY
DOUN2C | 275 | B-2-2a | SHET | 58.5752 | -3.7542 | T5 | T | T1 |  |  |  | DOUNREAY
DOUN3- | 33 | B-3-2a | SHET | 58.5752 | -3.7542 | T5 | T | T1 |  |  |  | DOUNREAY
DOUN3W | 33 | B-4-1a | SHET | 58.5752 | -3.7542 | T5 | T | T1 |  |  |  | DOUNREAY
DOUN3X | 33 | B-4-1a | SHET | 58.5752 | -3.7542 | T5 | T | T1 |  |  |  | DOUNREAY
DOUN3Y | 33 | B-4-2a | SHET | 58.5752 | -3.7542 | T5 | T | T1 |  |  |  | DOUNREAY
DRAK11 | 132 | B-3-1c | NGET | 52.7738 | -1.653 | L2 | L | T5 |  | Double busbar | Outdoor | DRAKELOW
DRAK21 | 275 | B-2-1c, B-3-1c | NGET | 52.7738 | -1.653 | L2 | L | T5 |  | Double busbar | Outdoor | DRAKELOW
DRAK41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 52.7738 | -1.653 | L2 | L | T5 |  | Double busbar | Outdoor | DRAKELOW
DRAX11 | 132 | B-3-1c | NGET | 53.7362 | -0.99241 | P4 | P | T4 |  | Double busbar | Outdoor | DRAX
DRAX41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 53.7362 | -0.99241 | P4 | P | T4 |  | Double busbar | Outdoor | DRAX
DRAX42 | 400 | B-2-1c, B-3-1c | NGET | 53.7362 | -0.99241 | P4 | P | T4 |  | Double busbar | Outdoor | DRAX
DRCR1Q | 132 | B-2-1b, B-3-1b | SPT | 55.9064 | -3.5866 | S5 | S | T2 |  |  |  | DRUMCROSS
DRCR1R | 132 | B-2-1b, B-3-1b | SPT | 55.9064 | -3.5866 | S5 | S | T2 |  |  |  | DRUMCROSS
DRCR3- | 33 | B-3-1b | SPT | 55.9064 | -3.5866 | S5 | S | T2 |  |  |  | DRUMCROSS
DRUM2Q | 275 | B-2-1b, B-3-1b | SPT | 55.9159 | -4.3485 | S5 | S | T2 |  |  |  | DRUMCHAPEL
DRUM2R | 275 | B-2-1b, B-3-1b | SPT | 55.9159 | -4.3485 | S5 | S | T2 |  |  |  | DRUMCHAPEL
DRUM3- | 33 | B-3-1b | SPT | 55.9159 | -4.3485 | S5 | S | T2 |  |  |  | DRUMCHAPEL
DUBE1Q | 132 | B-2-1a, B-3-1a | SHET | 58.2654 | -3.4349 | T5 | T | T1 |  |  |  | DUNBEATH
DUBE3- | 33 | B-3-1a | SHET | 58.2654 | -3.4349 | T5 | T | T1 |  |  |  | DUNBEATH
DUCC1J | 132 | B-2-1a | SHET | [8 empty] | DUNMORE CABLE COMPOUND
DUCC1K | 132 | B-2-1a | SHET | [8 empty] | DUNMORE CABLE COMPOUND
DUGR1Q | 132 | B-2-2a, B-3-1a | SHET | 57.4328 | -6.54 | T1 | T | T1 |  |  |  | DUNVEGAN GRID
DUGR3- | 33 | B-3-1a | SHET | 57.4328 | -6.54 | T1 | T | T1 |  |  |  | DUNVEGAN GRID
DUMF1- | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.0672 | -3.5915 |  |  | T2 |  |  |  | DUMFRIES
DUMF3A | 33 | B-3-1b | SPT | 55.0672 | -3.5915 |  |  | T2 |  |  |  | DUMFRIES
DUMF3B | 33 | B-3-1b | SPT | 55.0672 | -3.5915 |  |  | T2 |  |  |  | DUMFRIES
DUMF3I | 33 | B-3-1b | SPT | 55.0672 | -3.5915 |  |  | T2 |  |  |  | DUMFRIES
DUNB1Q | 132 | B-2-2b, B-3-1b | SPT | 55.9777 | -2.5739 | S6 | S | T2 |  |  |  | DUNBAR
DUNB1R | 132 | B-2-2b, B-3-1b | SPT | 55.9777 | -2.5739 | S6 | S | T2 |  |  |  | DUNBAR
DUNB1S | 132 | B-2-2b, B-3-1b | SPT | 55.9777 | -2.5739 | S6 | S | T2 |  |  |  | DUNBAR
DUNB1T | 132 | B-2-2b, B-3-1b | SPT | 55.9777 | -2.5739 | S6 | S | T2 |  |  |  | DUNBAR
DUNB3A | 33 | B-3-1b | SPT | 55.9777 | -2.5739 | S6 | S | T2 |  |  |  | DUNBAR
DUNB3B | 33 | B-3-1b | SPT | 55.9777 | -2.5739 | S6 | S | T2 |  |  |  | DUNBAR
DUNE1- | 132 | B-2-2b, B-3-1b, B-3-2b | SPT | [8 empty] | DUNLAW EXTENSION
DUNE3- | 33 | B-2-1b, B-2-2b, B-3-1b | SPT | [8 empty] | DUNLAW EXTENSION
DUNE3A | 33 | B-3-2b | SPT | [8 empty] | DUNLAW EXTENSION
DUNF1Q | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 56.0892 | -3.4503 | S5 | S | T2 |  |  |  | DUNFERMLINE
DUNF1R | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 56.0892 | -3.4503 | S5 | S | T2 |  |  |  | DUNFERMLINE
DUNF3- | 33 | B-3-1b | SPT | 56.0892 | -3.4503 | S5 | S | T2 |  |  |  | DUNFERMLINE
DUNG21 | 275 | B-3-1c | NGET | 50.915 | 0.94743 | C4 | C | T11 |  | Double busbar | Indoor | DUNGENESS
DUNG41 | 400 | B-2-1c, B-3-1c | NGET | 50.915 | 0.94743 | C4 | C | T11 |  | Double busbar | Indoor | DUNGENESS
DUNH1Q | 132 | B-2-1b | SPT | 55.3131 | -4.2044 |  |  | T2 |  |  |  | DUNHILL
DUNH1R | 132 | B-2-1b | SPT | 55.3131 | -4.2044 |  |  | T2 |  |  |  | DUNHILL
DUNH1S | 132 | B-2-1b, B-3-1b | SPT | 55.3131 | -4.2044 |  |  | T2 |  |  |  | DUNHILL
DUNH1T | 132 | B-2-1b, B-3-1b | SPT | 55.3131 | -4.2044 |  |  | T2 |  |  |  | DUNHILL
DUNH3- | 33 | B-3-1b | SPT | 55.3131 | -4.2044 |  |  | T2 |  |  |  | DUNHILL
DUNM1- | 132 | B-2-1a, B-3-1a | SHET | 57.2712 | -4.3071 |  |  | T1 |  |  |  | DUNMAGLASS
DUNM1C | 132 | B-2-1a | SHET | 57.2712 | -4.3071 |  |  | T1 |  |  |  | DUNMAGLASS
DUNM1T | 132 | B-2-1a, B-2-2a | SHET | 57.2712 | -4.3071 |  |  | T1 |  |  |  | DUNMAGLASS
DUNM3- | 33 | B-3-1a | SHET | 57.2712 | -4.3071 |  |  | T1 |  |  |  | DUNMAGLASS
DUNO1Q | 132 | B-2-2a, B-3-2a | SHET | 55.9758 | -4.9485 | S5 | S | T2 |  |  |  | DUNOON
DUNO1R | 132 | B-2-2a, B-3-2a | SHET | 55.9758 | -4.9485 | S5 | S | T2 |  |  |  | DUNOON
DUNO3- | 33 | B-3-2a | SHET | 55.9758 | -4.9485 | S5 | S | T2 |  |  |  | DUNOON
DWEX3- | 33 | B-2-2b | SPT | 55.558 | -3.872 |  |  | T2 |  |  |  | DOUGLAS WEST EXTENSION
DYCE1J | 132 | B-2-1a | SHET | 57.2162 | -2.1902 | T2 | T | T1 |  |  |  | DYCE
DYCE1Q | 132 | B-2-1a, B-3-1a | SHET | 57.2162 | -2.1902 | T2 | T | T1 |  |  |  | DYCE
DYCE1R | 132 | B-2-1a, B-3-1a | SHET | 57.2162 | -2.1902 | T2 | T | T1 |  |  |  | DYCE
DYCE1T | 132 | B-2-1a | SHET | 57.2162 | -2.1902 | T2 | T | T1 |  |  |  | DYCE
DYCE1U | 132 | B-2-1a | SHET | 57.2162 | -2.1902 | T2 | T | T1 |  |  |  | DYCE
DYCE3- | 33 | B-3-1a | SHET | 57.2162 | -2.1902 | T2 | T | T1 |  |  |  | DYCE
EALI21 | 275 | B-2-1c, B-3-1c | NGET | 51.5019 | -0.29614 | A7 | A | T11 |  | Four Switch Mesh | Indoor | EALING
EALI61 | 66 | B-3-1c | NGET | 51.5019 | -0.29614 | A7 | A | T11 |  | Four Switch Mesh | Indoor | EALING
EARR21 | 275 | B-2-2a | SHET | [8 empty] | EARRAGHAIL
EARR2A | 275 | B-2-2a | SHET | [8 empty] | EARRAGHAIL
EARR2B | 275 | B-2-2a, B-3-2a | SHET | [8 empty] | EARRAGHAIL
EARR3- | 33 | B-3-2a | SHET | [8 empty] | EARRAGHAIL
EASO11 | 132 | B-3-1c | NGET | 52.2146 | -0.30164 | J4 | J | T6 |  | Double busbar | Outdoor | EATON SOCON
EASO12 | 132 | B-3-1c | NGET | 52.2146 | -0.30164 | J4 | J | T6 |  | Double busbar | Outdoor | EATON SOCON
EASO41 | 400 | B-2-1c, B-3-1c | NGET | 52.2146 | -0.30164 | J4 | J | T6 |  | Double busbar | Outdoor | EATON SOCON
EASO4A | 400 | B-2-1c, B-3-1c | NGET | 52.2146 | -0.30164 | J4 | J | T6 |  | Double busbar | Outdoor | EATON SOCON
EASO4B | 400 | B-2-1c | NGET | 52.2146 | -0.30164 | J4 | J | T6 |  | Double busbar | Outdoor | EATON SOCON
EAST1Q | 132 | B-2-2b, B-3-1b | SPT | 55.1123 | -4.1742 | S6 | S | T2 |  |  |  | EARLSTOUN
EAST5- | 11 | B-3-1b | SPT | 55.1123 | -4.1742 | S6 | S | T2 |  |  |  | EARLSTOUN
ECCF1J | 132 | B-2-1b | SPT | 55.0662 | -3.2853 |  |  | T2 |  |  |  | ECCLEFECHAN
ECCF1K | 132 | B-2-1b | SPT | 55.0662 | -3.2853 |  |  | T2 |  |  |  | ECCLEFECHAN
ECCL1- | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.67 | -2.3316 | S6 | S | T2 |  |  |  | ECCLES
ECCL3- | 33 | B-3-1b | SPT | 55.67 | -2.3316 | S6 | S | T2 |  |  |  | ECCLES
ECCL3V | 33 | B-4-1b | SPT | 55.67 | -2.3316 | S6 | S | T2 |  |  |  | ECCLES
ECCL4A | 400 | B-2-1b, B-2-2b, B-3-1b, B-4-2b | SPT | 55.67 | -2.3316 | S6 | S | T2 |  |  |  | ECCLES
ECCL4B | 400 | B-2-1b, B-2-2b, B-3-1b, B-4-2b | SPT | 55.67 | -2.3316 | S6 | S | T2 |  |  |  | ECCLES
ECCL4C | 400 | B-2-1b | SPT | 55.67 | -2.3316 | S6 | S | T2 |  |  |  | ECCLES
ECCL4D | 400 | B-2-1b | SPT | 55.67 | -2.3316 | S6 | S | T2 |  |  |  | ECCLES
ECLA11 | 132 | B-3-1c | NGET | 51.9263 | -0.90719 | D4 | D | T6 |  | Double busbar | Outdoor | EAST CLAYDON
ECLA12 | 132 | B-3-1c, B-4-1c | NGET | 51.9263 | -0.90719 | D4 | D | T6 |  | Double busbar | Outdoor | EAST CLAYDON
ECLA41 | 400 | B-2-1c, B-3-1c, B-4-1c, B-4-2c | NGET | 51.9263 | -0.90719 | D4 | D | T6 |  | Double busbar | Outdoor | EAST CLAYDON
EDIN1A | 132 | B-2-2a, B-4-2a | SHET | 54.6117 | -5.884 |  |  | T1 |  |  |  | EDINBANE 132/33KV
EDIN1B | 132 | B-2-2a, B-4-2a | SHET | 54.6117 | -5.884 |  |  | T1 |  |  |  | EDINBANE 132/33KV
EDIN1C | 132 | B-2-2a | SHET | 54.6117 | -5.884 |  |  | T1 |  |  |  | EDINBANE 132/33KV
EDIN1D | 132 | B-2-2a | SHET | 54.6117 | -5.884 |  |  | T1 |  |  |  | EDINBANE 132/33KV
EDIN1J | 132 | B-2-2a, B-3-2a | SHET | 54.6117 | -5.884 |  |  | T1 |  |  |  | EDINBANE 132/33KV
EDIN1K | 132 | B-2-2a, B-3-2a | SHET | 54.6117 | -5.884 |  |  | T1 |  |  |  | EDINBANE 132/33KV
EDIN3- | 33 | B-3-2a | SHET | 54.6117 | -5.884 |  |  | T1 |  |  |  | EDINBANE 132/33KV
EDIN3A | 33 | B-3-2a | SHET | 54.6117 | -5.884 |  |  | T1 |  |  |  | EDINBANE 132/33KV
EDIN8A | 22 | B-3-2a, B-4-2a | SHET | 54.6117 | -5.884 |  |  | T1 |  |  |  | EDINBANE 132/33KV
EDIN8B | 22 | B-3-2a, B-4-2a | SHET | 54.6117 | -5.884 |  |  | T1 |  |  |  | EDINBANE 132/33KV
EERH2- | 275 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.8787 | -4.0727 | S6 | S | T2 |  |  |  | EASTERHOUSE
EERH3- | 33 | B-3-1b | SPT | 55.8787 | -4.0727 | S6 | S | T2 |  |  |  | EASTERHOUSE
EGGB41 | 400 | B-2-1c, B-2-2c | NGET | 53.7134 | -1.1298 | P6 | P | T4 |  | Double busbar | Indoor | EGGBOROUGH
EGGB42 | 400 | B-2-1c, B-2-2c | NGET | 53.7134 | -1.1298 | P6 | P | T4 |  | Double busbar | Indoor | EGGBOROUGH
EKIL2Q | 275 | B-2-1b | SPT | 55.7864 | -4.1941 | S6 | S | T2 |  |  |  | EAST KILBRIDE
EKIL2R | 275 | B-2-1b | SPT | 55.7864 | -4.1941 | S6 | S | T2 |  |  |  | EAST KILBRIDE
EKIL2S | 275 | B-2-1b, B-3-1b | SPT | 55.7864 | -4.1941 | S6 | S | T2 |  |  |  | EAST KILBRIDE
EKIL2T | 275 | B-2-1b, B-3-1b | SPT | 55.7864 | -4.1941 | S6 | S | T2 |  |  |  | EAST KILBRIDE
EKIL3A | 33 | B-2-1b, B-3-1b | SPT | 55.7864 | -4.1941 | S6 | S | T2 |  |  |  | EAST KILBRIDE
EKIL3B | 33 | B-2-1b, B-3-1b | SPT | 55.7864 | -4.1941 | S6 | S | T2 |  |  |  | EAST KILBRIDE
EKIS2- | 275 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.7402 | -4.1636 | S6 | S | T2 |  |  |  | EAST KILBRIDE SOUTH
EKIS3A | 33 | B-3-1b | SPT | 55.7402 | -4.1636 | S6 | S | T2 |  |  |  | EAST KILBRIDE SOUTH
EKIS3B | 33 | B-3-1b | SPT | 55.7402 | -4.1636 | S6 | S | T2 |  |  |  | EAST KILBRIDE SOUTH
ELCH1- | 132 | B-2-2a, B-3-2a | SHET | [8 empty] | ELCHIES
ELCH3- | 33 | B-3-2a | SHET | [8 empty] | ELCHIES
ELDE1Q | 132 | B-2-2b, B-3-1b | SPT | 55.8408 | -4.4643 | S6 | S | T2 |  |  |  | ELDERSLIE
ELDE1R | 132 | B-2-2b, B-3-1b | SPT | 55.8408 | -4.4643 | S6 | S | T2 |  |  |  | ELDERSLIE
ELDE3- | 33 | B-3-1b | SPT | 55.8408 | -4.4643 | S6 | S | T2 |  |  |  | ELDERSLIE
ELGI1L | 132 | B-2-1a | SHET | 57.6642 | -3.3207 | T1 | T | T1 |  |  |  | ELGIN
ELGI1M | 132 | B-2-1a | SHET | 57.6642 | -3.3207 | T1 | T | T1 |  |  |  | ELGIN
ELGI1Q | 132 | B-2-1a, B-3-1a | SHET | 57.6642 | -3.3207 | T1 | T | T1 |  |  |  | ELGIN
ELGI1R | 132 | B-2-1a, B-3-1a | SHET | 57.6642 | -3.3207 | T1 | T | T1 |  |  |  | ELGIN
ELGI3- | 33 | B-3-1a | SHET | 57.6642 | -3.3207 | T1 | T | T1 |  |  |  | ELGIN
ELIB1- | 132 | B-2-2a | SHET | [8 empty] | ELLIBISTER SWITCHING STATION
ELIB1A | 132 | B-2-2a | SHET | [8 empty] | ELLIBISTER SWITCHING STATION
ELLA11 | 132 | B-3-1c | NGET | 53.6939 | -1.8237 | P1 | P | T4 |  | Four Switch Mesh | Outdoor | ELLAND
ELLA12 | 132 | B-3-1c | NGET | 53.6939 | -1.8237 | P1 | P | T4 |  | Four Switch Mesh | Outdoor | ELLAND
ELLA21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 53.6939 | -1.8237 | P1 | P | T4 |  | Four Switch Mesh | Outdoor | ELLAND
ELST11 | 132 | B-3-1c | NGET | 51.6615 | -0.34538 | A6 | A | T11 |  | Double busbar | Indoor | ELSTREE
ELST12 | 132 | B-2-1c, B-3-1c | NGET | 51.6615 | -0.34538 | A6 | A | T11 |  | Double busbar | Indoor | ELSTREE
ELST13 | 132 | B-3-1c | NGET | 51.6615 | -0.34538 | A6 | A | T11 |  | Double busbar | Indoor | ELSTREE
ELST21 | 275 | B-2-1c, B-3-1c | NGET | 51.6615 | -0.34538 | A6 | A | T11 |  | Double busbar | Indoor | ELSTREE
ELST22 | 275 | B-2-1c, B-3-1c | NGET | 51.6615 | -0.34538 | A6 | A | T11 |  | Double busbar | Indoor | ELSTREE
ELST41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c, B-4-2c | NGET | 51.6615 | -0.34538 | A6 | A | T11 |  | Double busbar | Indoor | ELSTREE
ELST4A | 400 | B-2-2c | NGET | 51.6615 | -0.34538 | A6 | A | T11 |  | Double busbar | Indoor | ELSTREE
ELST4B | 400 | B-2-2c, B-3-1c | NGET | 51.6615 | -0.34538 | A6 | A | T11 |  | Double busbar | Indoor | ELSTREE
ELVA1- | 132 | B-2-2b, B-3-1b | SPT | 55.4382 | -3.6715 |  |  | T2 |  |  |  | ELVANFOOT
ELVA2Q | 275 | B-2-1b, B-3-1b | SPT | 55.4382 | -3.6715 |  |  | T2 |  |  |  | ELVANFOOT
ELVA2R | 275 | B-2-1b, B-3-1b | SPT | 55.4382 | -3.6715 |  |  | T2 |  |  |  | ELVANFOOT
ELVA3A | 33 | B-2-1b, B-3-1b | SPT | 55.4382 | -3.6715 |  |  | T2 |  |  |  | ELVANFOOT
ELVA3V | 33 | B-4-1b | SPT | 55.4382 | -3.6715 |  |  | T2 |  |  |  | ELVANFOOT
ELVA4- | 400 | B-2-1b, B-2-2b, B-3-1b, B-4-1b | SPT | 55.4382 | -3.6715 |  |  | T2 |  |  |  | ELVANFOOT
ENDE11 | 132 | B-3-1c | NGET | 52.5976 | -1.217 | L8 | L | T5 |  | Four Switch Mesh | Outdoor | ENDERBY
ENDE41 | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 52.5976 | -1.217 | L8 | L | T5 |  | Four Switch Mesh | Outdoor | ENDERBY
ENEI1- | 132 | B-2-2a | SHET | [8 empty] | ENERGY ISLES WIND FARM
ENEI1N | 132 | B-2-2a | SHET | [8 empty] | ENERGY ISLES WIND FARM
ENHI1- | 132 | B-2-1b | SPT | [8 empty] | ENOCH HILL WIND FARM
ENHI3- | 33 | B-2-2b | SPT | [8 empty] | ENOCH HILL WIND FARM
ERED2- | 275 | B-2-2a, B-3-2a | SHET | 56.2354 | -5.2781 |  |  | T1 |  |  |  | EREDINE
ERED3- | 33 | B-3-2a | SHET | 56.2354 | -5.2781 |  |  | T1 |  |  |  | EREDINE
ERRO1A | 132 | B-2-1a, B-3-1a | SHET | 56.7075 | -4.0096 |  |  | T1 |  |  |  | ERROCHTY
ERRO1B | 132 | B-2-1a, B-3-1a | SHET | 56.7075 | -4.0096 |  |  | T1 |  |  |  | ERROCHTY
ERRO1J | 132 | B-2-1a, B-2-2a, B-3-1a, B-3-2a | SHET | 56.7075 | -4.0096 |  |  | T1 |  |  |  | ERROCHTY
ERRO1K | 132 | B-2-1a, B-2-2a, B-3-1a, B-3-2a | SHET | 56.7075 | -4.0096 |  |  | T1 |  |  |  | ERROCHTY
ERRO1T | 132 | B-2-1a, B-3-1a | SHET | 56.7075 | -4.0096 |  |  | T1 |  |  |  | ERROCHTY
ERRO3- | 33 | B-3-2a | SHET | 56.7075 | -4.0096 |  |  | T1 |  |  |  | ERROCHTY
ERRO5J | 11 | B-3-1a | SHET | 56.7075 | -4.0096 |  |  | T1 |  |  |  | ERROCHTY
ERRO5L | 11 | B-3-1a | SHET | 56.7075 | -4.0096 |  |  | T1 |  |  |  | ERROCHTY
ERSK1Q | 132 | B-2-2b, B-3-1b | SPT | 55.9036 | -4.4828 | S6 | S | T2 |  |  |  | ERSKINE
ERSK1R | 132 | B-2-2b, B-3-1b | SPT | 55.9036 | -4.4828 | S6 | S | T2 |  |  |  | ERSKINE
ERSK3- | 33 | B-3-1b | SPT | 55.9036 | -4.4828 | S6 | S | T2 |  |  |  | ERSKINE
ESST1- | 132 | B-2-1b | SPT | [8 empty] | ESSENSIDE
ESST1Q | 132 | B-2-1b | SPT | [8 empty] | ESSENSIDE
EUCH1- | 132 | B-2-2b, B-3-2b | SPT | [8 empty] | EUCHANHEAD
EUCH3- | 33 | B-3-2b | SPT | [8 empty] | EUCHANHEAD
EWEH1Q | 132 | B-2-2b, B-3-1b | SPT | 55.1425 | -3.1788 |  |  | T2 |  |  |  | EWE HILL
EWEH3- | 33 | B-2-2b, B-3-1b | SPT | 55.1425 | -3.1788 |  |  | T2 |  |  |  | EWE HILL
EXET11 | 132 | B-3-1c, B-4-1c | NGET | 50.7676 | -3.4052 | F6 | F | T9 |  | Double busbar | Outdoor | EXETER
EXET41 | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 50.7676 | -3.4052 | F6 | F | T9 |  | Double busbar | Outdoor | EXETER
FAAR1Q | 132 | B-2-1a, B-3-1a | SHET | 57.3363 | -4.161 |  |  | T1 |  |  |  | FARR WINDFARM
FAAR1R | 132 | B-2-1a, B-3-1a | SHET | 57.3363 | -4.161 |  |  | T1 |  |  |  | FARR WINDFARM
FAAR3J | 33 | B-3-1a | SHET | 57.3363 | -4.161 |  |  | T1 |  |  |  | FARR WINDFARM
FAAR3K | 33 | B-3-1a | SHET | 57.3363 | -4.161 |  |  | T1 |  |  |  | FARR WINDFARM
FALL3A | 33 | B-3-1b | SPT | 55.8255 | -2.6668 |  |  | T2 |  |  |  | FALLAGO
FALL3B | 33 | B-3-1b | SPT | 55.8255 | -2.6668 |  |  | T2 |  |  |  | FALLAGO
FALL3C | 33 | B-3-2b | SPT | 55.8255 | -2.6668 |  |  | T2 |  |  |  | FALLAGO
FALL4- | 400 | B-2-2b, B-3-1b, B-3-2b | SPT | 55.8255 | -2.6668 |  |  | T2 |  |  |  | FALLAGO
FARI1J | 132 | B-2-1a, B-3-2a | SHET | 57.3183 | -4.3746 |  |  | T1 |  |  |  | FARIGAIG
FARI1K | 132 | B-2-1a, B-3-2a | SHET | 57.3183 | -4.3746 |  |  | T1 |  |  |  | FARIGAIG
FARI2J | 275 | B-2-1a, B-3-2a | SHET | 57.3183 | -4.3746 |  |  | T1 |  |  |  | FARIGAIG
FARI2K | 275 | B-2-1a, B-3-2a | SHET | 57.3183 | -4.3746 |  |  | T1 |  |  |  | FARIGAIG
FASI1- | 132 | B-2-2b | SPT | [8 empty] | FAW SIDE
FASI1A | 132 | B-2-2b | SPT | [8 empty] | FAW SIDE
FASI1B | 132 | B-2-2b | SPT | [8 empty] | FAW SIDE
FASN1A | 132 | B-2-2a, B-3-2a | SHET | 57.3301 | -4.7935 | T1 | T | T1 |  |  |  | FASNAKYLE
FASN1B | 132 | B-2-2a, B-3-2a | SHET | 57.3301 | -4.7935 | T1 | T | T1 |  |  |  | FASNAKYLE
FASN3- | 33 | B-3-2a | SHET | 57.3301 | -4.7935 | T1 | T | T1 |  |  |  | FASNAKYLE
FASQ1- | 132 | B-2-2a | SHET | [8 empty] | FASQUE
FASQ1J | 132 | B-2-2a, B-3-2a | SHET | [8 empty] | FASQUE
FASQ3- | 33 | B-3-2a | SHET | [8 empty] | FASQUE
FAUG1- | 132 | B-2-1a, B-2-2a, B-3-1a, B-3-2a | SHET | 57.1366 | -4.7199 | T1 | T | T1 |  |  |  | FORT AUGUSTUS
FAUG1J | 132 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.1366 | -4.7199 | T1 | T | T1 |  |  |  | FORT AUGUSTUS
FAUG1K | 132 | B-2-1a, B-3-1a | SHET | 57.1366 | -4.7199 | T1 | T | T1 |  |  |  | FORT AUGUSTUS
FAUG1Q | 132 | B-2-1a, B-3-1a | SHET | 57.1366 | -4.7199 | T1 | T | T1 |  |  |  | FORT AUGUSTUS
FAUG1R | 132 | B-2-2a | SHET | 57.1366 | -4.7199 | T1 | T | T1 |  |  |  | FORT AUGUSTUS
FAUG1S | 132 | B-2-2a | SHET | 57.1366 | -4.7199 | T1 | T | T1 |  |  |  | FORT AUGUSTUS
FAUG3- | 33 | B-3-1a | SHET | 57.1366 | -4.7199 | T1 | T | T1 |  |  |  | FORT AUGUSTUS
FAUG3W | 33 | B-4-1a | SHET | 57.1366 | -4.7199 | T1 | T | T1 |  |  |  | FORT AUGUSTUS
FAUG3X | 33 | B-4-1a | SHET | 57.1366 | -4.7199 | T1 | T | T1 |  |  |  | FORT AUGUSTUS
FAUG3Y | 33 | B-4-1a | SHET | 57.1366 | -4.7199 | T1 | T | T1 |  |  |  | FORT AUGUSTUS
FAUG3Z | 33 | B-4-1a | SHET | 57.1366 | -4.7199 | T1 | T | T1 |  |  |  | FORT AUGUSTUS
FAUG4J | 400 | B-2-1a, B-2-2a, B-3-1a, B-3-2a | SHET | 57.1366 | -4.7199 | T1 | T | T1 |  |  |  | FORT AUGUSTUS
FAUG4K | 400 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.1366 | -4.7199 | T1 | T | T1 |  |  |  | FORT AUGUSTUS
FAWL11 | 132 | B-3-1c | NGET | 50.8217 | -1.3286 | B2 | B | T10 |  | Double busbar | Indoor | FAWLEY
FAWL41 | 400 | B-2-1c, B-3-1c | NGET | 50.8217 | -1.3286 | B2 | B | T10 |  | Double busbar | Indoor | FAWLEY
FECK21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 52.2499 | -1.9719 | L3 | L | T5 |  | Double busbar | Outdoor | FECKENHAM
FECK41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c, B-4-2c | NGET | 52.2499 | -1.9719 | L3 | L | T5 |  | Double busbar | Outdoor | FECKENHAM
FECK61 | 66 | B-3-1c | NGET | 52.2499 | -1.9719 | L3 | L | T5 |  | Double busbar | Outdoor | FECKENHAM
FELL1- | 132 | B-2-2b, B-3-2b | SPT | [8 empty] | FELL WIND FARM
FELL3- | 33 | B-3-2b | SPT | [8 empty] | FELL WIND FARM
FENW4A | 400 | B-2-1c | NGET | 53.6394 | -1.1025 | P6 | P | T4 |  |  |  | FENWICK TEE
FERO1- | 132 | B-2-1a, B-3-1a | SHET | [8 empty] | FERNOCH WIND
FERO1S | 132 | B-2-1a, B-2-2a | SHET | [8 empty] | FERNOCH WIND
FERO3- | 33 | B-3-1a | SHET | [8 empty] | FERNOCH WIND
FERR11 | 132 | B-3-1c | NGET | 53.7173 | -1.2849 | P5 | P | T4 |  |  |  | FERRYBRIDGE
FERR21 | 275 | B-2-1c, B-3-1c | NGET | 53.7173 | -1.2849 | P5 | P | T4 |  |  |  | FERRYBRIDGE
FERR22 | 275 | B-2-1c, B-3-1c | NGET | 53.7173 | -1.2849 | P5 | P | T4 |  |  |  | FERRYBRIDGE
FERR23 | 275 | B-2-1c, B-3-1c | NGET | 53.7173 | -1.2849 | P5 | P | T4 |  |  |  | FERRYBRIDGE
FERR2A | 275 | B-2-1c, B-3-1c | NGET | 53.7173 | -1.2849 | P5 | P | T4 |  |  |  | FERRYBRIDGE
FERR2B | 275 | B-2-1c | NGET | 53.7173 | -1.2849 | P5 | P | T4 |  |  |  | FERRYBRIDGE
FERR4A | 400 | B-2-1c, B-3-1c | NGET | 53.7173 | -1.2849 | P5 | P | T4 |  |  |  | FERRYBRIDGE
FERR61 | 66 | B-3-1c | NGET | 53.7173 | -1.2849 | P5 | P | T4 |  |  |  | FERRYBRIDGE
FETT1- | 132 | B-2-2a, B-3-1a, B-3-2a | SHET | 56.9655 | -2.3491 | T2 | T | T1 |  |  |  | FETTERESSO
FETT3S | 33 | B-3-1a | SHET | 56.9655 | -2.3491 | T2 | T | T1 |  |  |  | FETTERESSO
FETT4J | 400 | B-2-2a, B-3-2a | SHET | 56.9655 | -2.3491 | T2 | T | T1 |  |  |  | FETTERESSO
FETT4K | 400 | B-2-2a, B-3-2a | SHET | 56.9655 | -2.3491 | T2 | T | T1 |  |  |  | FETTERESSO
FETT4Q | 400 | B-2-2a | SHET | 56.9655 | -2.3491 | T2 | T | T1 |  |  |  | FETTERESSO
FETT4R | 400 | B-2-2a | SHET | 56.9655 | -2.3491 | T2 | T | T1 |  |  |  | FETTERESSO
FFES21 | 275 | B-2-1c | NGET | 52.9807 | -3.969 | M7 | M | T4 |  | Single Switch Mesh | Outdoor | FFESTINIOG
FIDD1A | 132 | B-2-1a | SHET | 56.9245 | -2.3026 | T2 | T | T1 |  |  |  | FIDDES
FIDD1B | 132 | B-2-1a, B-3-1a | SHET | 56.9245 | -2.3026 | T2 | T | T1 |  |  |  | FIDDES
FIDD1Q | 132 | B-2-1a, B-3-1a | SHET | 56.9245 | -2.3026 | T2 | T | T1 |  |  |  | FIDDES
FIDD1R | 132 | B-2-1a, B-3-1a | SHET | 56.9245 | -2.3026 | T2 | T | T1 |  |  |  | FIDDES
FIDD3- | 33 | B-3-1a | SHET | 56.9245 | -2.3026 | T2 | T | T1 |  |  |  | FIDDES
FIDF11 | 132 | B-3-1c | NGET | 53.3713 | -2.6891 | N1 | N | T4 |  | Double busbar | Indoor | FIDDLERS FERRY
FIDF12 | 132 | B-3-1c | NGET | 53.3713 | -2.6891 | N1 | N | T4 |  | Double busbar | Indoor | FIDDLERS FERRY
FIDF21 | 275 | B-2-1c, B-3-1c | NGET | 53.3713 | -2.6891 | N1 | N | T4 |  | Double busbar | Indoor | FIDDLERS FERRY
FIGS2- | 275 | B-2-2b | SPT | [8 empty] | FIFE GRID SERVICES
FINL1Q | 132 | B-2-1a, B-3-1a | SHET | [8 empty] | FINLARIG
FINL5- | 11 | B-3-1a | SHET | [8 empty] | FINLARIG
FINN1Q | 132 | B-2-1b, B-3-1b | SPT | 55.865 | -4.286 | S5 | S | T2 |  |  |  | FINNIESTON
FINN1R | 132 | B-2-1b, B-3-1b | SPT | 55.865 | -4.286 | S5 | S | T2 |  |  |  | FINNIESTON
FINN3- | 33 | B-3-1b | SPT | 55.865 | -4.286 | S5 | S | T2 |  |  |  | FINNIESTON
FINS1- | 132 | B-2-2a, B-3-2a, B-4-2a | SHET | 51.924 | -1.7701 |  |  | T5 |  |  |  | ORKNEY FINSTOWN
FINS2A | 275 | B-2-2a, B-3-2a | SHET | 51.924 | -1.7701 |  |  | T5 |  |  |  | ORKNEY FINSTOWN
FINS2B | 275 | B-2-2a | SHET | 51.924 | -1.7701 |  |  | T5 |  |  |  | ORKNEY FINSTOWN
FINS2C | 275 | B-2-2a | SHET | 51.924 | -1.7701 |  |  | T5 |  |  |  | ORKNEY FINSTOWN
FINS3- | 33 | B-3-2a | SHET | 51.924 | -1.7701 |  |  | T5 |  |  |  | ORKNEY FINSTOWN
FINS3Y | 33 | B-4-2a | SHET | 51.924 | -1.7701 |  |  | T5 |  |  |  | ORKNEY FINSTOWN
FLEE11 | 132 | B-3-1c, B-4-1c | NGET | 51.2513 | -0.88336 | B3 | B | T10 |  | Four Switch Mesh | Outdoor | FLEET
FLEE12 | 132 | B-3-1c | NGET | 51.2513 | -0.88336 | B3 | B | T10 |  | Four Switch Mesh | Outdoor | FLEET
FLEE41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 51.2513 | -0.88336 | B3 | B | T10 |  | Four Switch Mesh | Outdoor | FLEET
FLIB41 | 400 | B-2-1c | NGET | 53.2383 | -3.0455 | M5 | M | T4 |  |  |  | FLINTSHIRE BRIDGE
FOGG1Q | 132 | B-2-1a | SHET | [8 empty] | FOGGIETON
FOGG1R | 132 | B-2-1a | SHET | [8 empty] | FOGGIETON
FOUR21 | 275 | B-2-1c, B-3-1c | NGET | 55.0118 | -2.1642 | Q8 | Q | T3 |  | Single Switch Mesh | Outdoor | FOURSTONES
FOUR31 | 33 | B-3-1c | NGET | 55.0118 | -2.1642 | Q8 | Q | T3 |  | Single Switch Mesh | Outdoor | FOURSTONES
FOUR71 | 25 | B-3-1c | NGET | 55.0118 | -2.1642 | Q8 | Q | T3 |  | Single Switch Mesh | Outdoor | FOURSTONES
FOUX41 | 400 | B-2-2c | NGET | 52.9894 | -3.9347 | L5 | L | T4 |  |  |  | FOUR CROSSES
FOYE2- | 275 | B-2-1a, B-2-2a | SHET | 57.2691 | -4.4743 |  |  | T1 |  |  |  | FOYERS
FOYE2J | 275 | B-2-2a | SHET | 57.2691 | -4.4743 |  |  | T1 |  |  |  | FOYERS
FRAS1Q | 132 | B-2-1a, B-3-1a | SHET | 57.6859 | -2.0244 | T2 | T | T1 |  |  |  | FRASERBURGH
FRAS1R | 132 | B-2-1a, B-3-1a | SHET | 57.6859 | -2.0244 | T2 | T | T1 |  |  |  | FRASERBURGH
FRAS3- | 33 | B-3-1a | SHET | 57.6859 | -2.0244 | T2 | T | T1 |  |  |  | FRASERBURGH
FRIN4A | 400 | B-2-1c | NGET | 52.1976 | 1.5295 | J2 | J | T7 |  |  |  | FRISTON NORTH
FRIN4B | 400 | B-2-1c | NGET | 52.1976 | 1.5295 | J2 | J | T7 |  |  |  | FRISTON NORTH
FRIS41 | 400 | B-2-1c | NGET | 52.1976 | 1.5295 | J2 | J | T7 |  |  |  | FRISTON
FRIS4A | 400 | B-2-1c | NGET | 52.1976 | 1.5295 | J2 | J | T7 |  |  |  | FRISTON
FRIS4B | 400 | B-2-1c | NGET | 52.1976 | 1.5295 | J2 | J | T7 |  |  |  | FRISTON
FRIS4C | 400 | B-2-1c | NGET | 52.1976 | 1.5295 | J2 | J | T7 |  |  |  | FRISTON
FRIS4D | 400 | B-2-1c | NGET | 52.1976 | 1.5295 | J2 | J | T7 |  |  |  | FRISTON
FROD11 | 132 | B-3-1c | NGET | 53.3087 | -2.716 | N3 | N | T4 |  | Single Switch Mesh | Outdoor | FRODSHAM
FROD21 | 275 | B-2-1c, B-3-1c | NGET | 53.3087 | -2.716 | N3 | N | T4 |  | Single Switch Mesh | Outdoor | FRODSHAM
FROD22 | 275 | B-2-1c, B-3-1c | NGET | 53.3087 | -2.716 | N3 | N | T4 |  | Single Switch Mesh | Outdoor | FRODSHAM
FROD41 | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 53.3087 | -2.716 | N3 | N | T4 |  | Single Switch Mesh | Outdoor | FRODSHAM
FWIL1Q | 132 | B-2-2a, B-3-1a | SHET | 56.8204 | -5.0779 | T1 | T | T1 |  |  |  | FORT WILLIAM
FWIL1R | 132 | B-2-1a, B-2-2a, B-3-1a | SHET | 56.8204 | -5.0779 | T1 | T | T1 |  |  |  | FORT WILLIAM
FWIL3- | 33 | B-3-1a | SHET | 56.8204 | -5.0779 | T1 | T | T1 |  |  |  | FORT WILLIAM
FYRI1J | 132 | B-2-1a, B-3-1a | SHET | 57.7001 | -4.3001 |  |  | T1 |  |  |  | FYRISH
FYRI1K | 132 | B-2-1a, B-3-1a | SHET | 57.7001 | -4.3001 |  |  | T1 |  |  |  | FYRISH
FYRI2J | 275 | B-2-2a, B-3-1a | SHET | 57.7001 | -4.3001 |  |  | T1 |  |  |  | FYRISH
FYRI2K | 275 | B-2-2a, B-3-1a | SHET | 57.7001 | -4.3001 |  |  | T1 |  |  |  | FYRISH
GALA1- | 132 | B-2-2b, B-3-1b, B-3-2b | SPT | 55.6109 | -2.7719 | S6 | S | T2 |  |  |  | GALASHIELS
GALA3- | 33 | B-3-1b, B-3-2b | SPT | 55.6109 | -2.7719 | S6 | S | T2 |  |  |  | GALASHIELS
GALN1Q | 132 | B-2-2b, B-3-2b | SPT | [8 empty] | GALA NORTH
GALN1R | 132 | B-2-2b, B-3-2b | SPT | [8 empty] | GALA NORTH
GALN4- | 400 | B-2-2b, B-3-2b | SPT | [8 empty] | GALA NORTH
GARB1Q | 132 | B-2-1b, B-2-2a | SHET, SPT | [8 empty] | GARELOCH BOUNDARY
GARB1R | 132 | B-2-1b, B-2-2a | SHET, SPT | [8 empty] | GARELOCH BOUNDARY
GARB1S | 132 | B-2-1b, B-2-2a | SHET, SPT | [8 empty] | GARELOCH BOUNDARY
GARB1T | 132 | B-2-1a, B-2-1b, B-2-2a | SHET, SPT | [8 empty] | GARELOCH BOUNDARY
GARE1S | 132 | B-2-1b | SPT | 56.084 | -4.831 |  |  | T2 |  |  |  | GARELOCH
GARE1T | 132 | B-2-1b | SPT | 56.084 | -4.831 |  |  | T2 |  |  |  | GARELOCH
GART4A | 400 | B-2-1c | NGET | 53.6437 | -0.72549 | P8 | P | T4 |  |  |  | GARTH CABLE COMPOUND
GART4B | 400 | B-2-1c, B-2-2c | NGET | 53.6437 | -0.72549 | P8 | P | T4 |  |  |  | GARTH CABLE COMPOUND
GAWH1Q | 132 | B-2-2b, B-3-1b | SPT | 55.5625 | -3.9467 |  |  | T2 |  |  |  | GALAWHISTLE
GAWH3- | 33 | B-2-1b, B-3-1b | SPT | 55.5625 | -3.9467 |  |  | T2 |  |  |  | GALAWHISTLE
GHPS1- | 132 | B-2-2b, B-3-2b | SPT | [8 empty] | GLENMUCKLOCH HYDRO PUMPED STORAGE
GHPS3A | 33 | B-3-2b | SPT | [8 empty] | GLENMUCKLOCH HYDRO PUMPED STORAGE
GHPS3B | 33 | B-3-2b | SPT | [8 empty] | GLENMUCKLOCH HYDRO PUMPED STORAGE
GHPS4- | 400 | B-2-2b, B-3-2b | SPT | [8 empty] | GLENMUCKLOCH HYDRO PUMPED STORAGE
GIFF2Q | 275 | B-2-1b, B-3-2b | SPT | 55.798 | -4.3 | S6 | S | T2 |  |  |  | GIFFNOCK
GIFF2R | 275 | B-2-1b, B-3-2b | SPT | 55.798 | -4.3 | S6 | S | T2 |  |  |  | GIFFNOCK
GIFF3A | 33 | B-3-2b | SPT | 55.798 | -4.3 | S6 | S | T2 |  |  |  | GIFFNOCK
GIFF3B | 33 | B-3-2b | SPT | 55.798 | -4.3 | S6 | S | T2 |  |  |  | GIFFNOCK
GILB1J | 132 | B-2-2a | SHET | [8 empty] | GILLS BAY SUBSTATION
GILB1K | 132 | B-2-2a | SHET | [8 empty] | GILLS BAY SUBSTATION
GILB1L | 132 | B-2-2a | SHET | [8 empty] | GILLS BAY SUBSTATION
GILB1M | 132 | B-2-2a | SHET | [8 empty] | GILLS BAY SUBSTATION
GLAG1Q | 132 | B-2-2a | SHET | 56.4621 | -2.9963 |  |  | T1 |  |  |  | GLENAGNES
GLAG1R | 132 | B-2-2a | SHET | 56.4621 | -2.9963 |  |  | T1 |  |  |  | GLENAGNES
GLAG1S | 132 | B-2-2a | SHET | 56.4621 | -2.9963 |  |  | T1 |  |  |  | GLENAGNES
GLAG1T | 132 | B-2-2a | SHET | 56.4621 | -2.9963 |  |  | T1 |  |  |  | GLENAGNES
GLAP3- | 33 | B-2-1b | SPT | 55.0225 | -5.006 |  |  | T2 |  |  |  | GLEN APP
GLDO1G | 132 | B-2-1a, B-3-1a | SHET | 57.143 | -4.6449 |  |  | T1 |  |  |  | GLENDOE SUBSTATION
GLDO8- | 22 | B-3-1a | SHET | 57.143 | -4.6449 |  |  | T1 |  |  |  | GLENDOE SUBSTATION
GLDY1- | 132 | B-2-2a | SHET | [8 empty] | GLENDYE
GLEN1Q | 132 | B-2-1a, B-3-1a | SHET | 57.2018 | -4.7202 |  |  | T1 |  |  |  | GLENMORISTON
GLEN5- | 11 | B-3-1a | SHET | 57.2018 | -4.7202 |  |  | T1 |  |  |  | GLENMORISTON
GLFA1- | 132 | B-2-1a, B-3-1a | SHET | 57.4157 | -3.3158 |  |  | T1 |  |  |  | GLENFARCLAS
GLFA3- | 33 | B-3-1a | SHET | 57.4157 | -3.3158 |  |  | T1 |  |  |  | GLENFARCLAS
GLGL1- | 132 | B-2-2b | SPT | 55.3375 | -4.0176 |  |  | T2 |  |  |  | GLENGLASS
GLGL1B | 132 | B-2-2b | SPT | 55.3375 | -4.0176 |  |  | T2 |  |  |  | GLENGLASS
GLGL1Q | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.3375 | -4.0176 |  |  | T2 |  |  |  | GLENGLASS
GLGL1R | 132 | B-2-2b, B-3-1b | SPT | 55.3375 | -4.0176 |  |  | T2 |  |  |  | GLENGLASS
GLGL3- | 33 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.3375 | -4.0176 |  |  | T2 |  |  |  | GLENGLASS
GLKO1- | 132 | B-2-1a | SHET | 57.3152 | -4.0878 |  |  | T1 |  |  |  | GLEN KYLLACHY
GLLE1- | 132 | B-2-2b, B-3-1b | SPT | 55.0996 | -4.1855 | S6 | S | T2 |  |  |  | GLENLEE
GLLE5- | 11 | B-3-1b | SPT | 55.0996 | -4.1855 | S6 | S | T2 |  |  |  | GLENLEE
GLLU1Q | 132 | B-2-1b, B-3-1b | SPT | 54.882 | -4.8071 | S6 | S | T2 |  |  |  | GLENLUCE
GLLU1R | 132 | B-2-2b, B-3-1b | SPT | 54.882 | -4.8071 | S6 | S | T2 |  |  |  | GLENLUCE
GLLU3- | 33 | B-3-1b | SPT | 54.882 | -4.8071 | S6 | S | T2 |  |  |  | GLENLUCE
GLMU3- | 33 | B-2-2b | SPT | [8 empty] | GLENMUCKLOCH
GLNI1- | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 56.1114 | -3.272 | S5 | S | T2 |  |  |  | GLENNISTON
GLNI3- | 33 | B-3-1b | SPT | 56.1114 | -3.272 | S5 | S | T2 |  |  |  | GLENNISTON
GLNU1- | 132 | B-2-2a, B-3-2a | SHET | [8 empty] | GLEN ULLINISH WINDFARM
GLNU3- | 33 | B-3-2a | SHET | [8 empty] | GLEN ULLINISH WINDFARM
GLRB2- | 275 | B-2-1a, B-2-1b | SHET, SPT | 56.2068 | -3.2003 |  |  | T2 |  |  |  | GLENROTHES BOUNDARY
GLRO2- | 275 | B-2-1b, B-3-1b | SPT | 56.2068 | -3.2003 | S5 | S | T2 |  |  |  | GLENROTHES
GLRO3A | 33 | B-3-1b | SPT | 56.2068 | -3.2003 | S5 | S | T2 |  |  |  | GLENROTHES
GLRO3B | 33 | B-3-1b | SPT | 56.2068 | -3.2003 | S5 | S | T2 |  |  |  | GLENROTHES
GLUE1- | 132 | B-2-2a | SHET | [8 empty] | GLEN ULLINISH EXTENSION
GNSH1- | 132 | B-2-2b, B-3-2b | SPT | [8 empty] | GLENSHIMMEROCH
GNSH3- | 33 | B-3-2b | SPT | [8 empty] | GLENSHIMMEROCH
GORG1Q | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.9361 | -3.2365 | S6 | S | T2 |  |  |  | GORGIE
GORG1R | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.9361 | -3.2365 | S6 | S | T2 |  |  |  | GORGIE
GORG3- | 33 | B-3-1b | SPT | 55.9361 | -3.2365 | S6 | S | T2 |  |  |  | GORGIE
GORW2- | 275 | B-2-2a, B-3-1a | SHET | 58.1149 | -3.9572 |  |  | T1 |  |  |  | GORDONBUSH WINDFARM
GORW3- | 33 | B-3-1a | SHET | 58.1149 | -3.9572 |  |  | T1 |  |  |  | GORDONBUSH WINDFARM
GOVA1Q | 132 | B-2-1b, B-3-1b | SPT | 55.8549 | -4.3169 | S6 | S | T2 |  |  |  | GOVAN
GOVA1R | 132 | B-2-1b, B-3-1b | SPT | 55.8549 | -4.3169 | S6 | S | T2 |  |  |  | GOVAN
GOVA3- | 33 | B-3-1b | SPT | 55.8549 | -4.3169 | S6 | S | T2 |  |  |  | GOVAN
GRAI11 | 132 | B-3-1c | NGET | 51.4451 | 0.71579 | C3 | C | T11 |  | Double busbar | Outdoor | GRAIN
GRAI41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 51.4451 | 0.71579 | C3 | C | T11 |  | Double busbar | Outdoor | GRAIN
GRAN61 | 66 | B-3-1c | NGET | 51.5629 | -3.7539 | H1 | H | T8 |  |  |  | GRANGE
GREM1J | 132 | B-2-2a, B-3-2a | SHET | 60.1666 | -1.1643 |  |  | T1 |  |  |  | GREMISTA
GREM1K | 132 | B-2-2a, B-3-2a | SHET | 60.1666 | -1.1643 |  |  | T1 |  |  |  | GREMISTA
GREM1L | 132 | B-2-2a | SHET | 60.1666 | -1.1643 |  |  | T1 |  |  |  | GREMISTA
GREM1M | 132 | B-2-2a | SHET | 60.1666 | -1.1643 |  |  | T1 |  |  |  | GREMISTA
GREM1N | 132 | B-2-2a, B-3-2a | SHET | 60.1666 | -1.1643 |  |  | T1 |  |  |  | GREMISTA
GREM1P | 132 | B-2-2a | SHET | 60.1666 | -1.1643 |  |  | T1 |  |  |  | GREMISTA
GREM1Q | 132 | B-2-2a | SHET | 60.1666 | -1.1643 |  |  | T1 |  |  |  | GREMISTA
GREM3- | 33 | B-3-2a | SHET | 60.1666 | -1.1643 |  |  | T1 |  |  |  | GREMISTA
GREN11 | 132 | B-3-1c, B-4-1c | NGET | 52.2431 | -0.72894 | J6 | J | T6 |  | Double busbar | Outdoor | GRENDON
GREN12 | 132 | B-3-1c | NGET | 52.2431 | -0.72894 | J6 | J | T6 |  | Double busbar | Outdoor | GRENDON
GREN41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 52.2431 | -0.72894 | J6 | J | T6 |  | Double busbar | Outdoor | GRENDON
GRIF1S | 132 | B-2-1a, B-3-1a | SHET | [8 empty] | GRIFFIN WINDFARM (SSE)
GRIF1T | 132 | B-2-1a, B-3-1a | SHET | [8 empty] | GRIFFIN WINDFARM (SSE)
GRIF36 | 33 | B-3-1a | SHET | [8 empty] | GRIFFIN WINDFARM (SSE)
GRIF38 | 33 | B-3-1a | SHET | [8 empty] | GRIFFIN WINDFARM (SSE)
GRIW11 | 132 | B-3-1c | NGET | 53.5653 | -0.15236 | P7 | P | T4 |  | Single Switch Mesh | Outdoor | GRIMSBY WEST
GRIW12 | 132 | B-3-1c | NGET | 53.5653 | -0.15236 | P7 | P | T4 |  | Single Switch Mesh | Outdoor | GRIMSBY WEST
GRIW41 | 400 | B-2-1c, B-3-1c | NGET | 53.5653 | -0.15236 | P7 | P | T4 |  | Single Switch Mesh | Outdoor | GRIMSBY WEST
GRMO2- | 275 | B-2-1b, B-3-1b | SPT | 56.005 | -3.6946 |  |  | T2 |  |  |  | GRANGEMOUTH
GRMO3A | 33 | B-2-1b | SPT | 56.005 | -3.6946 |  |  | T2 |  |  |  | GRANGEMOUTH
GRMO3C | 33 | B-2-1b, B-3-1b | SPT | 56.005 | -3.6946 |  |  | T2 |  |  |  | GRANGEMOUTH
GRNA1- | 132 | B-2-2b, B-3-1b | SPT | 55.0322 | -3.052 |  |  | T2 |  |  |  | GRETNA
GRNA3U | 33 | B-4-2b | SPT | 55.0322 | -3.052 |  |  | T2 |  |  |  | GRETNA
GRNA4- | 400 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.0322 | -3.052 |  |  | T2 |  |  |  | GRETNA
GRNA4C | 400 | B-2-1b | SPT | 55.0322 | -3.052 |  |  | T2 |  |  |  | GRETNA
GRNV4- | 400 | B-2-2a | SHET | [8 empty] | GREEN VOLT OFFSHORE WIND FARM
GRST2A | 275 | B-2-1c, B-4-1c | NGET | 54.5753 | -1.1247 | Q2 | Q | T3 |  |  |  | GREYSTONES
GRST2B | 275 | B-2-1c, B-4-1c | NGET | 54.5753 | -1.1247 | Q2 | Q | T3 |  |  |  | GREYSTONES
GRST61 | 66 | B-3-1c | NGET | 54.5753 | -1.1247 | Q2 | Q | T3 |  |  |  | GREYSTONES
GRTO61 | 66 | B-3-1c | NGET | 54.5805 | -1.1488 | Q2 | Q | T3 |  |  |  | GRANGETOWN
GRUB1Q | 132 | B-2-1a, B-3-1a | SHET | 57.6194 | -4.8312 | T1 | T | T1 |  |  |  | GRUDIE BRIDGE
GRUB1R | 132 | B-2-1a, B-3-1a | SHET | 57.6194 | -4.8312 | T1 | T | T1 |  |  |  | GRUDIE BRIDGE
GRUB3- | 33 | B-3-1a | SHET | 57.6194 | -4.8312 | T1 | T | T1 |  |  |  | GRUDIE BRIDGE
GWYD41 | 400 | B-2-2c | NGET | 52.9809 | -3.401 | M7 | M | T4 |  |  |  | GWYDDELWERN
HACK11 | 132 | B-3-1c | NGET | 51.5589 | -0.04435 | A1 | A | T11 |  | Teed Transformers | Outdoor | HACKNEY
HACK41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-3-2c | NGET | 51.5589 | -0.04435 | A1 | A | T11 |  | Teed Transformers | Outdoor | HACKNEY
HACK61 | 66 | B-3-2c | NGET | 51.5589 | -0.04435 | A1 | A | T11 |  | Teed Transformers | Outdoor | HACKNEY
HADH1- | 132 | B-2-1b, B-3-1b | SPT | 55.2504 | -4.7075 |  |  | T2 |  |  |  | HADYARD HILL
HADH3- | 33 | B-3-1b | SPT | 55.2504 | -4.7075 |  |  | T2 |  |  |  | HADYARD HILL
HAGH3- | 33 | B-2-1b | SPT | [8 empty] | HAGSHAW HILL PHASE 2
HAGR1Q | 132 | B-2-1b, B-3-1b | SPT | 55.8286 | -4.2955 | S6 | S | T2 |  |  |  | HAGGS ROAD
HAGR1R | 132 | B-2-1b, B-3-1b | SPT | 55.8286 | -4.2955 | S6 | S | T2 |  |  |  | HAGGS ROAD
HAGR3- | 33 | B-3-1b | SPT | 55.8286 | -4.2955 | S6 | S | T2 |  |  |  | HAGGS ROAD
HAHA3- | 33 | B-2-1b | SPT | [8 empty] | HAGSHAW HILL PHASE 1
HAKB1- | 132 | B-2-1b, B-2-2b | SPT | 55.0304 | -3.0331 | Q8 | Q | T3 |  |  |  | HARKER BOUNDARY
HAKB4- | 400 | B-2-2b, B-2-2c | NGET, SPT | 55.0304 | -3.0331 | Q8 | Q | T3 |  |  |  | HARKER BOUNDARY
HAKB4B | 400 | B-2-2b, B-2-2c | NGET, SPT | 55.0304 | -3.0331 | Q8 | Q | T3 |  |  |  | HARKER BOUNDARY
HAMB4A | 400 | B-2-1c, B-2-2c | NGET | 53.8788 | -2.9878 | R4 | R | T3 |  |  |  | HAMBLETON
HAMB4B | 400 | B-2-1c, B-2-2c | NGET | 53.8788 | -2.9878 | R4 | R | T3 |  |  |  | HAMBLETON
HAMH1A | 132 | B-2-1c | NGET | 52.531 | -1.7143 | L3 | L | T5 |  | Double busbar | Outdoor | HAMS HALL
HAMH1B | 132 | B-2-1c | NGET | 52.531 | -1.7143 | L3 | L | T5 |  | Double busbar | Outdoor | HAMS HALL
HAMH2A | 275 | B-2-1c, B-3-1c | NGET | 52.531 | -1.7143 | L3 | L | T5 |  | Double busbar | Outdoor | HAMS HALL
HAMH41 | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 52.531 | -1.7143 | L3 | L | T5 |  | Double busbar | Outdoor | HAMS HALL
HARE1- | 132 | B-2-2b, B-3-1b | SPT | 55.2643 | -3.5608 |  |  | T2 |  |  |  | HARESTANES
HARE3A | 33 | B-3-1b | SPT | 55.2643 | -3.5608 |  |  | T2 |  |  |  | HARESTANES
HARE3B | 33 | B-3-1b | SPT | 55.2643 | -3.5608 |  |  | T2 |  |  |  | HARESTANES
HARG11 | 132 | B-3-2c | NGET | 54.942 | -2.9627 | Q8 | Q | T3 |  |  |  | HARKER GIS
HARG21 | 275 | B-2-2c, B-3-2c | NGET | 54.942 | -2.9627 | Q8 | Q | T3 |  |  |  | HARKER GIS
HARG2A | 275 | B-2-2c, B-3-2c | NGET | 54.942 | -2.9627 | Q8 | Q | T3 |  |  |  | HARKER GIS
HARG41 | 400 | B-2-2c, B-3-2c, B-4-2c | NGET | 54.942 | -2.9627 | Q8 | Q | T3 |  |  |  | HARKER GIS
HARK13 | 132 | B-2-1b, B-2-2b | SPT | 54.9411 | -2.9616 | Q8 | Q | T3 |  | Double busbar | Outdoor | HARKER
HARK23 | 275 | B-2-1c, B-2-2c | NGET | 54.9411 | -2.9616 | Q8 | Q | T3 |  | Double busbar | Outdoor | HARKER
HARK24 | 275 | B-2-1c, B-2-2c | NGET | 54.9411 | -2.9616 | Q8 | Q | T3 |  | Double busbar | Outdoor | HARKER
HARM21 | 275 | B-2-1c, B-3-1c | NGET | 54.7005 | -1.292 | Q4 | Q | T3 |  | Four Switch Mesh | Outdoor | HARTMOOR
HARM61 | 66 | B-3-1c | NGET | 54.7005 | -1.292 | Q4 | Q | T3 |  | Four Switch Mesh | Outdoor | HARTMOOR
HARR3- | 33 | B-2-1b | SPT | [8 empty] | HARTING RIG WIND FARM
HATL21 | 275 | B-2-1c | NGET | 54.6357 | -1.1832 | Q2 | Q | T3 |  | Double busbar | Indoor | HARTLEPOOL
HAWI1- | 132 | B-2-2b, B-3-1b | SPT | 55.4331 | -2.8015 | S6 | S | T2 |  |  |  | HAWICK
HAWI1C | 132 | B-2-2b | SPT | 55.4331 | -2.8015 | S6 | S | T2 |  |  |  | HAWICK
HAWI1D | 132 | B-2-2b | SPT | 55.4331 | -2.8015 | S6 | S | T2 |  |  |  | HAWICK
HAWI3- | 33 | B-3-1b | SPT | 55.4331 | -2.8015 | S6 | S | T2 |  |  |  | HAWICK
HAWP21 | 275 | B-2-1c, B-3-1c, B-3-2c | NGET | 54.8054 | -1.4031 | Q4 | Q | T3 |  | Four Switch Mesh | Outdoor | HAWTHORN PIT
HAWP2A | 275 | B-2-1c | NGET | 54.8054 | -1.4031 | Q4 | Q | T3 |  | Four Switch Mesh | Outdoor | HAWTHORN PIT
HAWP41 | 400 | B-2-2c, B-3-2c | NGET | 54.8054 | -1.4031 | Q4 | Q | T3 |  | Four Switch Mesh | Outdoor | HAWTHORN PIT
HAWP4A | 400 | B-2-2c, B-3-1c | NGET | 54.8054 | -1.4031 | Q4 | Q | T3 |  | Four Switch Mesh | Outdoor | HAWTHORN PIT
HAWP61 | 66 | B-3-1c | NGET | 54.8054 | -1.4031 | Q4 | Q | T3 |  | Four Switch Mesh | Outdoor | HAWTHORN PIT
HBES4- | 400 | B-2-2b | SPT | 55.7199 | -4.8927 |  |  | T2 |  |  |  | HUNTERSTON BATTERY STORAGE
HEDO21 | 275 | B-2-1c | NGET | 53.7475 | -0.23436 | P8 | P | T4 |  | Double busbar | Indoor | HEDON (GIS)
HELE1Q | 132 | B-2-1b, B-3-1b | SPT | 56.0226 | -4.7087 | S5 | S | T2 |  |  |  | HELENSBURGH
HELE1R | 132 | B-2-1b, B-3-1b | SPT | 56.0226 | -4.7087 | S5 | S | T2 |  |  |  | HELENSBURGH
HELE3- | 33 | B-3-1b | SPT | 56.0226 | -4.7087 | S5 | S | T2 |  |  |  | HELENSBURGH
HEND11 | 132 | B-2-1c | NGET | 51.5948 | -0.25829 | A6 | A | T11 |  |  |  | HENDON
HESF4- | 400 | B-2-2b | SPT | 55.7199 | -4.8927 |  |  | T2 |  |  |  | HUNTERSTON ENERGY STORAGE FACILITY
HEST3- | 33 | B-3-2a | SHET | [8 empty] | HESTA HEAD
HEYS11 | 132 | B-3-1c | NGET | 54.0323 | -2.8911 | R5 | R | T3 |  | Double busbar | Outdoor | HEYSHAM
HEYS41 | 400 | B-2-1c, B-3-1c | NGET | 54.0323 | -2.8911 | R5 | R | T3 |  | Double busbar | Outdoor | HEYSHAM
HIBU41 | 400 | B-2-1c, B-3-1c | NGET | 51.5614 | -0.1137 | A1 | A | T11 |  | Double busbar | Indoor | HIGHBURY
HICL1- | 132 | B-2-2a | SHET | [8 empty] | HIGH CONSTELLATION
HIGM41 | 400 | B-2-2c, B-3-2c | NGET | 53.228 | -0.79574 | K2 | K | T5 |  | Single Switch Mesh | Outdoor | HIGH MARNHAM
HIMB21 | 275 | B-2-2c, B-3-2c | NGET | 53.228 | -0.79574 | K2 | K | T5 |  |  |  | HIGH MARNHAM SUBSTATION-B
HIMB41 | 400 | B-2-2c, B-3-2c | NGET | 53.228 | -0.79574 | K2 | K | T5 |  |  |  | HIGH MARNHAM SUBSTATION-B
HINP21 | 275 | B-3-1c | NGET | 51.2078 | -3.1277 | E7 | E | T9 |  | Double busbar | Outdoor | HINKLEY POINT
HINP22 | 275 | B-3-1c | NGET | 51.2078 | -3.1277 | E7 | E | T9 |  | Double busbar | Outdoor | HINKLEY POINT
HINP41 | 400 | B-2-1c, B-3-1c | NGET | 51.2078 | -3.1277 | E7 | E | T9 |  | Double busbar | Outdoor | HINKLEY POINT
HLND1- | 132 | B-2-2b, B-3-2b | SPT | 51.5069 | -3.1976 |  |  | T8 |  |  |  | HEATHLAND
HLND3- | 33 | B-3-2b | SPT | 51.5069 | -3.1976 |  |  | T8 |  |  |  | HEATHLAND
HOLM1- | 132 | B-2-2b | SPT | [8 empty] | HOLM HILL
HOLM1T | 132 | B-2-2b | SPT | [8 empty] | HOLM HILL
HORI1- | 132 | B-2-2b, B-3-2b | SPT | 58.2775 | -6.3083 |  |  | T1 |  |  |  | HOPSRIG COLLECTOR
HORI3A | 33 | B-3-2b | SPT | 58.2775 | -6.3083 |  |  | T1 |  |  |  | HOPSRIG COLLECTOR
HORI3B | 33 | B-3-2b | SPT | 58.2775 | -6.3083 |  |  | T1 |  |  |  | HOPSRIG COLLECTOR
HUCR4- | 400 | B-2-2b | SPT | 55.7199 | -4.8927 |  |  | T2 |  |  |  | HUNTERSTON CRYOBATTERY
HUCS4- | 400 | B-2-2b, B-4-1b | SPT | 55.7199 | -4.8927 |  |  | T2 |  |  |  | HUNTERSTON CONVERTER STATION
HUER4- | 400 | B-2-1b | SPT | 55.7199 | -4.8927 | S6 | S | T2 |  |  |  | HUNTERSTON
HUMR31 | 33 | B-3-1c | NGET | 53.6384 | -0.23849 | P7 | P | T4 |  | Double busbar | Indoor | HUMBER REFINERY
HUMR41 | 400 | B-2-1c, B-3-1c | NGET | 53.6384 | -0.23849 | P7 | P | T4 |  | Double busbar | Indoor | HUMBER REFINERY
HUNE1- | 132 | B-2-2b, B-3-2b | SPT | 55.7199 | -4.8883 |  |  | T2 |  |  |  | HUNTERSTON EAST
HUNE4- | 400 | B-2-1b, B-2-2b, B-3-2b, B-4-2b | SPT | 55.7199 | -4.8883 |  |  | T2 |  |  |  | HUNTERSTON EAST
HUNF1Q | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.7199 | -4.8927 |  |  | T2 |  |  |  | HUNTERSTON FARM
HUNF1R | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.7199 | -4.8927 |  |  | T2 |  |  |  | HUNTERSTON FARM
HUNF3- | 33 | B-3-1b | SPT | 55.7199 | -4.8927 |  |  | T2 |  |  |  | HUNTERSTON FARM
HUNN2A | 275 | B-2-1b, B-3-1b | SPT | 55.721 | -4.8864 |  |  | T2 |  |  |  | HUNTERSTON NORTH
HUNN2B | 275 | B-2-1b, B-3-1b | SPT | 55.721 | -4.8864 |  |  | T2 |  |  |  | HUNTERSTON NORTH
HUNN2C | 275 | B-2-1a, B-2-1b | SHET, SPT | 55.721 | -4.8864 |  |  | T2 |  |  |  | HUNTERSTON NORTH
HUNN2D | 275 | B-2-1a, B-2-1b | SHET, SPT | 55.721 | -4.8864 |  |  | T2 |  |  |  | HUNTERSTON NORTH
HUNN3W | 33 | B-4-1b | SPT | 55.721 | -4.8864 |  |  | T2 |  |  |  | HUNTERSTON NORTH
HUNN3X | 33 | B-4-1b | SPT | 55.721 | -4.8864 |  |  | T2 |  |  |  | HUNTERSTON NORTH
HUNN4A | 400 | B-2-1b, B-3-1b | SPT | 55.721 | -4.8864 |  |  | T2 |  |  |  | HUNTERSTON NORTH
HUNN4B | 400 | B-2-1b, B-3-1b | SPT | 55.721 | -4.8864 |  |  | T2 |  |  |  | HUNTERSTON NORTH
HURS1B | 132 | B-3-1c | NGET | 51.4327 | 0.1546 | A8 | A | T11 |  | Four Switch Mesh | Outdoor | HURST
HURS1C | 132 | B-3-1c | NGET | 51.4327 | 0.1546 | A8 | A | T11 |  | Four Switch Mesh | Outdoor | HURST
HURS1D | 132 | B-3-1c | NGET | 51.4327 | 0.1546 | A8 | A | T11 |  | Four Switch Mesh | Outdoor | HURST
HURS21 | 275 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 51.4327 | 0.1546 | A8 | A | T11 |  | Four Switch Mesh | Outdoor | HURST
HUTT11 | 132 | B-3-1c | NGET | 54.2975 | -2.6709 | R6 | R | T3 |  | Four Switch Mesh | Outdoor | HUTTON
HUTT41 | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 54.2975 | -2.6709 | R6 | R | T3 |  | Four Switch Mesh | Outdoor | HUTTON
HUTT42 | 400 | B-2-1c, B-2-2c | NGET | 54.2975 | -2.6709 | R6 | R | T3 |  | Four Switch Mesh | Outdoor | HUTTON
HUTT43 | 400 | B-2-1c, B-2-2c | NGET | 54.2975 | -2.6709 | R6 | R | T3 |  | Four Switch Mesh | Outdoor | HUTTON
HUTT71 | 25 | B-3-1c | NGET | 54.2975 | -2.6709 | R6 | R | T3 |  | Four Switch Mesh | Outdoor | HUTTON
IMPP31 | 33 | B-3-1c | NGET | 51.5479 | -3.0309 | H6 | H | T8 |  | Single Switch Mesh | Outdoor | IMPERIAL PARK
IMPP41 | 400 | B-2-1c, B-3-1c | NGET | 51.5479 | -3.0309 | H6 | H | T8 |  | Single Switch Mesh | Outdoor | IMPERIAL PARK
INCE11 | 132 | B-2-1c | NGET | 53.2778 | -2.8112 | N3 | N | T4 |  |  |  | INCE
INDQ11 | 132 | B-3-1c, B-4-1c | NGET | 50.395 | -4.8989 | F6 | F | T9 |  | Four Switch Mesh | Outdoor | INDIAN QUEENS
INDQ41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 50.395 | -4.8989 | F6 | F | T9 |  | Four Switch Mesh | Outdoor | INDIAN QUEENS
INGA1Q | 132 | B-2-2a, B-3-1a | SHET | 57.072 | -4.7737 |  |  | T1 |  |  |  | INVERGARRY
INGA5- | 11 | B-3-1a | SHET | 57.072 | -4.7737 |  |  | T1 |  |  |  | INVERGARRY
INKE1Q | 132 | B-2-2b, B-3-1b | SPT | 56.0424 | -3.3903 | S5 | S | T2 |  |  |  | INVERKEITHING
INKE1R | 132 | B-2-2b, B-3-1b | SPT | 56.0424 | -3.3903 | S5 | S | T2 |  |  |  | INVERKEITHING
INKE3- | 33 | B-3-1b | SPT | 56.0424 | -3.3903 | S5 | S | T2 |  |  |  | INVERKEITHING
INNE1J | 132 | B-2-1a, B-3-1a | SHET | 57.4536 | -4.2466 | T1 | T | T1 |  |  |  | INVERNESS
INNE1K | 132 | B-2-1a, B-3-1a | SHET | 57.4536 | -4.2466 | T1 | T | T1 |  |  |  | INVERNESS
INNE1L | 132 | B-2-1a, B-3-1a | SHET | 57.4536 | -4.2466 | T1 | T | T1 |  |  |  | INVERNESS
INNE1Q | 132 | B-2-1a | SHET | 57.4536 | -4.2466 | T1 | T | T1 |  |  |  | INVERNESS
INNE1R | 132 | B-2-1a | SHET | 57.4536 | -4.2466 | T1 | T | T1 |  |  |  | INVERNESS
INNE3- | 33 | B-3-1a | SHET | 57.4536 | -4.2466 | T1 | T | T1 |  |  |  | INVERNESS
INRU1Q | 132 | B-2-1a, B-2-2a | SHET | [8 empty] | INVERUGIE
INRU1R | 132 | B-2-1a, B-2-2a | SHET | [8 empty] | INVERUGIE
INRU1S | 132 | B-2-1a | SHET | [8 empty] | INVERUGIE
INVB2A | 275 | B-2-1b, B-3-1a | SHET, SPT | 56.3261 | -4.7245 |  |  | T1 |  |  |  | INVERARNAN BORDER NODE
INVB2B | 275 | B-2-1b, B-3-1a | SHET, SPT | 56.3261 | -4.7245 |  |  | T1 |  |  |  | INVERARNAN BORDER NODE
INVE1J | 132 | B-2-1a | SHET | 56.2624 | -5.0413 |  |  | T1 |  |  |  | INVERARAY
INVE1K | 132 | B-2-1a | SHET | 56.2624 | -5.0413 |  |  | T1 |  |  |  | INVERARAY
INVR1- | 132 | B-2-1a, B-3-1a | SHET | 56.3261 | -4.7245 |  |  | T1 |  |  |  | INVERARNAN
INVR1A | 132 | B-2-1a | SHET | 56.3261 | -4.7245 |  |  | T1 |  |  |  | INVERARNAN
INVR1B | 132 | B-2-1a | SHET | 56.3261 | -4.7245 |  |  | T1 |  |  |  | INVERARNAN
INVR1C | 132 | B-2-1a | SHET | 56.3261 | -4.7245 |  |  | T1 |  |  |  | INVERARNAN
INVR1D | 132 | B-2-1a | SHET | 56.3261 | -4.7245 |  |  | T1 |  |  |  | INVERARNAN
INVR2- | 275 | B-2-1b, B-2-2b | SPT | 56.3261 | -4.7245 |  |  | T1 |  |  |  | INVERARNAN
INWI1Q | 132 | B-2-2b | SPT | 58.442 | -3.1051 |  |  | T1 |  |  |  | INNERWICK
INWI1R | 132 | B-2-2b | SPT | 58.442 | -3.1051 |  |  | T1 |  |  |  | INNERWICK
IROA11 | 132 | B-2-1c, B-3-1c, B-4-1c | NGET | 51.5698 | -2.4807 | G5 | G | T8 |  | Double busbar | Outdoor | IRON ACTON
IROA12 | 132 | B-2-1c, B-3-1c | NGET | 51.5698 | -2.4807 | G5 | G | T8 |  | Double busbar | Outdoor | IRON ACTON
IROA13 | 132 | B-2-1c, B-3-1c | NGET | 51.5698 | -2.4807 | G5 | G | T8 |  | Double busbar | Outdoor | IRON ACTON
IROA21 | 275 | B-2-1c, B-3-1c | NGET | 51.5698 | -2.4807 | G5 | G | T8 |  | Double busbar | Outdoor | IRON ACTON
IRON11 | 132 | B-3-1c, B-4-1c | NGET | 52.632 | -2.5143 | L5 | L | T5 |  | Double busbar | Indoor | IRONBRIDGE
IRON12 | 132 | B-3-1c, B-4-1c | NGET | 52.632 | -2.5143 | L5 | L | T5 |  | Double busbar | Indoor | IRONBRIDGE
IRON13 | 132 | B-3-1c | NGET | 52.632 | -2.5143 | L5 | L | T5 |  | Double busbar | Indoor | IRONBRIDGE
IRON41 | 400 | B-2-1c, B-3-1c, B-4-1c, B-4-2c | NGET | 52.632 | -2.5143 | L5 | L | T5 |  | Double busbar | Indoor | IRONBRIDGE
ISLI11 | 132 | B-3-1c | NGET | 51.5494 | -0.11462 | A7 | A | T11 |  |  |  | ISLINGTON
IVER11 | 132 | B-3-1c | NGET | 51.5441 | -0.49887 | A6 | A | T11 |  | Double busbar | Outdoor | IVER
IVER21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 51.5441 | -0.49887 | A6 | A | T11 |  | Double busbar | Outdoor | IVER
IVER22 | 275 | B-2-1c, B-3-1c | NGET | 51.5441 | -0.49887 | A6 | A | T11 |  | Double busbar | Outdoor | IVER
IVER2A | 275 | B-2-1c, B-3-1c | NGET | 51.5441 | -0.49887 | A6 | A | T11 |  | Double busbar | Outdoor | IVER
IVER4A | 400 | B-2-2c, B-3-1c, B-4-1c | NGET | 51.5441 | -0.49887 | A6 | A | T11 |  | Double busbar | Outdoor | IVER
IVER4B | 400 | B-2-2c, B-3-1c, B-4-1c | NGET | 51.5441 | -0.49887 | A6 | A | T11 |  | Double busbar | Outdoor | IVER
IVER61 | 66 | B-3-1c | NGET | 51.5441 | -0.49887 | A6 | A | T11 |  | Double busbar | Outdoor | IVER
JOHN1Q | 132 | B-2-2b, B-3-1b | SPT | 55.8457 | -4.5064 | S6 | S | T2 |  |  |  | JOHNSTONE
JOHN1R | 132 | B-2-2b, B-3-1b | SPT | 55.8457 | -4.5064 | S6 | S | T2 |  |  |  | JOHNSTONE
JOHN3- | 33 | B-3-1b | SPT | 55.8457 | -4.5064 | S6 | S | T2 |  |  |  | JOHNSTONE
JORD21 | 275 | B-2-1c, B-3-1c | NGET | 53.3295 | -1.458 | P3 | P | T4 |  | Single Switch Mesh | Outdoor | JORDANTHORPE
JORD31 | 33 | B-3-1c, B-4-1c | NGET | 53.3295 | -1.458 | P3 | P | T4 |  | Single Switch Mesh | Outdoor | JORDANTHORPE
JUNA1T | 132 | B-2-1b, B-2-2b | SPT | [8 empty] | JUNCTION A
JUNB1- | 132 | B-2-2b | SPT | [8 empty] | JUNCTION B
JUNB1A | 132 | B-2-2b | SPT | [8 empty] | JUNCTION B
JUNV1- | 132 | B-2-2b | SPT | 54.9411 | -2.9616 | Q8 | Q | T3 |  |  |  | JUNCTION V
JUNV1A | 132 | B-2-2b | SPT | 54.9411 | -2.9616 | Q8 | Q | T3 |  |  |  | JUNCTION V
KAIM2- | 275 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.8926 | -3.166 | S6 | S | T2 |  |  |  | KAIMES
KAIM3- | 33 | B-2-1b | SPT | 55.8926 | -3.166 | S6 | S | T2 |  |  |  | KAIMES
KAIM3A | 33 | B-2-1b, B-3-1b | SPT | 55.8926 | -3.166 | S6 | S | T2 |  |  |  | KAIMES
KAIM3B | 33 | B-2-1b, B-3-1b | SPT | 55.8926 | -3.166 | S6 | S | T2 |  |  |  | KAIMES
KEAD11 | 132 | B-3-1c | NGET | 53.5981 | -0.75621 | P8 | P | T4 |  | Double busbar | Outdoor | KEADBY
KEAD41 | 400 | B-2-1c, B-2-2c, B-3-1c | NGET | 53.5981 | -0.75621 | P8 | P | T4 |  | Double busbar | Outdoor | KEADBY
KEAD42 | 400 | B-2-1c, B-3-1c | NGET | 53.5981 | -0.75621 | P8 | P | T4 |  | Double busbar | Outdoor | KEADBY
KEAD43 | 400 | B-2-1c | NGET | 53.5981 | -0.75621 | P8 | P | T4 |  | Double busbar | Outdoor | KEADBY
KEAD44 | 400 | B-2-1c | NGET | 53.5981 | -0.75621 | P8 | P | T4 |  | Double busbar | Outdoor | KEADBY
KEAD4C | 400 | B-2-2c, B-3-1c | NGET | 53.5981 | -0.75621 | P8 | P | T4 |  | Double busbar | Outdoor | KEADBY
KEAD4D | 400 | B-2-2c, B-3-1c | NGET | 53.5981 | -0.75621 | P8 | P | T4 |  | Double busbar | Outdoor | KEADBY
KEAR11 | 132 | B-3-1c, B-4-1c | NGET | 53.5373 | -2.3585 | N4 | N | T4 |  | Double busbar | Outdoor | KEARSLEY
KEAR21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 53.5373 | -2.3585 | N4 | N | T4 |  | Double busbar | Outdoor | KEARSLEY
KEAR31 | 33 | B-3-1c | NGET | 53.5373 | -2.3585 | N4 | N | T4 |  | Double busbar | Outdoor | KEARSLEY
KEAR41 | 400 | B-2-1c, B-3-1c | NGET | 53.5373 | -2.3585 | N4 | N | T4 |  | Double busbar | Outdoor | KEARSLEY
KEIH3- | 33 | B-2-2b | SPT | 57.5403 | -2.9396 |  |  | T1 |  |  |  | KEITHSHILL
KEIT1- | 132 | B-2-1a, B-3-1a | SHET | 57.5403 | -2.9396 | T1 | T | T1 |  |  |  | KEITH
KEIT1J | 132 | B-2-1a | SHET | 57.5403 | -2.9396 | T1 | T | T1 |  |  |  | KEITH
KEIT1K | 132 | B-2-1a | SHET | 57.5403 | -2.9396 | T1 | T | T1 |  |  |  | KEITH
KEIT2Q | 275 | B-2-1a, B-3-1a | SHET | 57.5403 | -2.9396 | T1 | T | T1 |  |  |  | KEITH
KEIT2R | 275 | B-2-1a, B-3-1a | SHET | 57.5403 | -2.9396 | T1 | T | T1 |  |  |  | KEITH
KEIT3- | 33 | B-2-1a, B-3-1a | SHET | 57.5403 | -2.9396 | T1 | T | T1 |  |  |  | KEITH
KEIT3A | 33 | B-2-1a, B-3-1a | SHET | 57.5403 | -2.9396 | T1 | T | T1 |  |  |  | KEITH
KEMS11 | 132 | B-3-1c | NGET | 51.3683 | 0.74147 | C3 | C | T11 |  | Double busbar | Outdoor | KEMSLEY
KEMS41 | 400 | B-2-1c, B-3-1c | NGET | 51.3683 | 0.74147 | C3 | C | T11 |  | Double busbar | Outdoor | KEMSLEY
KEMS4A | 400 | B-2-1c, B-3-1c | NGET | 51.3683 | 0.74147 | C3 | C | T11 |  | Double busbar | Outdoor | KEMSLEY
KEMS4B | 400 | B-2-1c, B-3-1c | NGET | 51.3683 | 0.74147 | C3 | C | T11 |  | Double busbar | Outdoor | KEMSLEY
KENE3- | 33 | B-3-1b | SPT | [8 empty] | KENNOXHEAD WINDFARM EXTENSION
KENG41 | 400 | B-2-1c | NGET | 51.5262 | -0.22404 | A7 | A | T11 |  | Double busbar | Outdoor | KENSAL GREEN
KENN1- | 132 | B-2-2b, B-3-1b | SPT | [8 empty] | KENNOXHEAD
KENN3- | 33 | B-3-1b | SPT | [8 empty] | KENNOXHEAD
KEOO1- | 132 | B-2-2b, B-3-1b | SPT | 55.1637 | -4.1914 | S6 | S | T2 |  |  |  | KENDOON
KEOO1Q | 132 | B-2-2b | SPT | 55.1637 | -4.1914 | S6 | S | T2 |  |  |  | KENDOON
KEOO5- | 11 | B-3-1b | SPT | 55.1637 | -4.1914 | S6 | S | T2 |  |  |  | KENDOON
KERG1- | 132 | B-2-1a | SHET | 60.295 | -1.2727 |  |  | T1 |  |  |  | KERGORD
KERG1A | 132 | B-2-2a | SHET | 60.295 | -1.2727 |  |  | T1 |  |  |  | KERGORD
KERG1B | 132 | B-2-2a | SHET | 60.295 | -1.2727 |  |  | T1 |  |  |  | KERGORD
KERG1J | 132 | B-2-1a, B-2-2a | SHET | 60.295 | -1.2727 |  |  | T1 |  |  |  | KERGORD
KERG1K | 132 | B-2-1a, B-2-2a | SHET | 60.295 | -1.2727 |  |  | T1 |  |  |  | KERGORD
KERG1L | 132 | B-2-2a | SHET | 60.295 | -1.2727 |  |  | T1 |  |  |  | KERGORD
KERG1M | 132 | B-2-2a | SHET | 60.295 | -1.2727 |  |  | T1 |  |  |  | KERGORD
KERG1N | 132 | B-2-2a | SHET | 60.295 | -1.2727 |  |  | T1 |  |  |  | KERGORD
KERG1P | 132 | B-2-1a | SHET | 60.295 | -1.2727 |  |  | T1 |  |  |  | KERGORD
KERG1Q | 132 | B-2-1a | SHET | 60.295 | -1.2727 |  |  | T1 |  |  |  | KERGORD
KERG1R | 132 | B-2-1a | SHET | 60.295 | -1.2727 |  |  | T1 |  |  |  | KERGORD
KERG1T | 132 | B-2-1a | SHET | 60.295 | -1.2727 |  |  | T1 |  |  |  | KERGORD
KERG1U | 132 | B-2-2a | SHET | 60.295 | -1.2727 |  |  | T1 |  |  |  | KERGORD
KERG1V | 132 | B-2-2a | SHET | 60.295 | -1.2727 |  |  | T1 |  |  |  | KERGORD
KERG1W | 132 | B-2-2a | SHET | 60.295 | -1.2727 |  |  | T1 |  |  |  | KERGORD
KIBY11 | 132 | B-3-1c, B-4-1c | NGET | 53.4692 | -2.8477 | N1 | N | T4 |  | Double busbar | Outdoor | KIRKBY
KIBY21 | 275 | B-2-1c, B-3-1c | NGET | 53.4692 | -2.8477 | N1 | N | T4 |  | Double busbar | Outdoor | KIRKBY
KIER1Q | 132 | B-2-1b, B-3-1b | SPT | 55.9036 | -4.3105 | S5 | S | T2 |  |  |  | KILLERMONT
KIER1R | 132 | B-2-1b, B-3-1b | SPT | 55.9036 | -4.3105 | S5 | S | T2 |  |  |  | KILLERMONT
KIER3- | 33 | B-3-1b | SPT | 55.9036 | -4.3105 | S5 | S | T2 |  |  |  | KILLERMONT
KIIN1- | 132 | B-2-1a, B-3-1a | SHET | 56.4774 | -4.3303 | T4 | T | T1 |  |  |  | KILLIN
KIIN3- | 33 | B-3-1a | SHET | 56.4774 | -4.3303 | T4 | T | T1 |  |  |  | KILLIN
KILB1Q | 132 | B-2-1b, B-3-1b | SPT | 55.9186 | -4.4107 |  |  | T2 |  |  |  | KILBOWIE
KILB1R | 132 | B-2-1b, B-3-1b | SPT | 55.9186 | -4.4107 |  |  | T2 |  |  |  | KILBOWIE
KILB3- | 33 | B-3-1b | SPT | 55.9186 | -4.4107 |  |  | T2 |  |  |  | KILBOWIE
KILB5- | 11 | B-3-1b | SPT | 55.9186 | -4.4107 |  |  | T2 |  |  |  | KILBOWIE
KILC1Q | 132 | B-2-1a, B-2-2a | SHET | 56.4774 | -4.3303 |  |  | T1 |  |  |  | KILLIN CASCADE GROUP
KILG2- | 275 | B-2-1b, B-3-1b, B-4-1b | SPT | 55.0501 | -4.7647 |  |  | T2 |  |  |  | KILGALLIOCH
KILG3A | 33 | B-3-1b | SPT | 55.0501 | -4.7647 |  |  | T2 |  |  |  | KILGALLIOCH
KILG3B | 33 | B-3-1b | SPT | 55.0501 | -4.7647 |  |  | T2 |  |  |  | KILGALLIOCH
KILG3C | 33 | B-3-1b | SPT | 55.0501 | -4.7647 |  |  | T2 |  |  |  | KILGALLIOCH
KILL41 | 400 | B-2-1c | NGET | 53.6557 | -0.25722 | P7 | P | T4 |  | Double busbar | Indoor | KILLINGHOLME
KILO1- | 132 | B-2-1a, B-3-1a | SHET | 56.1992 | -3.0397 |  |  | T2 |  |  |  | KINLOCHLEVEN
KILO3- | 33 | B-3-1a | SHET | 56.1992 | -3.0397 |  |  | T2 |  |  |  | KINLOCHLEVEN
KILS1- | 132 | B-2-1b, B-3-1b | SPT | 55.576 | -4.4657 | S6 | S | T2 |  |  |  | KILMARNOCK SOUTH
KILS2- | 275 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.576 | -4.4657 | S6 | S | T2 |  |  |  | KILMARNOCK SOUTH
KILS3- | 33 | B-3-1b | SPT | 55.576 | -4.4657 | S6 | S | T2 |  |  |  | KILMARNOCK SOUTH
KILS3U | 33 | B-4-1b | SPT | 55.576 | -4.4657 | S6 | S | T2 |  |  |  | KILMARNOCK SOUTH
KILS3X | 33 | B-4-1b | SPT | 55.576 | -4.4657 | S6 | S | T2 |  |  |  | KILMARNOCK SOUTH
KILS4- | 400 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.576 | -4.4657 | S6 | S | T2 |  |  |  | KILMARNOCK SOUTH
KILS4T | 400 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.576 | -4.4657 | S6 | S | T2 |  |  |  | KILMARNOCK SOUTH
KILT2Q | 275 | B-2-2b, B-3-1b | SPT | 55.5982 | -4.4955 | S6 | S | T2 |  |  |  | KILMARNOCK TOWN
KILT2R | 275 | B-2-2b, B-3-1b | SPT | 55.5982 | -4.4955 | S6 | S | T2 |  |  |  | KILMARNOCK TOWN
KILT3A | 33 | B-3-1b | SPT | 55.5982 | -4.4955 | S6 | S | T2 |  |  |  | KILMARNOCK TOWN
KILW1Q | 132 | B-2-1b, B-3-1b | SPT | 55.6648 | -4.6813 | S6 | S | T2 |  |  |  | KILWINNING
KILW1R | 132 | B-2-1b, B-3-1b | SPT | 55.6648 | -4.6813 | S6 | S | T2 |  |  |  | KILWINNING
KILW3- | 33 | B-3-1b | SPT | 55.6648 | -4.6813 | S6 | S | T2 |  |  |  | KILWINNING
KINA4A | 400 | B-2-2a, B-3-2a, B-4-2a | SHET | [8 empty] | KINARDOCHY
KINA4B | 400 | B-2-2a, B-3-2a, B-4-2a | SHET | [8 empty] | KINARDOCHY
KINB4J | 400 | B-2-2a, B-2-2b | SHET, SPT | 56.0749 | -3.7333 |  |  | T2 |  |  |  | KINCARDINE BORDER NODE
KINB4K | 400 | B-2-2a, B-2-2b | SHET, SPT | 56.0749 | -3.7333 |  |  | T2 |  |  |  | KINCARDINE BORDER NODE
KINC2- | 275 | B-2-1b, B-2-2b, B-4-2b | SPT | 56.0749 | -3.7333 |  |  | T2 |  |  |  | KINCARDINE
KINM2A | 275 | B-2-2a | SHET | [8 empty] | KINMUCK
KINM2B | 275 | B-2-2a | SHET | [8 empty] | KINMUCK
KINM2C | 275 | B-2-2a | SHET | [8 empty] | KINMUCK
KINN2A | 275 | B-2-2b, B-3-2b | SPT | 56.0749 | -3.7333 |  |  | T2 |  |  |  | KINCARDINE NORTH
KINN2B | 275 | B-2-2b, B-3-2b | SPT | 56.0749 | -3.7333 |  |  | T2 |  |  |  | KINCARDINE NORTH
KINN4- | 400 | B-2-2b, B-3-2b | SPT | 56.0749 | -3.7333 |  |  | T2 |  |  |  | KINCARDINE NORTH
KINO11 | 132 | B-3-1c | NGET | 51.4186 | 0.59839 | C2 | C | T11 |  | Double busbar | Indoor | KINGSNORTH
KINO41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 51.4186 | 0.59839 | C2 | C | T11 |  | Double busbar | Indoor | KINGSNORTH
KINT1- | 132 | B-2-1a, B-3-1a, B-3-2a, B-4-1a | SHET | 57.2197 | -2.3811 | T2 | T | T1 |  |  |  | KINTORE
KINT1B | 132 | B-2-1a, B-4-1a | SHET | 57.2197 | -2.3811 | T2 | T | T1 |  |  |  | KINTORE
KINT1P | 132 | B-2-1a | SHET | 57.2197 | -2.3811 | T2 | T | T1 |  |  |  | KINTORE
KINT1R | 132 | B-2-1a | SHET | 57.2197 | -2.3811 | T2 | T | T1 |  |  |  | KINTORE
KINT1T | 132 | B-2-1a | SHET | 57.2197 | -2.3811 | T2 | T | T1 |  |  |  | KINTORE
KINT1U | 132 | B-2-1a | SHET | 57.2197 | -2.3811 | T2 | T | T1 |  |  |  | KINTORE
KINT2J | 275 | B-2-1a, B-3-1a | SHET | 57.2197 | -2.3811 | T2 | T | T1 |  |  |  | KINTORE
KINT2K | 275 | B-2-1a, B-3-1a, B-3-2a | SHET | 57.2197 | -2.3811 | T2 | T | T1 |  |  |  | KINTORE
KINT3- | 33 | B-3-1a, B-3-2a | SHET | 57.2197 | -2.3811 | T2 | T | T1 |  |  |  | KINTORE
KINT3W | 33 | B-4-1a | SHET | 57.2197 | -2.3811 | T2 | T | T1 |  |  |  | KINTORE
KINT3Y | 33 | B-4-1a | SHET | 57.2197 | -2.3811 | T2 | T | T1 |  |  |  | KINTORE
KINT4J | 400 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.2197 | -2.3811 | T2 | T | T1 |  |  |  | KINTORE
KINT4K | 400 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.2197 | -2.3811 | T2 | T | T1 |  |  |  | KINTORE
KION1- | 132 | B-2-2a, B-3-2a | SHET | [8 empty] | KILMORACK NORTH
KION1A | 132 | B-2-2a | SHET | [8 empty] | KILMORACK NORTH
KION1B | 132 | B-2-2a | SHET | [8 empty] | KILMORACK NORTH
KION5- | 11 | B-3-2a | SHET | [8 empty] | KILMORACK NORTH
KIRK11 | 132 | B-3-1c | NGET | 53.8062 | -1.5981 | P1 | P | T4 |  | Four Switch Mesh | Outdoor | KIRKSTALL
KIRK21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 53.8062 | -1.5981 | P1 | P | T4 |  | Four Switch Mesh | Outdoor | KIRKSTALL
KIRK2A | 275 | B-2-1c, B-3-1c | NGET | 53.8062 | -1.5981 | P1 | P | T4 |  | Four Switch Mesh | Outdoor | KIRKSTALL
KITW11 | 132 | B-3-1c | NGET | 52.4308 | -2.0139 | L2 | L | T5 |  | Four Switch Mesh | Outdoor | KITWELL
KITW21 | 275 | B-2-1c, B-3-1c | NGET | 52.4308 | -2.0139 | L2 | L | T5 |  | Four Switch Mesh | Outdoor | KITWELL
KLYN41 | 400 | B-2-2c | NGET | 52.7267 | 0.37878 | J1 | J | T6 |  |  |  | KINGS LYNN
KNAR11 | 132 | B-3-1c | NGET | 54.0313 | -1.4878 | P2 | P | T4 |  | Single Switch Mesh | Outdoor | KNARESBOROUGH
KNAR21 | 275 | B-2-2c, B-3-1c | NGET | 54.0313 | -1.4878 | P2 | P | T4 |  | Single Switch Mesh | Outdoor | KNARESBOROUGH
KNOC1J | 132 | B-2-1a, B-3-1a | SHET | 57.4233 | -4.2461 |  |  | T1 |  |  |  | KNOCKNAGAEL
KNOC2J | 275 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.4233 | -4.2461 |  |  | T1 |  |  |  | KNOCKNAGAEL
KNOC2K | 275 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.4233 | -4.2461 |  |  | T1 |  |  |  | KNOCKNAGAEL
KNOC2L | 275 | B-2-1a | SHET | 57.4233 | -4.2461 |  |  | T1 |  |  |  | KNOCKNAGAEL
KNOC2M | 275 | B-2-1a | SHET | 57.4233 | -4.2461 |  |  | T1 |  |  |  | KNOCKNAGAEL
KNOC2N | 275 | B-2-1a | SHET | 57.4233 | -4.2461 |  |  | T1 |  |  |  | KNOCKNAGAEL
KNOC2P | 275 | B-2-1a | SHET | 57.4233 | -4.2461 |  |  | T1 |  |  |  | KNOCKNAGAEL
KNOK1- | 132 | B-2-2b, B-3-2b | SPT | [8 empty] | KNOCKODHAR
KNOK3- | 33 | B-3-2b | SPT | [8 empty] | KNOCKODHAR
KRKN1- | 132 | B-2-2a, B-3-2a | SHET | 55.89 | -3.536 |  |  | T2 |  |  |  | KIRKTON
KRKN3- | 33 | B-3-2a | SHET | 55.89 | -3.536 |  |  | T2 |  |  |  | KIRKTON
KYPE1- | 132 | B-2-1b, B-3-1b | SPT | [8 empty] | KYPE MUIR
KYPE3- | 33 | B-3-1b | SPT | [8 empty] | KYPE MUIR
KYPE3A | 33 | B-2-1b, B-3-1b | SPT | [8 empty] | KYPE MUIR
LACK21 | 275 | B-2-1c, B-3-1c | NGET | 54.567 | -1.1317 | Q2 | Q | T3 |  | Double busbar | Indoor | LACKENBY
LACK2A | 275 | B-2-1c, B-3-1c | NGET | 54.567 | -1.1317 | Q2 | Q | T3 |  | Double busbar | Indoor | LACKENBY
LACK2B | 275 | B-2-1c, B-3-1c | NGET | 54.567 | -1.1317 | Q2 | Q | T3 |  | Double busbar | Indoor | LACKENBY
LACK41 | 400 | B-2-1c, B-3-1c, B-4-2c | NGET | 54.567 | -1.1317 | Q2 | Q | T3 |  | Double busbar | Indoor | LACKENBY
LACK61 | 66 | B-3-1c | NGET | 54.567 | -1.1317 | Q2 | Q | T3 |  | Double busbar | Indoor | LACKENBY
LAGA41 | 400 | B-2-1c | NGET | 50.3891 | -4.0127 | F6 | F | T9 |  | Double busbar | Indoor | LANGAGE
LAGG1Q | 132 | B-2-1a | SHET | [8 empty] | LAGGAN
LAGG1R | 132 | B-2-1a | SHET | [8 empty] | LAGGAN
LAIR1- | 132 | B-2-1a, B-3-1a | SHET | 58.0304 | -4.3936 | T5 | T | T1 |  |  |  | LAIRG
LAIR3- | 33 | B-3-1a | SHET | 58.0304 | -4.3936 | T5 | T | T1 |  |  |  | LAIRG
LAIS1A | 132 | B-2-2a | SHET | 58.0304 | -4.3936 |  |  | T1 |  |  |  | LAIRG SOUTH
LAIS1B | 132 | B-2-2a, B-3-2a | SHET | 58.0304 | -4.3936 |  |  | T1 |  |  |  | LAIRG SOUTH
LAIS3- | 33 | B-3-2a | SHET | 58.0304 | -4.3936 |  |  | T1 |  |  |  | LAIRG SOUTH
LALE11 | 132 | B-3-1c | NGET | 51.4238 | -0.47062 | A6 | A | T11 |  | Double busbar | Indoor | LALEHAM
LALE21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 51.4238 | -0.47062 | A6 | A | T11 |  | Double busbar | Indoor | LALEHAM
LALE31 | 33 | B-3-1c | NGET | 51.4238 | -0.47062 | A6 | A | T11 |  | Double busbar | Indoor | LALEHAM
LAMB2- | 275 | B-2-1b, B-2-2b | SPT | 55.9038 | -4.2555 |  |  | T2 |  |  |  | LAMBHILL
LAMB4T | 400 | B-2-2b | SPT | 55.9038 | -4.2555 |  |  | T2 |  |  |  | LAMBHILL
LAND11 | 132 | B-3-1c, B-4-1c | NGET | 50.445 | -4.2426 | F6 | F | T9 |  | Single Switch Mesh | Outdoor | LANDULPH
LAND41 | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 50.445 | -4.2426 | F6 | F | T9 |  | Single Switch Mesh | Outdoor | LANDULPH
LAND42 | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 50.445 | -4.2426 | F6 | F | T9 |  | Single Switch Mesh | Outdoor | LANDULPH
LEGA11 | 132 | B-3-1c | NGET | 53.0285 | -3.0538 | M4 | M | T4 |  | Double busbar | Outdoor | LEGACY
LEGA41 | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 53.0285 | -3.0538 | M4 | M | T4 |  | Double busbar | Outdoor | LEGACY
LEGA4A | 400 | B-2-1c, B-3-1c | NGET | 53.0285 | -3.0538 | M4 | M | T4 |  | Double busbar | Outdoor | LEGACY
LEGA4B | 400 | B-2-1c, B-3-1c | NGET | 53.0285 | -3.0538 | M4 | M | T4 |  | Double busbar | Outdoor | LEGACY
LEGO1Q | 132 | B-2-2b, B-3-2b | SPT | 55.642 | -3.88 |  |  | T2 |  |  |  | LESMAHAGOW
LEGO1R | 132 | B-2-2b, B-3-2b | SPT | 55.642 | -3.88 |  |  | T2 |  |  |  | LESMAHAGOW
LEGO3- | 33 | B-3-2b | SPT | 55.642 | -3.88 |  |  | T2 |  |  |  | LESMAHAGOW
LEIB4A | 400 | B-2-1c | NGET | 51.9045 | -0.67766 | D4 | D | T6 |  | Four Switch Mesh | Outdoor | LEIGHTON BUZZARD
LEIB4B | 400 | B-2-1c | NGET | 51.9045 | -0.67766 | D4 | D | T6 |  | Four Switch Mesh | Outdoor | LEIGHTON BUZZARD
LEIS11 | 132 | B-2-1c, B-3-1c | NGET | 52.208 | 1.6112 | J2 | J | T7 |  | Double busbar | Indoor | LEISTON
LEIS4A | 400 | B-2-1c, B-3-1c | NGET | 52.208 | 1.6112 | J2 | J | T7 |  | Double busbar | Indoor | LEISTON
LEMR11 | 132 | B-2-1c, B-3-1c | NGET | 52.5287 | -1.7088 | L3 | L | T5 |  | Double busbar | Indoor | LEA MARSTON
LETH1- | 132 | B-2-2b, B-3-2b | SPT | [8 empty] | LETHANS
LETH3- | 33 | B-3-2b | SPT | [8 empty] | LETHANS
LEVE1Q | 132 | B-2-1b, B-3-1b | SPT | 56.1992 | -3.0397 | S5 | S | T2 |  |  |  | LEVEN
LEVE1R | 132 | B-2-1b, B-3-1b | SPT | 56.1992 | -3.0397 | S5 | S | T2 |  |  |  | LEVEN
LEVE3- | 33 | B-3-1b | SPT | 56.1992 | -3.0397 | S5 | S | T2 |  |  |  | LEVEN
LEVT1Q | 132 | B-2-1b | SPT | 56.1992 | -3.0397 |  |  | T2 |  |  |  | LEVEN TEE
LEVT1R | 132 | B-2-1b | SPT | 56.1992 | -3.0397 |  |  | T2 |  |  |  | LEVEN TEE
LHOR11 | 132 | B-3-2c | NGET | 50.9417 | 0.12071 | B1 | B | T11 |  |  |  | LITTLE HORSTED
LHOR4A | 400 | B-2-2c, B-3-2c | NGET | 50.9417 | 0.12071 | B1 | B | T11 |  |  |  | LITTLE HORSTED
LHOR4B | 400 | B-2-2c, B-3-2c | NGET | 50.9417 | 0.12071 | B1 | B | T11 |  |  |  | LITTLE HORSTED
LIMK1- | 132 | B-2-2a | SHET | [8 empty] | LIMEKILNS WINDFARM
LIMK1A | 132 | B-2-2a | SHET | [8 empty] | LIMEKILNS WINDFARM
LING1Q | 132 | B-2-1b, B-3-1b | SPT | 55.8828 | -3.4936 | S6 | S | T2 |  |  |  | LIVINGSTON
LING1R | 132 | B-2-1b, B-3-1b | SPT | 55.8828 | -3.4936 | S6 | S | T2 |  |  |  | LIVINGSTON
LING3- | 33 | B-3-1b | SPT | 55.8828 | -3.4936 | S6 | S | T2 |  |  |  | LIVINGSTON
LINM1Q | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.672 | -3.8271 | S6 | S | T2 |  |  |  | LINNMILL
LINM1R | 132 | B-2-1b, B-3-1b | SPT | 55.672 | -3.8271 | S6 | S | T2 |  |  |  | LINNMILL
LINM3- | 33 | B-3-1b | SPT | 55.672 | -3.8271 | S6 | S | T2 |  |  |  | LINNMILL
LISD11 | 132 | B-3-1c | NGET | 53.4186 | -2.9242 | N1 | N | T4 |  | Double busbar | Indoor | LISTER DRIVE
LISD21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 53.4186 | -2.9242 | N1 | N | T4 |  | Double busbar | Indoor | LISTER DRIVE
LISD2A | 275 | B-2-1c | NGET | 53.4186 | -2.9242 | N1 | N | T4 |  | Double busbar | Indoor | LISTER DRIVE
LITB11 | 132 | B-3-1c | NGET | 52.2049 | -0.26912 | J4 | J | T6 |  |  |  | LITTLE BARFORD
LITT11 | 132 | B-3-1c | NGET | 51.4647 | 0.23919 | A8 | A | T11 |  | Double busbar | Outdoor | LITTLEBROOK
LITT2A | 275 | B-2-1c, B-3-1c | NGET | 51.4647 | 0.23919 | A8 | A | T11 |  | Double busbar | Outdoor | LITTLEBROOK
LITT2B | 275 | B-2-1c, B-3-1c | NGET | 51.4647 | 0.23919 | A8 | A | T11 |  | Double busbar | Outdoor | LITTLEBROOK
LITT41 | 400 | B-2-1c, B-3-1c | NGET | 51.4647 | 0.23919 | A8 | A | T11 |  | Double busbar | Outdoor | LITTLEBROOK
LOAN2- | 275 | B-2-2b | SPT | 56.0505 | -3.6806 |  |  | T2 |  |  |  | LONGANNET
LOCB1J | 132 | B-2-1a, B-3-1a | SHET | 57.9508 | -4.2772 |  |  | T1 |  |  |  | LOCH BUIDHE
LOCB1K | 132 | B-2-1a, B-3-1a | SHET | 57.9508 | -4.2772 |  |  | T1 |  |  |  | LOCH BUIDHE
LOCB1L | 132 | B-2-1a | SHET | 57.9508 | -4.2772 |  |  | T1 |  |  |  | LOCH BUIDHE
LOCB1M | 132 | B-2-1a, B-2-2a | SHET | 57.9508 | -4.2772 |  |  | T1 |  |  |  | LOCH BUIDHE
LOCB1R | 132 | B-2-1a | SHET | 57.9508 | -4.2772 |  |  | T1 |  |  |  | LOCH BUIDHE
LOCB1S | 132 | B-2-1a | SHET | 57.9508 | -4.2772 |  |  | T1 |  |  |  | LOCH BUIDHE
LOCB1T | 132 | B-2-1a | SHET | 57.9508 | -4.2772 |  |  | T1 |  |  |  | LOCH BUIDHE
LOCB1U | 132 | B-2-1a | SHET | 57.9508 | -4.2772 |  |  | T1 |  |  |  | LOCH BUIDHE
LOCB2J | 275 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.9508 | -4.2772 |  |  | T1 |  |  |  | LOCH BUIDHE
LOCB2K | 275 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.9508 | -4.2772 |  |  | T1 |  |  |  | LOCH BUIDHE
LOCH1- | 132 | B-2-1a, B-3-1a | SHET | 56.4848 | -4.3639 |  |  | T1 |  |  |  | LOCHAY
LOCH5J | 11 | B-3-1a | SHET | 56.4848 | -4.3639 |  |  | T1 |  |  |  | LOCHAY
LOCH5K | 11 | B-3-1a | SHET | 56.4848 | -4.3639 |  |  | T1 |  |  |  | LOCHAY
LOCL1J | 132 | B-2-2a, B-3-2a | SHET | [8 empty] | LOCH LUNDIE
LOCL1K | 132 | B-2-2a, B-3-2a | SHET | [8 empty] | LOCH LUNDIE
LOCL4J | 400 | B-2-2a, B-3-2a | SHET | [8 empty] | LOCH LUNDIE
LOCL4K | 400 | B-2-2a, B-3-2a | SHET | [8 empty] | LOCH LUNDIE
LODR61 | 66 | B-3-1c, B-3-2c | NGET | 51.5275 | -0.16956 | A7 | A | T11 |  |  |  | LODGE ROAD
LODR62 | 66 | B-3-1c | NGET | 51.5275 | -0.16956 | A7 | A | T11 |  |  |  | LODGE ROAD
LOFI4A | 400 | B-2-1c | NGET | 51.3986 | 0.29875 | A8 | A | T11 |  |  |  | LONGFIELD
LOFI4B | 400 | B-2-1c | NGET | 51.3986 | 0.29875 | A8 | A | T11 |  |  |  | LONGFIELD
LORG1- | 132 | B-2-2b, B-3-2b | SPT | 55.2345 | -4.789 |  |  | T2 |  |  |  | LORG
LORG3- | 33 | B-3-2b | SPT | 55.2345 | -4.789 |  |  | T2 |  |  |  | LORG
LOVE11 | 132 | B-3-1c | NGET | 50.9174 | -1.04 | B2 | B | T10 |  | Double busbar | Outdoor | LOVEDEAN
LOVE12 | 132 | B-3-1c | NGET | 50.9174 | -1.04 | B2 | B | T10 |  | Double busbar | Outdoor | LOVEDEAN
LOVE41 | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 50.9174 | -1.04 | B2 | B | T10 |  | Double busbar | Outdoor | LOVEDEAN
LUIC1Q | 132 | B-2-1a, B-3-1a | SHET | 57.5758 | -4.6899 |  |  | T1 |  |  |  | LUICHART
LUIC1R | 132 | B-2-1a, B-3-1a | SHET | 57.5758 | -4.6899 |  |  | T1 |  |  |  | LUICHART
LUIC5J | 11 | B-3-1a | SHET | 57.5758 | -4.6899 |  |  | T1 |  |  |  | LUICHART
LUIC5K | 11 | B-3-1a | SHET | 57.5758 | -4.6899 |  |  | T1 |  |  |  | LUICHART
LUMB1Q | 132 | B-2-1a | SHET | [8 empty] | LUMBS
LUMB1R | 132 | B-2-1a | SHET | [8 empty] | LUMBS
LUNA1Q | 132 | B-2-1a, B-3-2a | SHET | 56.6543 | -2.8654 | T4 | T | T1 |  |  |  | LUNANHEAD
LUNA1R | 132 | B-2-1a, B-3-2a | SHET | 56.6543 | -2.8654 | T4 | T | T1 |  |  |  | LUNANHEAD
LUNA3- | 33 | B-3-2a | SHET | 56.6543 | -2.8654 | T4 | T | T1 |  |  |  | LUNANHEAD
LUND1- | 132 | B-2-1a | SHET | [8 empty] | LUNDAVRA
LYND1Q | 132 | B-2-1a, B-3-1a | SHET | 51.432 | 0.15647 | T4 | T | T1 |  |  |  | LYNDHURST
LYND1R | 132 | B-2-1a, B-3-1a | SHET | 51.432 | 0.15647 | T4 | T | T1 |  |  |  | LYNDHURST
LYND3- | 33 | B-3-1a | SHET | 51.432 | 0.15647 | T4 | T | T1 |  |  |  | LYNDHURST
MACC21 | 275 | B-2-1c, B-3-1c | NGET | 53.2687 | -2.1215 | N6 | N | T4 |  | Four Switch Mesh | Outdoor | MACCLESFIELD
MACC31 | 33 | B-3-1c | NGET | 53.2687 | -2.1215 | N6 | N | T4 |  | Four Switch Mesh | Outdoor | MACCLESFIELD
MACC41 | 400 | B-2-1c, B-3-1c | NGET | 53.2687 | -2.1215 | N6 | N | T4 |  | Four Switch Mesh | Outdoor | MACCLESFIELD
MACD1Q | 132 | B-2-1a, B-3-1a | SHET | 57.6639 | -2.4992 | T1 | T | T1 |  |  |  | MACDUFF
MACD1R | 132 | B-2-1a, B-3-1a | SHET | 57.6639 | -2.4992 | T1 | T | T1 |  |  |  | MACDUFF
MACD3- | 33 | B-3-1a, B-4-1a | SHET | 57.6639 | -2.4992 | T1 | T | T1 |  |  |  | MACDUFF
MAGA21 | 275 | B-2-1c, B-3-1c | NGET | 51.5629 | -3.7539 | H1 | H | T8 |  | Single Switch Mesh | Outdoor | MARGAM
MAHI1- | 132 | B-2-1b, B-3-1b | SPT | 55.1379 | -4.7681 |  |  | T2 |  |  |  | MARK HILL
MAHI1B | 132 | B-2-2b | SPT | 55.1379 | -4.7681 |  |  | T2 |  |  |  | MARK HILL
MAHI1C | 132 | B-2-2b, B-3-2b | SPT | 55.1379 | -4.7681 |  |  | T2 |  |  |  | MARK HILL
MAHI2- | 275 | B-2-1b, B-2-2b, B-3-1b, B-3-2b | SPT | 55.1379 | -4.7681 |  |  | T2 |  |  |  | MARK HILL
MAHI3- | 33 | B-2-2b, B-3-1b | SPT | 55.1379 | -4.7681 |  |  | T2 |  |  |  | MARK HILL
MAHI3U | 33 | B-4-1b | SPT | 55.1379 | -4.7681 |  |  | T2 |  |  |  | MARK HILL
MANN11 | 132 | B-3-1c, B-4-1c | NGET | 50.8469 | -1.896 | E1 | E | T9 |  | Four Switch Mesh | Outdoor | MANNINGTON
MANN41 | 400 | B-2-1c, B-3-1c, B-4-2c | NGET | 50.8469 | -1.896 | E1 | E | T9 |  | Four Switch Mesh | Outdoor | MANNINGTON
MARH41 | 400 | B-2-1c | NGET | 52.4647 | -0.88546 | J4 | J | T6 |  |  |  | MARKET HARBOROUGH
MARH42 | 400 | B-2-1c | NGET | 52.4647 | -0.88546 | J4 | J | T6 |  |  |  | MARKET HARBOROUGH
MARH4A | 400 | B-2-1c | NGET | 52.4647 | -0.88546 | J4 | J | T6 |  |  |  | MARKET HARBOROUGH
MARH4B | 400 | B-2-1c | NGET | 52.4647 | -0.88546 | J4 | J | T6 |  |  |  | MARKET HARBOROUGH
MARV41 | 400 | B-2-1c | NGET | 52.0568 | -0.52585 | J6 | J | T6 |  |  |  | MARSTON VALE
MARV4A | 400 | B-2-1c, B-2-2c | NGET | 52.0568 | -0.52585 | J6 | J | T6 |  |  |  | MARSTON VALE
MARV4B | 400 | B-2-1c, B-2-2c | NGET | 52.0568 | -0.52585 | J6 | J | T6 |  |  |  | MARSTON VALE
MAWO41 | 400 | B-2-1c | NGET | 50.8984 | -1.4402 | B2 | B | T10 |  | Double busbar | Indoor | MARCHWOOD
MAYB1- | 132 | B-2-1b, B-3-1b | SPT | 55.3423 | -4.6862 | S6 | S | T2 |  |  |  | MAYBOLE
MAYB3- | 33 | B-3-1b | SPT | 55.3423 | -4.6862 | S6 | S | T2 |  |  |  | MAYBOLE
MAYT1T | 132 | B-2-1b | SPT | 55.3423 | -4.6862 |  |  | T2 |  |  |  | MAYBOLE TEE
MEAD1- | 132 | B-2-1b | SPT | 55.5843 | -4.6388 |  |  | T2 |  |  |  | MEADOWHEAD
MEAD1Q | 132 | B-2-1b | SPT | 55.5843 | -4.6388 |  |  | T2 |  |  |  | MEADOWHEAD
MEAD1R | 132 | B-2-1b | SPT | 55.5843 | -4.6388 |  |  | T2 |  |  |  | MEADOWHEAD
MEDB4A | 400 | B-2-1c | NGET | 55.0287 | -1.7925 | Q6 | Q | T3 |  |  |  | MEDBURN TEE B
MEDB4B | 400 | B-2-1c | NGET | 55.0287 | -1.7925 | Q6 | Q | T3 |  |  |  | MEDBURN TEE B
MEDW41 | 400 | B-2-1c | NGET | 51.4401 | 0.69035 | C3 | C | T11 |  |  |  | MEDWAY
MELG1J | 132 | B-2-1a, B-3-1a | SHET | 57.0281 | -4.4723 |  |  | T1 |  |  |  | MELGARVE SUBSTATION
MELG1K | 132 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.0281 | -4.4723 |  |  | T1 |  |  |  | MELGARVE SUBSTATION
MELG4J | 400 | B-2-1a, B-3-1a, B-4-1a | SHET | 57.0281 | -4.4723 |  |  | T1 |  |  |  | MELGARVE SUBSTATION
MELG4K | 400 | B-2-1a, B-3-1a, B-4-1a | SHET | 57.0281 | -4.4723 |  |  | T1 |  |  |  | MELGARVE SUBSTATION
MELG8J | 22 | B-3-1a | SHET | 57.0281 | -4.4723 |  |  | T1 |  |  |  | MELGARVE SUBSTATION
MELG8K | 22 | B-3-1a | SHET | 57.0281 | -4.4723 |  |  | T1 |  |  |  | MELGARVE SUBSTATION
MELK11 | 132 | B-3-1c, B-4-1c | NGET | 51.3945 | -2.1508 | G6 | G | T8 |  | Teed Transformers | Outdoor | MELKSHAM
MELK2A | 275 | B-2-1c, B-3-1c | NGET | 51.3945 | -2.1508 | G6 | G | T8 |  | Teed Transformers | Outdoor | MELKSHAM
MELK2B | 275 | B-2-1c, B-3-1c | NGET | 51.3945 | -2.1508 | G6 | G | T8 |  | Teed Transformers | Outdoor | MELKSHAM
MELK41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c, B-4-2c | NGET | 51.3945 | -2.1508 | G6 | G | T8 |  | Teed Transformers | Outdoor | MELKSHAM
MEYG1- | 132 | B-2-2a | SHET | [8 empty] | MEYGEN
MFSN21 | 275 | B-2-2c, B-3-2c | NGET | 53.7563 | -1.2668 | P5 | P | T4 |  |  |  | MONK FRYSTON NEW
MFSN41 | 400 | B-2-2c | NGET | 53.7563 | -1.2668 | P5 | P | T4 |  |  |  | MONK FRYSTON NEW
MIDL41 | 400 | B-2-1c | NGET | 54.0253 | -2.8813 | R5 | R | T3 |  | Double busbar | Indoor | MIDDLETON
MIDM1- | 132 | B-2-2b, B-3-1b | SPT | [8 empty] | MIDDLE MUIR
MIDM3- | 33 | B-3-1b | SPT | [8 empty] | MIDDLE MUIR
MILC1R | 132 | B-2-1a, B-2-2a, B-3-1a | SHET | 56.4746 | -2.9246 | T4 | T | T1 |  |  |  | MILTON OF CRAIGIE
MILC1S | 132 | B-2-1a, B-3-1a | SHET | 56.4746 | -2.9246 | T4 | T | T1 |  |  |  | MILTON OF CRAIGIE
MILC1T | 132 | B-2-1a | SHET | 56.4746 | -2.9246 | T4 | T | T1 |  |  |  | MILTON OF CRAIGIE
MILC1V | 132 | B-2-1a, B-2-2a | SHET | 56.4746 | -2.9246 | T4 | T | T1 |  |  |  | MILTON OF CRAIGIE
MILC3- | 33 | B-3-1a | SHET | 56.4746 | -2.9246 | T4 | T | T1 |  |  |  | MILTON OF CRAIGIE
MILH11 | 132 | B-3-1c | NGET | 51.6179 | -0.20859 | A6 | A | T11 |  | Teed Transformers | Outdoor | MILL HILL
MILH12 | 132 | B-3-1c | NGET | 51.6179 | -0.20859 | A6 | A | T11 |  | Teed Transformers | Outdoor | MILL HILL
MILH2A | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 51.6179 | -0.20859 | A6 | A | T11 |  | Teed Transformers | Outdoor | MILL HILL
MILH2B | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 51.6179 | -0.20859 | A6 | A | T11 |  | Teed Transformers | Outdoor | MILL HILL
MILP31 | 33 | B-3-1c | NGET | 51.6196 | -1.2963 | D6 | D | T8 |  |  |  | MILTON PARK
MILW1Q | 132 | B-2-1a, B-3-1a | SHET | [8 empty] | MILLENIUM WIND
MILW1S | 132 | B-2-1a | SHET | [8 empty] | MILLENIUM WIND
MILW3- | 33 | B-3-1a | SHET | [8 empty] | MILLENIUM WIND
MINN3- | 33 | B-2-1b | SPT | 55.256 | -3.5251 |  |  | T2 |  |  |  | MINNYGAP
MITY11 | 132 | B-3-1c | NGET | 51.6078 | -2.0026 | G6 | G | T8 |  | Four Switch Mesh | Outdoor | MINETY
MITY12 | 132 | B-3-1c | NGET | 51.6078 | -2.0026 | G6 | G | T8 |  | Four Switch Mesh | Outdoor | MINETY
MITY41 | 400 | B-2-1c, B-2-2c, B-3-1c | NGET | 51.6078 | -2.0026 | G6 | G | T8 |  | Four Switch Mesh | Outdoor | MINETY
MOFF1- | 132 | B-2-2b, B-3-1b, B-3-2b | SPT | 55.3022 | -3.4267 |  |  | T2 |  |  |  | MOFFAT
MOFF1A | 132 | B-2-2b, B-3-2b | SPT | 55.3022 | -3.4267 |  |  | T2 |  |  |  | MOFFAT
MOFF3- | 33 | B-3-2b | SPT | 55.3022 | -3.4267 |  |  | T2 |  |  |  | MOFFAT
MOFF3A | 33 | B-2-1b, B-3-1b | SPT | 55.3022 | -3.4267 |  |  | T2 |  |  |  | MOFFAT
MOFF3U | 33 | B-4-1b | SPT | 55.3022 | -3.4267 |  |  | T2 |  |  |  | MOFFAT
MOFF4- | 400 | B-2-1b, B-3-1b, B-3-2b, B-4-1b | SPT | 55.3022 | -3.4267 |  |  | T2 |  |  |  | MOFFAT
MOFF4C | 400 | B-2-1b, B-2-2b | SPT | 55.3022 | -3.4267 |  |  | T2 |  |  |  | MOFFAT
MONF21 | 275 | B-2-1c, B-3-1c, B-3-2c, B-4-1c | NGET | 53.7563 | -1.2668 | P5 | P | T4 |  | Double busbar | Outdoor | MONK FRYSTON
MONF22 | 275 | B-2-1c, B-3-1c | NGET | 53.7563 | -1.2668 | P5 | P | T4 |  | Double busbar | Outdoor | MONK FRYSTON
MONF41 | 400 | B-2-1c, B-3-1c | NGET | 53.7563 | -1.2668 | P5 | P | T4 |  | Double busbar | Outdoor | MONK FRYSTON
MONF42 | 400 | B-3-2c | NGET | 53.7563 | -1.2668 | P5 | P | T4 |  | Double busbar | Outdoor | MONK FRYSTON
MONQ3- | 33 | B-2-2b | SPT | [8 empty] | MONQUHILL
MORF4- | 400 | B-2-1a | SHET | 57.4912 | -2.283 |  |  | T1 |  |  |  | MORAY EAST ONSHORE
MOSH1Q | 132 | B-2-1b, B-3-1b | SPT | 56.1062 | -3.2941 |  |  | T2 |  |  |  | MOSSMORRAN SHELL
MOSH1R | 132 | B-2-1b, B-3-1b | SPT | 56.1062 | -3.2941 |  |  | T2 |  |  |  | MOSSMORRAN SHELL
MOSH5J | 11 | B-3-1b | SPT | 56.1062 | -3.2941 |  |  | T2 |  |  |  | MOSSMORRAN SHELL
MOSH5K | 11 | B-3-1b | SPT | 56.1062 | -3.2941 |  |  | T2 |  |  |  | MOSSMORRAN SHELL
MOSM1A | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 56.1062 | -3.2941 |  |  | T2 |  |  |  | MOSSMORRAN
MOSM1B | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 56.1062 | -3.2941 |  |  | T2 |  |  |  | MOSSMORRAN
MOSM2- | 275 | B-2-1b, B-2-2b, B-3-1b | SPT | 56.1062 | -3.2941 |  |  | T2 |  |  |  | MOSSMORRAN
MOSM3Q | 33 | B-3-1b | SPT | 56.1062 | -3.2941 |  |  | T2 |  |  |  | MOSSMORRAN
MOSM3R | 33 | B-3-1b | SPT | 56.1062 | -3.2941 |  |  | T2 |  |  |  | MOSSMORRAN
MOSS1Q | 132 | B-2-1a, B-3-1a | SHET | 53.3864 | -3.0861 |  |  | T4 |  |  |  | MOSSFORD
MOSS1R | 132 | B-2-1a, B-3-1a | SHET | 53.3864 | -3.0861 |  |  | T4 |  |  |  | MOSSFORD
MOSS1S | 132 | B-2-1a | SHET | 53.3864 | -3.0861 |  |  | T4 |  |  |  | MOSSFORD
MOSS1T | 132 | B-2-1a | SHET | 53.3864 | -3.0861 |  |  | T4 |  |  |  | MOSSFORD
MOSS5- | 11 | B-3-1a | SHET | 53.3864 | -3.0861 |  |  | T4 |  |  |  | MOSSFORD
MOTA1Q | 132 | B-2-1a | SHET | [8 empty] | MOULTAIVE
MOTA1R | 132 | B-2-1a | SHET | [8 empty] | MOULTAIVE
MOWO4- | 400 | B-2-1a | SHET | [8 empty] | MORAY WEST ONSHORE
MSHL3- | 33 | B-3-2a | SHET | 53.3753 | -2.9224 |  |  | T4 |  |  |  | MOSSY HILL
MYBS1Q | 132 | B-2-1a | SHET | 58.4474 | -3.4251 | T5 | T | T1 |  |  |  | MYBSTER
MYBS1R | 132 | B-2-1a | SHET | 58.4474 | -3.4251 | T5 | T | T1 |  |  |  | MYBSTER
MYBS1S | 132 | B-2-1a, B-3-1a | SHET | 58.4474 | -3.4251 | T5 | T | T1 |  |  |  | MYBSTER
MYBS1T | 132 | B-2-1a, B-3-1a | SHET | 58.4474 | -3.4251 | T5 | T | T1 |  |  |  | MYBSTER
MYBS3J | 33 | B-3-1a | SHET | 58.4474 | -3.4251 | T5 | T | T1 |  |  |  | MYBSTER
MYBS3K | 33 | B-3-1a | SHET | 58.4474 | -3.4251 | T5 | T | T1 |  |  |  | MYBSTER
MYBS3M | 33 | B-2-1a, B-3-1a | SHET | 58.4474 | -3.4251 | T5 | T | T1 |  |  |  | MYBSTER
MYBS3N | 33 | B-2-1a, B-3-1a | SHET | 58.4474 | -3.4251 | T5 | T | T1 |  |  |  | MYBSTER
NAIR1Q | 132 | B-2-1a, B-3-1a | SHET | 57.5767 | -3.8476 | T1 | T | T1 |  |  |  | NAIRN
NAIR1R | 132 | B-2-1a, B-3-1a | SHET | 57.5767 | -3.8476 | T1 | T | T1 |  |  |  | NAIRN
NAIR3- | 33 | B-3-1a | SHET | 57.5767 | -3.8476 | T1 | T | T1 |  |  |  | NAIRN
NANT1Q | 132 | B-2-1a, B-3-1a | SHET | [8 empty] | NANT (LOCH NANT)
NANT5- | 11 | B-3-1a | SHET | [8 empty] | NANT (LOCH NANT)
NEAR2Q | 275 | B-2-1b, B-3-1b | SPT | 55.8248 | -3.9467 | S6 | S | T2 |  |  |  | NEWARTHILL
NEAR2R | 275 | B-2-1b, B-3-1b | SPT | 55.8248 | -3.9467 | S6 | S | T2 |  |  |  | NEWARTHILL
NEAR3- | 33 | B-3-1b | SPT | 55.8248 | -3.9467 | S6 | S | T2 |  |  |  | NEWARTHILL
NECH11 | 132 | B-3-1c | NGET | 52.5068 | -1.8524 | L3 | L | T5 |  | Four Switch Mesh | Outdoor | NECHELLS
NECH12 | 132 | B-3-1c | NGET | 52.5068 | -1.8524 | L3 | L | T5 |  | Four Switch Mesh | Outdoor | NECHELLS
NECH21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 52.5068 | -1.8524 | L3 | L | T5 |  | Four Switch Mesh | Outdoor | NECHELLS
NECT41 | 400 | B-2-2c | NGET | 52.6698 | 0.79929 | J3 | J | T7 |  | Double busbar | Outdoor | NECTON
NECU1- | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.3457 | -4.3346 |  |  | T2 |  |  |  | NEW CUMNOCK
NECU1B | 132 | B-2-2b, B-3-2b | SPT | 55.3457 | -4.3346 |  |  | T2 |  |  |  | NEW CUMNOCK
NECU1C | 132 | B-2-1b, B-2-2b, B-3-2b | SPT | 55.3457 | -4.3346 |  |  | T2 |  |  |  | NEW CUMNOCK
NECU2- | 275 | B-2-2b, B-3-1b, B-3-2b | SPT | 55.3457 | -4.3346 |  |  | T2 |  |  |  | NEW CUMNOCK
NEDE4J | 400 | B-2-1a, B-2-2a | SHET | 57.492 | -2.2845 |  |  | T1 |  |  |  | NEW DEER
NEDE4K | 400 | B-2-1a | SHET | 57.492 | -2.2845 |  |  | T1 |  |  |  | NEW DEER
NEEP21 | 275 | B-2-1c, B-3-1c | NGET | 53.4067 | -1.4885 | P3 | P | T4 |  | Teed Transformers | Outdoor | NEEPSEND
NEEP31 | 33 | B-3-1c | NGET | 53.4067 | -1.4885 | P3 | P | T4 |  | Teed Transformers | Outdoor | NEEPSEND
NEEP4A | 400 | B-2-1c, B-3-1c | NGET | 53.4067 | -1.4885 | P3 | P | T4 |  | Teed Transformers | Outdoor | NEEPSEND
NEIL1- | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.8083 | -4.4782 |  |  | T2 |  |  |  | NEILSTON
NEIL1C | 132 | B-2-1b, B-3-1b | SPT | 55.8083 | -4.4782 |  |  | T2 |  |  |  | NEILSTON
NEIL2- | 275 | B-2-1b, B-2-2b, B-3-1b, B-4-1b | SPT | 55.8083 | -4.4782 |  |  | T2 |  |  |  | NEILSTON
NEIL2C | 275 | B-2-1b, B-3-1b | SPT | 55.8083 | -4.4782 |  |  | T2 |  |  |  | NEILSTON
NEIL2D | 275 | B-2-2b, B-3-1b | SPT | 55.8083 | -4.4782 |  |  | T2 |  |  |  | NEILSTON
NEIL3U | 33 | B-4-1b | SPT | 55.8083 | -4.4782 |  |  | T2 |  |  |  | NEILSTON
NEIL3V | 33 | B-4-1b | SPT | 55.8083 | -4.4782 |  |  | T2 |  |  |  | NEILSTON
NEIL4Q | 400 | B-2-1b, B-3-1b | SPT | 55.8083 | -4.4782 |  |  | T2 |  |  |  | NEILSTON
NEIL4R | 400 | B-2-1b, B-3-1b | SPT | 55.8083 | -4.4782 |  |  | T2 |  |  |  | NEILSTON
NETH3- | 33 | B-2-2b | SPT | 53.4923 | -2.9703 |  |  | T4 |  |  |  | NETHERTON ENERGY
NETS1- | 132 | B-2-1b, B-2-2b, B-3-1b, B-3-2b | SPT | 54.9529 | -4.4992 | S6 | S | T2 |  |  |  | NEWTON STEWART
NETS3- | 33 | B-3-1b, B-3-2b | SPT | 54.9529 | -4.4992 | S6 | S | T2 |  |  |  | NEWTON STEWART
NEWX11 | 132 | B-3-1c | NGET | 51.4846 | -0.059541 | A4 | A | T11 |  | Double busbar | Outdoor | NEW CROSS
NEWX21 | 275 | B-2-2c, B-3-1c, B-3-2c, B-4-1c | NGET | 51.4846 | -0.059541 | A4 | A | T11 |  | Double busbar | Outdoor | NEW CROSS
NEWX41 | 400 | B-2-2c, B-3-2c | NGET | 51.4846 | -0.059541 | A4 | A | T11 |  | Double busbar | Outdoor | NEW CROSS
NEWX61 | 66 | B-3-1c | NGET | 51.4846 | -0.059541 | A4 | A | T11 |  | Double busbar | Outdoor | NEW CROSS
NEWX62 | 66 | B-3-1c | NGET | 51.4846 | -0.059541 | A4 | A | T11 |  | Double busbar | Outdoor | NEW CROSS
NFLE11 | 132 | B-3-1c | NGET | 51.4288 | 0.33031 | C2 | C | T11 |  | Double busbar | Indoor | NORTHFLEET EAST
NFLE12 | 132 | B-3-1c | NGET | 51.4288 | 0.33031 | C2 | C | T11 |  | Double busbar | Indoor | NORTHFLEET EAST
NFLE41 | 400 | B-2-1c, B-3-1c | NGET | 51.4288 | 0.33031 | C2 | C | T11 |  | Double busbar | Indoor | NORTHFLEET EAST
NHYD2A | 275 | B-2-1c, B-3-1c | NGET | 51.4999 | -0.4114 | A6 | A | T11 |  | Single Switch Mesh | Outdoor | NORTH HYDE
NHYD2B | 275 | B-2-1c, B-3-1c | NGET | 51.4999 | -0.4114 | A6 | A | T11 |  | Single Switch Mesh | Outdoor | NORTH HYDE
NHYD61 | 66 | B-3-1c | NGET | 51.4999 | -0.4114 | A6 | A | T11 |  | Single Switch Mesh | Outdoor | NORTH HYDE
NINF11 | 132 | B-3-1c | NGET | 50.8815 | 0.44775 | B1 | B | T11 |  | Double busbar | Outdoor | NINFIELD
NINF12 | 132 | B-3-1c | NGET | 50.8815 | 0.44775 | B1 | B | T11 |  | Double busbar | Outdoor | NINFIELD
NINF41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 50.8815 | 0.44775 | B1 | B | T11 |  | Double busbar | Outdoor | NINFIELD
NLEI1- | 132 | B-2-2b, B-3-2b | SPT | [8 empty] | NORTH LOWTHER ENERGY INITIATIVE
NLEI3A | 33 | B-3-2b | SPT | [8 empty] | NORTH LOWTHER ENERGY INITIATIVE
NLEI3B | 33 | B-3-2b | SPT | [8 empty] | NORTH LOWTHER ENERGY INITIATIVE
NOKY1- | 132 | B-2-1b, B-2-2b, B-3-2b | SPT | 57.281 | -5.7097 |  |  | T1 |  |  |  | NORTH KYLE
NOKY3A | 33 | B-3-2b | SPT | 57.281 | -5.7097 |  |  | T1 |  |  |  | NORTH KYLE
NOKY3B | 33 | B-3-2b | SPT | 57.281 | -5.7097 |  |  | T1 |  |  |  | NORTH KYLE
NORL2A | 275 | B-2-1c, B-3-1c | NGET | 53.3485 | -1.4715 | P3 | P | T4 |  | Teed Transformers | Outdoor | NORTON LEES
NORL2B | 275 | B-2-1c, B-3-1c | NGET | 53.3485 | -1.4715 | P3 | P | T4 |  | Teed Transformers | Outdoor | NORTON LEES
NORL31 | 33 | B-3-1c | NGET | 53.3485 | -1.4715 | P3 | P | T4 |  | Teed Transformers | Outdoor | NORTON LEES
NORM11 | 132 | B-3-1c | NGET | 52.5741 | 1.2719 | J3 | J | T7 |  | Double busbar | Outdoor | NORWICH MAIN
NORM12 | 132 | B-3-1c | NGET | 52.5741 | 1.2719 | J3 | J | T7 |  | Double busbar | Outdoor | NORWICH MAIN
NORM1A | 132 | B-3-1c | NGET | 52.5741 | 1.2719 | J3 | J | T7 |  | Double busbar | Outdoor | NORWICH MAIN
NORM1B | 132 | B-3-1c | NGET | 52.5741 | 1.2719 | J3 | J | T7 |  | Double busbar | Outdoor | NORWICH MAIN
NORM41 | 400 | B-2-1c, B-2-2c, B-3-1c | NGET | 52.5741 | 1.2719 | J3 | J | T7 |  | Double busbar | Outdoor | NORWICH MAIN
NORT11 | 132 | B-3-1c | NGET | 54.5928 | -1.3673 | Q4 | Q | T3 |  | Double busbar | Outdoor | NORTON
NORT21 | 275 | B-2-1c, B-3-1c | NGET | 54.5928 | -1.3673 | Q4 | Q | T3 |  | Double busbar | Outdoor | NORTON
NORT41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-2c | NGET | 54.5928 | -1.3673 | Q4 | Q | T3 |  | Double busbar | Outdoor | NORTON
NURS11 | 132 | B-3-1c | NGET | 50.9425 | -1.4867 | B2 | B | T10 |  | Single Switch Mesh | Outdoor | NURSLING
NURS41 | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 50.9425 | -1.4867 | B2 | B | T10 |  | Single Switch Mesh | Outdoor | NURSLING
NURS4A | 400 | B-2-1c, B-3-1c | NGET | 50.9425 | -1.4867 | B2 | B | T10 |  | Single Switch Mesh | Outdoor | NURSLING
OBST4A | 400 | B-2-2c | NGET | 53.9566 | -1.0226 | P6 | P | T4 |  |  |  | OSBALDWICK TEE
OBST4B | 400 | B-2-2c | NGET | 53.9566 | -1.0226 | P6 | P | T4 |  |  |  | OSBALDWICK TEE
OCKH11 | 132 | B-3-1c | NGET | 52.5419 | -2.0297 | L2 | L | T5 |  | Four Switch Mesh | Outdoor | OCKER HILL
OCKH21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 52.5419 | -2.0297 | L2 | L | T5 |  | Four Switch Mesh | Outdoor | OCKER HILL
OCKH2A | 275 | B-2-1c, B-3-1c | NGET | 52.5419 | -2.0297 | L2 | L | T5 |  | Four Switch Mesh | Outdoor | OCKER HILL
OFFE21 | 275 | B-2-1c, B-3-1c | NGET | 54.8808 | -1.458 | Q4 | Q | T3 |  | Single Switch Mesh | Outdoor | OFFERTON
OFFE31 | 33 | B-3-1c | NGET | 54.8808 | -1.458 | Q4 | Q | T3 |  | Single Switch Mesh | Outdoor | OFFERTON
OFFE32 | 33 | B-3-1c | NGET | 54.8808 | -1.458 | Q4 | Q | T3 |  | Single Switch Mesh | Outdoor | OFFERTON
OFOA1- | 132 | B-2-2b, B-3-2b | SPT | [8 empty] | OLD FOREST OF AE
OFOA1T | 132 | B-2-2b | SPT | [8 empty] | OLD FOREST OF AE
OFOA3- | 33 | B-3-2b | SPT | [8 empty] | OLD FOREST OF AE
OHLL1- | 132 | B-2-2b, B-3-2b | SPT | 53.1914 | -2.5383 | S6 | S | T2 |  |  |  | OVERHILL
OHLL3- | 33 | B-3-2b | SPT | 53.1914 | -2.5383 | S6 | S | T2 |  |  |  | OVERHILL
OLDB11 | 132 | B-3-1c | NGET | 52.4994 | -2.023 | L2 | L | T5 |  | Single Switch Mesh | Outdoor | OLDBURY
OLDB21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 52.4994 | -2.023 | L2 | L | T5 |  | Single Switch Mesh | Outdoor | OLDBURY
OLDB2A | 275 | B-2-1c, B-3-1c | NGET | 52.4994 | -2.023 | L2 | L | T5 |  | Single Switch Mesh | Outdoor | OLDBURY
OLDB4A | 400 | B-2-1c, B-3-1c | NGET | 52.4994 | -2.023 | L2 | L | T5 |  | Single Switch Mesh | Outdoor | OLDBURY
OLDS12 | 132 | B-2-1c | NGET | 51.6473 | -2.5719 | L2 | L | T8 |  |  |  | OLDBURY ON SEVERN
ORRI1Q | 132 | B-2-1a, B-3-1a | SHET | 51.383 | -2.1694 | T1 | T | T1 |  |  |  | ORRIN
ORRI1R | 132 | B-2-1a, B-3-1a | SHET | 51.383 | -2.1694 | T1 | T | T1 |  |  |  | ORRIN
ORRI1S | 132 | B-2-1a | SHET | 51.383 | -2.1694 | T1 | T | T1 |  |  |  | ORRIN
ORRI1T | 132 | B-2-1a | SHET | 51.383 | -2.1694 | T1 | T | T1 |  |  |  | ORRIN
ORRI3- | 33 | B-3-1a | SHET | 51.383 | -2.1694 | T1 | T | T1 |  |  |  | ORRIN
ORRI5- | 11 | B-3-1a | SHET | 51.383 | -2.1694 | T1 | T | T1 |  |  |  | ORRIN
OSBA11 | 132 | B-3-1c, B-3-2c | NGET | 53.9568 | -1.0225 | P6 | P | T4 |  | Four Switch Mesh | Outdoor | OSBALDWICK
OSBA41 | 400 | B-2-2c, B-3-1c | NGET | 53.9568 | -1.0225 | P6 | P | T4 |  | Four Switch Mesh | Outdoor | OSBALDWICK
OSBA42 | 400 | B-2-2c, B-3-1c, B-3-2c | NGET | 53.9568 | -1.0225 | P6 | P | T4 |  | Four Switch Mesh | Outdoor | OSBALDWICK
OVER21 | 275 | B-2-2c, B-3-2c | NGET | 54.0036 | -1.1561 | P6 | P | T4 |  |  |  | YORK NORTH (Overton)
OWFD1- | 132 | B-2-2a | SHET | [8 empty] | OWF-100
OWPL4- | 400 | B-2-2a | SHET | [8 empty] | OWPL WINDFARM
PADI11 | 132 | B-3-1c | NGET | 53.7954 | -2.3211 | N5 | N | T4 |  | Double busbar | Outdoor | PADIHAM
PADI41 | 400 | B-2-1c, B-3-1c | NGET | 53.7954 | -2.3211 | N5 | N | T4 |  | Double busbar | Outdoor | PADIHAM
PAFB4A | 400 | B-2-1c | NGET | 52.2916 | -1.0552 | L3 | L | T6 |  | Teed Transformers | Outdoor | PATFORD BRIDGE
PAFB4B | 400 | B-2-1c | NGET | 52.2916 | -1.0552 | L3 | L | T6 |  | Teed Transformers | Outdoor | PATFORD BRIDGE
PAIS1Q | 132 | B-2-1b | SPT | 55.8402 | -4.4126 | S6 | S | T2 |  |  |  | PAISLEY
PAIS1R | 132 | B-2-1b | SPT | 55.8402 | -4.4126 | S6 | S | T2 |  |  |  | PAISLEY
PAIS1S | 132 | B-2-1b, B-3-1b | SPT | 55.8402 | -4.4126 | S6 | S | T2 |  |  |  | PAISLEY
PAIS1T | 132 | B-2-1b, B-3-1b | SPT | 55.8402 | -4.4126 | S6 | S | T2 |  |  |  | PAISLEY
PAIS3- | 33 | B-3-1b | SPT | 55.8402 | -4.4126 | S6 | S | T2 |  |  |  | PAISLEY
PART1Q | 132 | B-2-1b, B-3-1b | SPT | 55.8694 | -4.3162 | S5 | S | T2 |  |  |  | PARTICK
PART1R | 132 | B-2-1b, B-3-1b | SPT | 55.8694 | -4.3162 | S5 | S | T2 |  |  |  | PARTICK
PART3- | 33 | B-3-1b | SPT | 55.8694 | -4.3162 | S5 | S | T2 |  |  |  | PARTICK
PEHE1- | 132 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.4741 | -1.7975 |  |  | T1 |  |  |  | PETERHEAD
PEHE2- | 275 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.4741 | -1.7975 |  |  | T1 |  |  |  | PETERHEAD
PEHE4J | 400 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.4741 | -1.7975 |  |  | T1 |  |  |  | PETERHEAD
PEHE4K | 400 | B-2-1a, B-3-1a | SHET | 57.4741 | -1.7975 |  |  | T1 |  |  |  | PETERHEAD
PEHE4L | 400 | B-2-2a | SHET | 57.4741 | -1.7975 |  |  | T1 |  |  |  | PETERHEAD
PEHG1Q | 132 | B-2-1a, B-3-1a | SHET | 57.5087 | -1.8063 | T2 | T | T1 |  |  |  | PETERHEAD GRANGE
PEHG1R | 132 | B-2-1a, B-3-1a | SHET | 57.5087 | -1.8063 | T2 | T | T1 |  |  |  | PETERHEAD GRANGE
PEHG3- | 33 | B-3-1a | SHET | 57.5087 | -1.8063 | T2 | T | T1 |  |  |  | PETERHEAD GRANGE
PEHS5- | 11 | B-3-1a | SHET | 57.4741 | -1.7975 | T2 | T | T1 |  |  |  | PETERHEAD SHELL
PELH11 | 132 | B-3-1c | NGET | 51.9351 | 0.11868 | D5 | D | T6 |  | Double busbar | Outdoor | PELHAM
PELH12 | 132 | B-3-1c | NGET | 51.9351 | 0.11868 | D5 | D | T6 |  | Double busbar | Outdoor | PELHAM
PELH41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-3-2c, B-4-1c | NGET | 51.9351 | 0.11868 | D5 | D | T6 |  | Double busbar | Outdoor | PELHAM
PELH4A | 400 | B-2-2c, B-3-2c | NGET | 51.9351 | 0.11868 | D5 | D | T6 |  | Double busbar | Outdoor | PELHAM
PEMB11 | 132 | B-3-1c | NGET | 51.6821 | -4.9905 | H6 | H | T8 |  | Double busbar | Indoor | PEMBROKE
PEMB41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 51.6821 | -4.9905 | H6 | H | T8 |  | Double busbar | Indoor | PEMBROKE
PENE11 | 132 | B-3-1c | NGET | 53.7463 | -2.7566 | R4 | R | T3 |  |  |  | PENWORTHAM EAST
PENI4A | 400 | B-2-2c | NGET | 53.1542 | -4.1777 | M6 | M | T4 |  |  |  | PENISARWAUN
PENN11 | 132 | B-3-1c | NGET | 52.5569 | -2.2098 | L1 | L | T5 |  | Four Switch Mesh | Outdoor | PENN
PENN21 | 275 | B-2-1c, B-3-1c | NGET | 52.5569 | -2.2098 | L1 | L | T5 |  | Four Switch Mesh | Outdoor | PENN
PENN4A | 400 | B-2-1c, B-3-1c | NGET | 52.5569 | -2.2098 | L1 | L | T5 |  | Four Switch Mesh | Outdoor | PENN
PENN4B | 400 | B-2-1c, B-3-1c | NGET | 52.5569 | -2.2098 | L1 | L | T5 |  | Four Switch Mesh | Outdoor | PENN
PENT11 | 132 | B-3-1c | NGET | 53.1876 | -4.158 | M6 | M | T4 |  | Double busbar | Outdoor | PENTIR
PENT41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 53.1876 | -4.158 | M6 | M | T4 |  | Double busbar | Outdoor | PENTIR
PENW11 | 132 | B-3-1c | NGET | 53.745 | -2.7581 | R4 | R | T3 |  | Teed Transformers | Outdoor | PENWORTHAM WEST
PERS1Q | 132 | B-2-1a, B-3-1a | SHET | 57.1747 | -2.1392 | T2 | T | T1 |  |  |  | PERSLEY
PERS1R | 132 | B-2-1a, B-3-1a | SHET | 57.1747 | -2.1392 | T2 | T | T1 |  |  |  | PERSLEY
PERS2Q | 275 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.1747 | -2.1392 | T2 | T | T1 |  |  |  | PERSLEY
PERS2R | 275 | B-2-1a, B-3-1a | SHET | 57.1747 | -2.1392 | T2 | T | T1 |  |  |  | PERSLEY
PERS3- | 33 | B-3-1a | SHET | 57.1747 | -2.1392 | T2 | T | T1 |  |  |  | PERSLEY
PEWO2A | 275 | B-2-1c, B-3-1c | NGET | 53.7433 | -2.7561 | R4 | R | T3 |  |  |  | PENWORTHAM
PEWO2B | 275 | B-2-1c, B-3-1c | NGET | 53.7433 | -2.7561 | R4 | R | T3 |  |  |  | PENWORTHAM
PEWO2C | 275 | B-2-1c | NGET | 53.7433 | -2.7561 | R4 | R | T3 |  |  |  | PENWORTHAM
PEWO2D | 275 | B-2-1c | NGET | 53.7433 | -2.7561 | R4 | R | T3 |  |  |  | PENWORTHAM
PEWO41 | 400 | B-2-1c, B-3-1c, B-4-1c, B-4-2c | NGET | 53.7433 | -2.7561 | R4 | R | T3 |  |  |  | PENWORTHAM
PEWO4A | 400 | B-2-1c, B-3-1c | NGET | 53.7433 | -2.7561 | R4 | R | T3 |  |  |  | PENWORTHAM
PEWO4B | 400 | B-2-1c, B-3-1c | NGET | 53.7433 | -2.7561 | R4 | R | T3 |  |  |  | PENWORTHAM
PITS21 | 275 | B-2-1c, B-2-2c, B-3-1c | NGET | 53.4007 | -1.4437 | P3 | P | T4 |  | Four Switch Mesh | Outdoor | PITSMOOR
PITS31 | 33 | B-3-1c, B-4-1c | NGET | 53.4007 | -1.4437 | P3 | P | T4 |  | Four Switch Mesh | Outdoor | PITSMOOR
PITS32 | 33 | B-3-1c | NGET | 53.4007 | -1.4437 | P3 | P | T4 |  | Four Switch Mesh | Outdoor | PITSMOOR
PLOE3- | 33 | B-2-2b | SPT | [8 empty] | PENCLOE
POAB11 | 132 | B-3-2c | NGET | 51.7478 | -4.0668 | H6 | H | T8 |  |  |  | PONT ABRAHAM
POAB41 | 400 | B-2-2c, B-3-2c | NGET | 51.7478 | -4.0668 | H6 | H | T8 |  |  |  | PONT ABRAHAM
POGB3- | 33 | B-2-2b | SPT | [8 empty] | POGBIE
POOB2Q | 275 | B-2-1b, B-3-1b | SPT | 55.954 | -3.125 | S6 | S | T2 |  |  |  | PORTOBELLO
POOB2R | 275 | B-2-1b, B-3-1b | SPT | 55.954 | -3.125 | S6 | S | T2 |  |  |  | PORTOBELLO
POOB3- | 33 | B-3-1b | SPT | 55.954 | -3.125 | S6 | S | T2 |  |  |  | PORTOBELLO
POPP21 | 275 | B-2-2c, B-3-1c | NGET | 53.9751 | -1.1317 | P2 | P | T4 |  | Single Switch Mesh | Outdoor | POPPLETON
POPP31 | 33 | B-3-1c | NGET | 53.9751 | -1.1317 | P2 | P | T4 |  | Single Switch Mesh | Outdoor | POPPLETON
PORA1S | 132 | B-2-1a | SHET | 56.0286 | -5.3567 | T3 | T | T1 |  |  |  | PORT ANN
PORA1U | 132 | B-2-1a | SHET | 56.0286 | -5.3567 | T3 | T | T1 |  |  |  | PORT ANN
PORD2Q | 275 | B-2-1b, B-3-1b | SPT | 55.8741 | -4.2557 | S5 | S | T2 |  |  |  | PORT DUNDAS
PORD2R | 275 | B-2-1b, B-3-2b | SPT | 55.8741 | -4.2557 | S5 | S | T2 |  |  |  | PORT DUNDAS
PORD3- | 33 | B-3-1b, B-3-2b | SPT | 55.8741 | -4.2557 | S5 | S | T2 |  |  |  | PORT DUNDAS
PORH11 | 132 | B-3-1c, B-4-1c | NGET | 51.8792 | -2.2539 | G1 | G | T8 |  |  |  | PORT HAM
PRST3A | 33 | B-2-1b | SPT | [8 empty] | PRIESTGILL
PUDM41 | 400 | B-2-1c | NGET | 51.5314 | -0.014417 | A1 | A | T11 |  | Single Switch Mesh | Indoor | PUDDING MILL LANE
PYLE11 | 132 | B-3-1c | NGET | 51.5359 | -3.6878 | H1 | H | T8 |  | Single Switch Mesh | Outdoor | PYLE
PYLE21 | 275 | B-2-1c, B-3-1c | NGET | 51.5359 | -3.6878 | H1 | H | T8 |  | Single Switch Mesh | Outdoor | PYLE
QUAN1- | 132 | B-2-2b, B-3-2b | SPT | [8 empty] | QUANTANS HILL
QUAN3- | 33 | B-3-2b | SPT | [8 empty] | QUANTANS HILL
QUER4A | 400 | B-2-1c | NGET | 54.047 | -2.7418 | R6 | R | T3 |  |  |  | QUERNMOOR
QUER4B | 400 | B-2-1c | NGET | 54.047 | -2.7418 | R6 | R | T3 |  |  |  | QUERNMOOR
QUOI1- | 132 | B-2-1a, B-3-1a | SHET | 57.0628 | -5.1235 | T1 | T | T1 |  |  |  | QUOICH
QUOI1Q | 132 | B-2-1a, B-2-2a | SHET | 57.0628 | -5.1235 | T1 | T | T1 |  |  |  | QUOICH
QUOI5- | 11 | B-3-1a | SHET | 57.0628 | -5.1235 | T1 | T | T1 |  |  |  | QUOICH
RAIN11 | 132 | B-3-1c, B-4-1c | NGET | 53.4212 | -2.7389 | N1 | N | T4 |  | Four Switch Mesh | Indoor | RAINHILL
RAIN12 | 132 | B-3-1c, B-4-1c | NGET | 53.4212 | -2.7389 | N1 | N | T4 |  | Four Switch Mesh | Indoor | RAINHILL
RAIN21 | 275 | B-2-1c, B-3-1c | NGET | 53.4212 | -2.7389 | N1 | N | T4 |  | Four Switch Mesh | Indoor | RAINHILL
RANN1Q | 132 | B-2-1a, B-3-1a | SHET | 56.6933 | -4.4015 | T4 | T | T1 |  |  |  | RANNOCH
RANN1R | 132 | B-2-1a, B-3-1a | SHET | 56.6933 | -4.4015 | T4 | T | T1 |  |  |  | RANNOCH
RANN3Q | 33 | B-3-1a | SHET | 56.6933 | -4.4015 | T4 | T | T1 |  |  |  | RANNOCH
RASS11 | 132 | B-3-1c | NGET | 51.8083 | -3.2267 | H6 | H | T8 |  | Single Switch Mesh | Outdoor | RASSAU
RASS41 | 400 | B-2-1c, B-3-1c | NGET | 51.8083 | -3.2267 | H6 | H | T8 |  | Single Switch Mesh | Outdoor | RASSAU
RATS11 | 132 | B-3-1c | NGET | 52.8638 | -1.256 | L7 | L | T5 |  | Double busbar | Indoor | RATCLIFFE-ON-SOAR
RATS12 | 132 | B-3-1c | NGET | 52.8638 | -1.256 | L7 | L | T5 |  | Double busbar | Indoor | RATCLIFFE-ON-SOAR
RATS2A | 275 | B-2-1c, B-3-1c | NGET | 52.8638 | -1.256 | L7 | L | T5 |  | Double busbar | Indoor | RATCLIFFE-ON-SOAR
RATS41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 52.8638 | -1.256 | L7 | L | T5 |  | Double busbar | Indoor | RATCLIFFE-ON-SOAR
RAVE3S | 33 | B-2-1b | SPT | [8 empty] | RAVENSCRAIG
RAVE3T | 33 | B-2-1b | SPT | [8 empty] | RAVENSCRAIG
RAYL41 | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 51.5941 | 0.56645 | C5 | C | T11 |  | Double busbar | Outdoor | RAYLEIGH
RAYM11 | 132 | B-3-1c | NGET | 51.5937 | 0.5685 | C5 | C | T11 |  |  |  | RAYLEIGH MAIN
REBR21 | 275 | B-2-1c, B-3-1c | NGET | 51.5885 | 0.042994 | A1 | A | T11 |  | Single Switch Mesh | Outdoor | REDBRIDGE
REBR22 | 275 | B-2-1c, B-3-1c | NGET | 51.5885 | 0.042994 | A1 | A | T11 |  | Single Switch Mesh | Outdoor | REDBRIDGE
REBR31 | 33 | B-3-1c | NGET | 51.5885 | 0.042994 | A1 | A | T11 |  | Single Switch Mesh | Outdoor | REDBRIDGE
REBR32 | 33 | B-3-1c | NGET | 51.5885 | 0.042994 | A1 | A | T11 |  | Single Switch Mesh | Outdoor | REDBRIDGE
REDH1- | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 56.1461 | -3.1461 | S5 | S | T2 |  |  |  | REDHOUSE
REDH3- | 33 | B-3-1b | SPT | 56.1461 | -3.1461 | S5 | S | T2 |  |  |  | REDHOUSE
REDM1Q | 132 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.1085 | -2.0922 | T2 | T | T1 |  |  |  | REDMOSS
REDM1R | 132 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.1085 | -2.0922 | T2 | T | T1 |  |  |  | REDMOSS
REDM3- | 33 | B-3-1a | SHET | 57.1085 | -2.0922 | T2 | T | T1 |  |  |  | REDMOSS
REDS1A | 132 | B-2-2b, B-3-2b | SPT | [8 empty] | REDSHAW
REDS3A | 33 | B-3-2b | SPT | [8 empty] | REDSHAW
REDS4- | 400 | B-2-2b, B-3-2b | SPT | [8 empty] | REDSHAW
RHIG41 | 400 | B-2-1c | NGET | 51.7466 | -3.545 | H6 | H | T8 |  | Double busbar | Outdoor | RHIGOS
RICH11 | 132 | B-3-1c | NGET | 51.3115 | 1.3441 | C7 | C | T11 |  |  |  | RICHBOROUGH
RICH41 | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 51.3115 | 1.3441 | C7 | C | T11 |  |  |  | RICHBOROUGH
ROCH11 | 132 | B-3-1c, B-4-1c | NGET | 53.6219 | -2.2168 | N4 | N | T4 |  | Single Switch Mesh | Outdoor | ROCHDALE
ROCH12 | 132 | B-3-1c | NGET | 53.6219 | -2.2168 | N4 | N | T4 |  | Single Switch Mesh | Outdoor | ROCHDALE
ROCH21 | 275 | B-2-1c, B-3-1c | NGET | 53.6219 | -2.2168 | N4 | N | T4 |  | Single Switch Mesh | Outdoor | ROCHDALE
ROCH4A | 400 | B-2-1c, B-3-1c | NGET | 53.6219 | -2.2168 | N4 | N | T4 |  | Single Switch Mesh | Outdoor | ROCHDALE
ROCK1A | 132 | B-3-1c | NGET | 53.315 | -2.725 | N3 | N | T4 |  | Single Switch Mesh | Outdoor | ROCKSAVAGE
ROCK41 | 400 | B-2-1c, B-3-1c | NGET | 53.315 | -2.725 | N3 | N | T4 |  | Single Switch Mesh | Outdoor | ROCKSAVAGE
ROTI3- | 33 | B-3-1a | SHET | 57.4082 | -2.5159 | T2 | T | T1 |  |  |  | ROTHIENORMAN
ROTI4J | 400 | B-2-1a, B-3-1a | SHET | 57.4082 | -2.5159 | T2 | T | T1 |  |  |  | ROTHIENORMAN
ROTI4K | 400 | B-2-1a, B-3-1a | SHET | 57.4082 | -2.5159 | T2 | T | T1 |  |  |  | ROTHIENORMAN
ROWD41 | 400 | B-2-1c, B-4-2c | NGET | 51.3519 | -0.0035626 | A8 | A | T11 |  | Single Switch Mesh | Outdoor | ROWDOWN
ROWD42 | 400 | B-2-1c | NGET | 51.3519 | -0.0035626 | A8 | A | T11 |  | Single Switch Mesh | Outdoor | ROWDOWN
RUGE11 | 132 | B-3-1c | NGET | 52.7567 | -1.915 | L5 | L | T5 |  | Double busbar | Indoor | RUGELEY
RUGE41 | 400 | B-2-1c, B-3-1c | NGET | 52.7567 | -1.915 | L5 | L | T5 |  | Double busbar | Indoor | RUGELEY
RYEH11 | 132 | B-3-1c | NGET | 51.759 | 0.0085411 | A9 | A | T11 |  | Double busbar | Outdoor | RYE HOUSE
RYEH12 | 132 | B-3-1c | NGET | 51.759 | 0.0085411 | A9 | A | T11 |  | Double busbar | Outdoor | RYE HOUSE
RYEH13 | 132 | B-3-1c | NGET | 51.759 | 0.0085411 | A9 | A | T11 |  | Double busbar | Outdoor | RYE HOUSE
RYEH41 | 400 | B-2-2c, B-3-1c, B-4-1c | NGET | 51.759 | 0.0085411 | A9 | A | T11 |  | Double busbar | Outdoor | RYE HOUSE
RYEH42 | 400 | B-2-1c, B-3-1c | NGET | 51.759 | 0.0085411 | A9 | A | T11 |  | Double busbar | Outdoor | RYE HOUSE
RYEH43 | 400 | B-2-1c, B-3-1c | NGET | 51.759 | 0.0085411 | A9 | A | T11 |  | Double busbar | Outdoor | RYE HOUSE
RYEH4A | 400 | B-2-1c, B-2-2c | NGET | 51.759 | 0.0085411 | A9 | A | T11 |  | Double busbar | Outdoor | RYE HOUSE
RYEH4B | 400 | B-2-1c, B-2-2c | NGET | 51.759 | 0.0085411 | A9 | A | T11 |  | Double busbar | Outdoor | RYE HOUSE
RYHA4A | 400 | B-2-1c | NGET | 52.6866 | -0.45843 | J7 | J | T6 |  | Teed Transformers | Outdoor | RYHALL
RYHA4B | 400 | B-2-1c | NGET | 52.6866 | -0.45843 | J7 | J | T6 |  | Teed Transformers | Outdoor | RYHALL
SACO1Q | 132 | B-2-1b, B-3-1b | SPT | 55.6467 | -4.7966 |  |  | T2 |  |  |  | SALTCOATS
SACO1R | 132 | B-2-1b, B-3-1b | SPT | 55.6467 | -4.7966 |  |  | T2 |  |  |  | SALTCOATS
SACO3J | 33 | B-3-1b | SPT | 55.6467 | -4.7966 |  |  | T2 |  |  |  | SALTCOATS
SACO3K | 33 | B-3-1b | SPT | 55.6467 | -4.7966 |  |  | T2 |  |  |  | SALTCOATS
SAEN11 | 132 | B-3-1c | NGET | 53.742 | -0.2385 | P8 | P | T4 |  | Single Switch Mesh | Outdoor | SALTEND NORTH
SAEN21 | 275 | B-2-1c, B-3-1c | NGET | 53.742 | -0.2385 | P8 | P | T4 |  | Single Switch Mesh | Outdoor | SALTEND NORTH
SAES21 | 275 | B-2-1c | NGET | 53.7372 | -0.2429 | P8 | P | T4 |  | Double busbar | Outdoor | SALTEND SOUTH
SAFO11 | 132 | B-3-1c | NGET | 51.3393 | -2.8413 | G7 | G | T9 |  |  |  | SANDFORD
SAFO41 | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 51.3393 | -2.8413 | G7 | G | T9 |  |  |  | SANDFORD
SAKN1- | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | [8 empty] | SANDY KNOWE
SAKN3- | 33 | B-3-1b | SPT | [8 empty] | SANDY KNOWE
SALH11 | 132 | B-3-1c | NGET | 54.6055 | -1.2378 | Q2 | Q | T3 |  | Single Switch Mesh | Outdoor | SALTHOLME
SALH21 | 275 | B-2-1c, B-3-1c | NGET | 54.6055 | -1.2378 | Q2 | Q | T3 |  | Single Switch Mesh | Outdoor | SALTHOLME
SALH41 | 400 | B-2-1c, B-2-2c | NGET | 54.6055 | -1.2378 | Q2 | Q | T3 |  | Single Switch Mesh | Outdoor | SALTHOLME
SALH42 | 400 | B-2-1c, B-2-2c | NGET | 54.6055 | -1.2378 | Q2 | Q | T3 |  | Single Switch Mesh | Outdoor | SALTHOLME
SALM1A | 132 | B-2-2a | SHET | [8 empty] | SALAMANDER OFFSHORE WIND FARM
SALM1B | 132 | B-2-2a | SHET | [8 empty] | SALAMANDER OFFSHORE WIND FARM
SALM1C | 132 | B-2-2a | SHET | [8 empty] | SALAMANDER OFFSHORE WIND FARM
SANQ1- | 132 | B-2-2b | SPT | [8 empty] | SANQUHAR II WIND FARM
SANX1Q | 132 | B-2-1b, B-3-1b | SPT | 51.9219 | -2.5903 | S6 | S | T2 |  |  |  | ST ANDREWS CROSS
SANX1R | 132 | B-2-1b, B-3-1b | SPT | 51.9219 | -2.5903 | S6 | S | T2 |  |  |  | ST ANDREWS CROSS
SANX3- | 33 | B-3-1b | SPT | 51.9219 | -2.5903 | S6 | S | T2 |  |  |  | ST ANDREWS CROSS
SASA11 | 132 | B-3-1c | NGET | 53.2516 | -3.4773 | M6 | M | T4 |  |  |  | ST ASAPHS
SCOP1- | 132 | B-2-2b | SPT | [8 empty] | SCOOP HILL WIND FARM
SCOP1A | 132 | B-2-2b | SPT | [8 empty] | SCOOP HILL WIND FARM
SEAB11 | 132 | B-3-1c | NGET | 51.5371 | -2.67 | G7 | G | T8 |  | Double busbar | Indoor | SEABANK
SEAB41 | 400 | B-2-1c, B-3-1c | NGET | 51.5371 | -2.67 | G7 | G | T8 |  | Double busbar | Indoor | SEABANK
SELL11 | 132 | B-3-1c | NGET | 51.1065 | 0.9761 | C4 | C | T11 |  | Double busbar | Indoor | SELLINDGE
SELL12 | 132 | B-3-1c | NGET | 51.1065 | 0.9761 | C4 | C | T11 |  | Double busbar | Indoor | SELLINDGE
SELL13 | 132 | B-3-1c | NGET | 51.1065 | 0.9761 | C4 | C | T11 |  | Double busbar | Indoor | SELLINDGE
SELL4A | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 51.1065 | 0.9761 | C4 | C | T11 |  | Double busbar | Indoor | SELLINDGE
SELL4B | 400 | B-2-1c | NGET | 51.1065 | 0.9761 | C4 | C | T11 |  | Double busbar | Indoor | SELLINDGE
SELL4C | 400 | B-2-1c | NGET | 51.1065 | 0.9761 | C4 | C | T11 |  | Double busbar | Indoor | SELLINDGE
SELL4D | 400 | B-2-1c | NGET | 51.1065 | 0.9761 | C4 | C | T11 |  | Double busbar | Indoor | SELLINDGE
SELL4E | 400 | B-2-1c | NGET | 51.1065 | 0.9761 | C4 | C | T11 |  | Double busbar | Indoor | SELLINDGE
SELL4F | 400 | B-2-1c | NGET | 51.1065 | 0.9761 | C4 | C | T11 |  | Double busbar | Indoor | SELLINDGE
SFEE1A | 132 | B-2-1a | SHET | 57.5754 | -1.8555 |  |  | T1 |  |  |  | ST FERGUS EAST
SFEE1B | 132 | B-2-1a | SHET | 57.5754 | -1.8555 |  |  | T1 |  |  |  | ST FERGUS EAST
SFEE1C | 132 | B-2-1a, B-3-1a | SHET | 57.5754 | -1.8555 |  |  | T1 |  |  |  | ST FERGUS EAST
SFEE1D | 132 | B-2-1a, B-3-1a | SHET | 57.5754 | -1.8555 |  |  | T1 |  |  |  | ST FERGUS EAST
SFEE5- | 11 | B-3-1a | SHET | 57.5754 | -1.8555 |  |  | T1 |  |  |  | ST FERGUS EAST
SFEG1Q | 132 | B-2-1a | SHET | 57.5741 | -1.8491 | T2 | T | T1 |  |  |  | ST FERGUS GAS TERMINAL
SFEG1R | 132 | B-2-1a | SHET | 57.5741 | -1.8491 | T2 | T | T1 |  |  |  | ST FERGUS GAS TERMINAL
SFEM1Q | 132 | B-2-1a | SHET | 57.5657 | -1.8805 |  |  | T1 |  |  |  | ST FERGUS MOBIL
SFEM1R | 132 | B-2-1a | SHET | 57.5657 | -1.8805 |  |  | T1 |  |  |  | ST FERGUS MOBIL
SFER1J | 132 | B-2-1a | SHET | 57.5741 | -1.8491 |  |  | T1 |  |  |  | ST FERGUS
SFER1K | 132 | B-2-1a | SHET | 57.5741 | -1.8491 |  |  | T1 |  |  |  | ST FERGUS
SFER1L | 132 | B-2-1a, B-2-2a | SHET | 57.5741 | -1.8491 |  |  | T1 |  |  |  | ST FERGUS
SFER1M | 132 | B-2-1a, B-2-2a | SHET | 57.5741 | -1.8491 |  |  | T1 |  |  |  | ST FERGUS
SFEV1S | 132 | B-2-1a | SHET | 57.5657 | -1.8805 |  |  | T1 |  |  |  | ST FERGUS VSD
SFEV1T | 132 | B-2-1a | SHET | 57.5657 | -1.8805 |  |  | T1 |  |  |  | ST FERGUS VSD
SFIL1Q | 132 | B-2-1a, B-3-2a | SHET | 56.3959 | -4.1171 | T4 | T | T1 |  |  |  | ST FILLANS
SFIL5- | 11 | B-3-2a | SHET | 56.3959 | -4.1171 | T4 | T | T1 |  |  |  | ST FILLANS
SGRX2- | 275 | B-2-1a | SHET | [8 empty] | SEAGREEN ONE 275KV ONSHORE
SHBA41 | 400 | B-2-1c | NGET | 53.6014 | -0.14626 | P7 | P | T4 |  | Double busbar | Indoor | SOUTH HUMBER BANK
SHEC21 | 275 | B-2-1c, B-3-1c | NGET | 53.3747 | -1.4786 | P3 | P | T4 |  | Single Switch Mesh | Indoor | SHEFFIELD CITY
SHEC31 | 33 | B-3-1c | NGET | 53.3747 | -1.4786 | P3 | P | T4 |  | Single Switch Mesh | Indoor | SHEFFIELD CITY
SHEE11 | 132 | B-3-1c | NGET | 51.4346 | 0.76713 | C3 | C | T11 |  |  |  | SHEERNESS
SHIN1- | 132 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.9436 | -4.4143 | T5 | T | T1 |  |  |  | SHIN
SHIN3- | 33 | B-3-1a | SHET | 57.9436 | -4.4143 | T5 | T | T1 |  |  |  | SHIN
SHIN5- | 11 | B-3-1a | SHET | 57.9436 | -4.4143 | T5 | T | T1 |  |  |  | SHIN
SHRE11 | 132 | B-3-1c | NGET | 52.709 | -2.6928 | L5 | L | T5 |  | Teed Transformers | Outdoor | SHREWSBURY
SHRE4A | 400 | B-2-1c | NGET | 52.709 | -2.6928 | L5 | L | T5 |  | Teed Transformers | Outdoor | SHREWSBURY
SHRE4B | 400 | B-2-1c, B-3-1c | NGET | 52.709 | -2.6928 | L5 | L | T5 |  | Teed Transformers | Outdoor | SHREWSBURY
SHRG1T | 132 | B-2-2b | SPT | [8 empty] | SHEPHERDS RIG
SHRU2Q | 275 | B-2-1b, B-3-1b | SPT | 55.9655 | -3.1856 | S6 | S | T2 |  |  |  | SHRUBHILL
SHRU2R | 275 | B-2-1b, B-3-1b | SPT | 55.9655 | -3.1856 | S6 | S | T2 |  |  |  | SHRUBHILL
SHRU3A | 33 | B-3-1b | SPT | 55.9655 | -3.1856 | S6 | S | T2 |  |  |  | SHRUBHILL
SHRU3B | 33 | B-3-1b | SPT | 55.9655 | -3.1856 | S6 | S | T2 |  |  |  | SHRUBHILL
SHUR41 | 400 | B-2-1c | NGET | 51.2039 | -3.1368 | E8 | E | T9 |  |  |  | SHURTON
SIGH2Q | 275 | B-2-2b, B-3-1b | SPT | 55.929 | -3.305 | S6 | S | T2 |  |  |  | SIGHTHILL
SIGH2R | 275 | B-2-2b, B-3-1b | SPT | 55.929 | -3.305 | S6 | S | T2 |  |  |  | SIGHTHILL
SIGH3A | 33 | B-3-1b | SPT | 55.929 | -3.305 | S6 | S | T2 |  |  |  | SIGHTHILL
SING41 | 400 | B-2-1c | NGET | 51.405 | 0.39236 | C2 | C | T11 |  | Single Switch Mesh | Outdoor | SINGLEWELL
SIZE11 | 132 | B-2-1c, B-3-1c | NGET | 52.215 | 1.6165 | J2 | J | T7 |  | Double busbar | Indoor | SIZEWELL
SIZE12 | 132 | B-3-1c | NGET | 52.215 | 1.6165 | J2 | J | T7 |  | Double busbar | Indoor | SIZEWELL
SIZE1A | 132 | B-2-1c, B-3-1c | NGET | 52.215 | 1.6165 | J2 | J | T7 |  | Double busbar | Indoor | SIZEWELL
SIZE1B | 132 | B-2-1c, B-3-1c | NGET | 52.215 | 1.6165 | J2 | J | T7 |  | Double busbar | Indoor | SIZEWELL
SIZE41 | 400 | B-2-1c, B-3-1c | NGET | 52.215 | 1.6165 | J2 | J | T7 |  | Double busbar | Indoor | SIZEWELL
SJOW11 | 132 | B-3-1c, B-3-2c, B-4-1c | NGET | 51.5275 | -0.16956 | A7 | A | T11 |  | Four Switch Mesh | Indoor | ST JOHNS WOOD
SJOW12 | 132 | B-3-1c | NGET | 51.5275 | -0.16956 | A7 | A | T11 |  | Four Switch Mesh | Indoor | ST JOHNS WOOD
SJOW13 | 132 | B-3-1c | NGET | 51.5275 | -0.16956 | A7 | A | T11 |  | Four Switch Mesh | Indoor | ST JOHNS WOOD
SJOW41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-3-2c, B-4-1c | NGET | 51.5275 | -0.16956 | A7 | A | T11 |  | Four Switch Mesh | Indoor | ST JOHNS WOOD
SKLG11 | 132 | B-3-1c, B-4-1c | NGET | 53.7769 | -1.4969 | P1 | P | T4 |  | Four Switch Mesh | Outdoor | SKELTON GRANGE
SKLG21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 53.7769 | -1.4969 | P1 | P | T4 |  | Four Switch Mesh | Outdoor | SKELTON GRANGE
SLCK1- | 132 | B-2-2a | SHET | [8 empty] | SLICKLY WIND FARM
SLKB1J | 132 | B-2-1a | SHET | [8 empty] | SLACKBUIE
SLKB1K | 132 | B-2-1a | SHET | [8 empty] | SLACKBUIE
SLKB1L | 132 | B-2-1a | SHET | [8 empty] | SLACKBUIE
SLKB1M | 132 | B-2-1a | SHET | [8 empty] | SLACKBUIE
SLOY1A | 132 | B-2-1a | SHET | 56.2455 | -4.729 | T3 | T | T1 |  |  |  | SLOY
SLOY1B | 132 | B-2-1a | SHET | 56.2455 | -4.729 | T3 | T | T1 |  |  |  | SLOY
SLOY1C | 132 | B-2-1a | SHET | 56.2455 | -4.729 | T3 | T | T1 |  |  |  | SLOY
SLOY1D | 132 | B-2-1a | SHET | 56.2455 | -4.729 | T3 | T | T1 |  |  |  | SLOY
SLOY1E | 132 | B-2-1a | SHET | 56.2455 | -4.729 | T3 | T | T1 |  |  |  | SLOY
SLOY1F | 132 | B-2-1a | SHET | 56.2455 | -4.729 | T3 | T | T1 |  |  |  | SLOY
SLOY1J | 132 | B-2-1a, B-2-2a | SHET | 56.2455 | -4.729 | T3 | T | T1 |  |  |  | SLOY
SLOY1K | 132 | B-2-1a, B-2-2a | SHET | 56.2455 | -4.729 | T3 | T | T1 |  |  |  | SLOY
SLOY1L | 132 | B-2-1a, B-3-2a | SHET | 56.2455 | -4.729 | T3 | T | T1 |  |  |  | SLOY
SLOY1M | 132 | B-2-1a, B-3-2a | SHET | 56.2455 | -4.729 | T3 | T | T1 |  |  |  | SLOY
SLOY1N | 132 | B-2-1a, B-3-2a | SHET | 56.2455 | -4.729 | T3 | T | T1 |  |  |  | SLOY
SLOY1P | 132 | B-2-1a, B-3-2a | SHET | 56.2455 | -4.729 | T3 | T | T1 |  |  |  | SLOY
SLOY1T | 132 | B-2-1a | SHET | 56.2455 | -4.729 | T3 | T | T1 |  |  |  | SLOY
SLOY5L | 11 | B-3-2a | SHET | 56.2455 | -4.729 | T3 | T | T1 |  |  |  | SLOY
SLOY5M | 11 | B-3-2a | SHET | 56.2455 | -4.729 | T3 | T | T1 |  |  |  | SLOY
SLOY5N | 11 | B-3-2a | SHET | 56.2455 | -4.729 | T3 | T | T1 |  |  |  | SLOY
SLOY5P | 11 | B-3-2a | SHET | 56.2455 | -4.729 | T3 | T | T1 |  |  |  | SLOY
SMAN11 | 132 | B-3-1c | NGET | 53.4203 | -2.2763 | N2 | N | T4 |  | Four Switch Mesh | Outdoor | SOUTH MANCHESTER
SMAN12 | 132 | B-3-1c | NGET | 53.4203 | -2.2763 | N2 | N | T4 |  | Four Switch Mesh | Outdoor | SOUTH MANCHESTER
SMAN21 | 275 | B-2-1c, B-3-1c | NGET | 53.4203 | -2.2763 | N2 | N | T4 |  | Four Switch Mesh | Outdoor | SOUTH MANCHESTER
SMEA1- | 132 | B-3-1b | SPT | 55.9085 | -3.0376 |  |  | T2 |  |  |  | SMEATON
SMEA2- | 275 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.9085 | -3.0376 |  |  | T2 |  |  |  | SMEATON
SMEA3U | 33 | B-4-1b | SPT | 55.9085 | -3.0376 |  |  | T2 |  |  |  | SMEATON
SMEA3V | 33 | B-4-1b | SPT | 55.9085 | -3.0376 |  |  | T2 |  |  |  | SMEATON
SMEA4Q | 400 | B-2-2b | SPT | 55.9085 | -3.0376 |  |  | T2 |  |  |  | SMEATON
SMEA4R | 400 | B-2-2b, B-3-1b | SPT | 55.9085 | -3.0376 |  |  | T2 |  |  |  | SMEATON
SNQR3- | 33 | B-2-1b | SPT | [8 empty] | SANQUHAR
SOKY1- | 132 | B-2-1b, B-2-2b | SPT | 57.281 | -5.7097 |  |  | T1 |  |  |  | SOUTH KYLE
SPAV1Q | 132 | B-2-2b, B-3-1b | SPT | 55.9372 | -4.8133 | S6 | S | T2 |  |  |  | SPANGO VALLEY
SPAV1R | 132 | B-2-2b, B-3-1b | SPT | 55.9372 | -4.8133 | S6 | S | T2 |  |  |  | SPANGO VALLEY
SPAV3- | 33 | B-3-1b | SPT | 55.9372 | -4.8133 | S6 | S | T2 |  |  |  | SPANGO VALLEY
SPEN11 | 132 | B-3-1c | NGET | 54.7055 | -1.5548 | Q7 | Q | T3 |  | Four Switch Mesh | Outdoor | SPENNYMOOR
SPEN41 | 400 | B-2-2c, B-3-1c, B-4-1c, B-4-2c | NGET | 54.7055 | -1.5548 | Q7 | Q | T3 |  | Four Switch Mesh | Outdoor | SPENNYMOOR
SPEN42 | 400 | B-2-1c, B-2-2c, B-3-1c | NGET | 54.7055 | -1.5548 | Q7 | Q | T3 |  | Four Switch Mesh | Outdoor | SPENNYMOOR
SPIT1J | 132 | B-2-1a, B-3-1a | SHET | 58.4801 | -3.4539 |  |  | T1 |  |  |  | SPITTAL
SPIT1K | 132 | B-2-1a, B-3-1a | SHET | 58.4801 | -3.4539 |  |  | T1 |  |  |  | SPITTAL
SPIT1M | 132 | B-2-1a, B-3-1a | SHET | 58.4801 | -3.4539 |  |  | T1 |  |  |  | SPITTAL
SPIT2J | 275 | B-2-1a, B-3-1a, B-3-2a | SHET | 58.4801 | -3.4539 |  |  | T1 |  |  |  | SPITTAL
SPIT2K | 275 | B-2-1a, B-3-1a, B-3-2a | SHET | 58.4801 | -3.4539 |  |  | T1 |  |  |  | SPITTAL
SPIT2R | 275 | B-2-1a | SHET | 58.4801 | -3.4539 |  |  | T1 |  |  |  | SPITTAL
SPLN41 | 400 | B-2-1c | NGET | 52.8058 | -0.13332 | K1 | K | T5 |  | Double busbar | Outdoor | SPALDING NORTH
SPRB1- | 132 | B-2-2b, B-3-2b | SPT | [8 empty] | SPIREBUSH
SPRB3- | 33 | B-3-2b | SPT | [8 empty] | SPIREBUSH
SSHI22 | 275 | B-2-1c, B-3-1c | NGET | 54.9734 | -1.4495 | Q4 | Q | T3 |  | Single Switch Mesh | Outdoor | SOUTH SHIELDS
SSHI31 | 33 | B-3-1c | NGET | 54.9734 | -1.4495 | Q4 | Q | T3 |  | Single Switch Mesh | Outdoor | SOUTH SHIELDS
STAH11 | 132 | B-3-1c | NGET | 53.8788 | -2.9878 | R4 | R | T3 |  | Teed Transformers | Outdoor | STANAH
STAH4A | 400 | B-2-2c, B-3-1c | NGET | 53.8788 | -2.9878 | R4 | R | T3 |  | Teed Transformers | Outdoor | STANAH
STAH4B | 400 | B-2-2c, B-3-1c | NGET | 53.8788 | -2.9878 | R4 | R | T3 |  | Teed Transformers | Outdoor | STANAH
STAL11 | 132 | B-3-1c | NGET | 53.4937 | -2.0413 | N7 | N | T4 |  | Single Switch Mesh | Outdoor | STALYBRIDGE
STAL21 | 275 | B-2-1c, B-3-1c | NGET | 53.4937 | -2.0413 | N7 | N | T4 |  | Single Switch Mesh | Outdoor | STALYBRIDGE
STAL4A | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 53.4937 | -2.0413 | N7 | N | T4 |  | Single Switch Mesh | Outdoor | STALYBRIDGE
STAL4B | 400 | B-2-1c | NGET | 53.4937 | -2.0413 | N7 | N | T4 |  | Single Switch Mesh | Outdoor | STALYBRIDGE
STAY41 | 400 | B-2-1c, B-2-2c, B-3-1c | NGET | 53.0775 | -0.86898 | K5 | K | T5 |  | Double busbar | Outdoor | STAYTHORPE
STAY4A | 400 | B-2-2c, B-3-1c | NGET | 53.0775 | -0.86898 | K5 | K | T5 |  | Double busbar | Outdoor | STAYTHORPE
STCS1A | 132 | B-2-2a | SHET | 58.2775 | -6.3083 |  |  | T1 |  |  |  | STRATHY COLLECTOR STATION
STCS1B | 132 | B-2-2a | SHET | 58.2775 | -6.3083 |  |  | T1 |  |  |  | STRATHY COLLECTOR STATION
STEN11 | 132 | B-2-1c, B-3-1c | NGET | 54.9781 | -1.7245 | Q5 | Q | T3 |  | Double busbar | Outdoor | STELLA NORTH
STES11 | 132 | B-2-1c, B-3-1c | NGET | 54.9744 | -1.7325 | Q5 | Q | T3 |  | Double busbar | Outdoor | STELLA SOUTH
STEW21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 54.9777 | -1.7422 | Q5 | Q | T3 |  | Double busbar | Outdoor | STELLA WEST
STEW41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 54.9777 | -1.7422 | Q5 | Q | T3 |  | Double busbar | Outdoor | STELLA WEST
STHA2A | 275 | B-2-1b, B-3-1b | SPT | 55.7522 | -4.0818 | S6 | S | T2 |  |  |  | STRATHAVEN
STHA2B | 275 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.7522 | -4.0818 | S6 | S | T2 |  |  |  | STRATHAVEN
STHA3- | 33 | B-3-1b | SPT | 55.7522 | -4.0818 | S6 | S | T2 |  |  |  | STRATHAVEN
STHA3V | 33 | B-4-1b | SPT | 55.7522 | -4.0818 | S6 | S | T2 |  |  |  | STRATHAVEN
STHA4A | 400 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.7522 | -4.0818 | S6 | S | T2 |  |  |  | STRATHAVEN
STHA4B | 400 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.7522 | -4.0818 | S6 | S | T2 |  |  |  | STRATHAVEN
STIR1S | 132 | B-2-1b, B-3-1b | SPT | 56.1169 | -3.92 | S5 | S | T2 |  |  |  | STIRLING
STIR1T | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 56.1169 | -3.92 | S5 | S | T2 |  |  |  | STIRLING
STIR3- | 33 | B-3-1b | SPT | 56.1169 | -3.92 | S5 | S | T2 |  |  |  | STIRLING
STLE1Q | 132 | B-2-1b, B-3-1b | SPT | 55.9617 | -4.5628 | S5 | S | T2 |  |  |  | STRATHLEVEN
STLE1R | 132 | B-2-1b, B-3-1b | SPT | 55.9617 | -4.5628 | S5 | S | T2 |  |  |  | STRATHLEVEN
STLE3S | 33 | B-3-1b | SPT | 55.9617 | -4.5628 | S5 | S | T2 |  |  |  | STRATHLEVEN
STNG1A | 132 | B-2-2a | SHET | [8 empty] | STANNERGATE
STNG1B | 132 | B-2-2a | SHET | [8 empty] | STANNERGATE
STNG1C | 132 | B-2-2a | SHET | [8 empty] | STANNERGATE
STNG1D | 132 | B-2-2a | SHET | [8 empty] | STANNERGATE
STNG1E | 132 | B-2-2a, B-3-2a | SHET | [8 empty] | STANNERGATE
STNG3- | 33 | B-3-2a | SHET | [8 empty] | STANNERGATE
STOB11 | 132 | B-3-1c | NGET | 52.9598 | -1.0506 | L7 | L | T5 |  | Single Switch Mesh | Indoor | STOKE BARDOLPH
STOB41 | 400 | B-2-2c, B-3-1c | NGET | 52.9598 | -1.0506 | L7 | L | T5 |  | Single Switch Mesh | Indoor | STOKE BARDOLPH
STOC1- | 132 | B-2-2b, B-3-2b | SPT | [8 empty] | STRANOCH WIND FARM
STOC3- | 33 | B-3-2b | SPT | [8 empty] | STRANOCH WIND FARM
STRB2- | 275 | B-2-2a, B-3-1a | SHET | 58.0202 | -3.8755 |  |  | T1 |  |  |  | STRATH BRORA WIND
STRB3W | 33 | B-3-1a | SHET | 58.0202 | -3.8755 |  |  | T1 |  |  |  | STRATH BRORA WIND
STRI1Q | 132 | B-2-1a, B-3-1a | SHET | 57.5864 | -2.0694 | T2 | T | T1 |  |  |  | STRICHEN
STRI1R | 132 | B-2-1a, B-3-1a | SHET | 57.5864 | -2.0694 | T2 | T | T1 |  |  |  | STRICHEN
STRI3- | 33 | B-3-1a | SHET | 57.5864 | -2.0694 | T2 | T | T1 |  |  |  | STRICHEN
STRL1- | 132 | B-2-1a, B-3-1a | SHET | 57.0947 | -4.4339 |  |  | T1 |  |  |  | STRONELAIRG WIND FARM (SSE)
STRL3P | 33 | B-3-1a | SHET | 57.0947 | -4.4339 |  |  | T1 |  |  |  | STRONELAIRG WIND FARM (SSE)
STRL3Q | 33 | B-3-1a | SHET | 57.0947 | -4.4339 |  |  | T1 |  |  |  | STRONELAIRG WIND FARM (SSE)
STRL3R | 33 | B-3-1a | SHET | 57.0947 | -4.4339 |  |  | T1 |  |  |  | STRONELAIRG WIND FARM (SSE)
STRW1- | 132 | B-2-1a, B-3-1a | SHET | [8 empty] | STRATHY WIND
STRW1A | 132 | B-2-1a, B-2-2a | SHET | [8 empty] | STRATHY WIND
STRW3- | 33 | B-3-1a | SHET | [8 empty] | STRATHY WIND
STSB4A | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 53.4877 | -1.602 | P3 | P | T4 |  | Single Switch Mesh | Outdoor | STOCKSBRIDGE
STSB4B | 400 | B-2-1c, B-3-1c | NGET | 53.4877 | -1.602 | P3 | P | T4 |  | Single Switch Mesh | Outdoor | STOCKSBRIDGE
STSO1A | 132 | B-2-2a | SHET | [8 empty] | STRATHY SOUTH
STSO1B | 132 | B-2-2a, B-3-2a | SHET | [8 empty] | STRATHY SOUTH
STSO3A | 33 | B-3-2a | SHET | [8 empty] | STRATHY SOUTH
STSO3B | 33 | B-3-2a | SHET | [8 empty] | STRATHY SOUTH
STWB4Q | 400 | B-2-1b, B-2-1c | NGET, SPT | 55.6524 | -2.2476 | Q6 | Q | T2 |  |  |  | STELLA WEST BORDER 400KV
STWB4R | 400 | B-2-1b, B-2-1c | NGET, SPT | 55.6524 | -2.2476 | Q6 | Q | T2 |  |  |  | STELLA WEST BORDER 400KV
STWO1- | 132 | B-2-2a, B-3-2a | SHET | [8 empty] | STRATHY WOOD
STWO3- | 33 | B-3-2a | SHET | [8 empty] | STRATHY WOOD
STYC11 | 132 | B-3-1c | NGET | 53.0775 | -0.86898 | K5 | K | T5 |  |  |  | STAYTHORPE C
STYC12 | 132 | B-3-1c | NGET | 53.0775 | -0.86898 | K5 | K | T5 |  |  |  | STAYTHORPE C
SUND11 | 132 | B-3-1c | NGET | 51.9363 | -0.50301 | D4 | D | T6 |  | Double busbar | Outdoor | SUNDON
SUND31 | 33 | B-3-1c | NGET | 51.9363 | -0.50301 | D4 | D | T6 |  | Double busbar | Outdoor | SUNDON
SUND41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 51.9363 | -0.50301 | D4 | D | T6 |  | Double busbar | Outdoor | SUNDON
SUND42 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 51.9363 | -0.50301 | D4 | D | T6 |  | Double busbar | Outdoor | SUNDON
SWAN11 | 132 | B-3-1c | NGET | 51.6894 | -3.9568 | H6 | H | T8 |  | Single Switch Mesh | Outdoor | SWANSEA NORTH
SWAN12 | 132 | B-3-1c | NGET | 51.6894 | -3.9568 | H6 | H | T8 |  | Single Switch Mesh | Outdoor | SWANSEA NORTH
SWAN21 | 275 | B-2-1c, B-3-1c | NGET | 51.6894 | -3.9568 | H6 | H | T8 |  | Single Switch Mesh | Outdoor | SWANSEA NORTH
SWAN22 | 275 | B-3-1c | NGET | 51.6894 | -3.9568 | H6 | H | T8 |  | Single Switch Mesh | Outdoor | SWANSEA NORTH
SWAN41 | 400 | B-2-1c, B-2-2c, B-3-1c | NGET | 51.6894 | -3.9568 | H6 | H | T8 |  | Single Switch Mesh | Outdoor | SWANSEA NORTH
SWAN42 | 400 | B-2-1c | NGET | 51.6894 | -3.9568 | H6 | H | T8 |  | Single Switch Mesh | Outdoor | SWANSEA NORTH
SWAN4A | 400 | B-2-1c, B-3-1c | NGET | 51.6894 | -3.9568 | H6 | H | T8 |  | Single Switch Mesh | Outdoor | SWANSEA NORTH
SWAN4B | 400 | B-2-1c, B-3-1c | NGET | 51.6894 | -3.9568 | H6 | H | T8 |  | Single Switch Mesh | Outdoor | SWANSEA NORTH
SYEL1- | 132 | B-2-2a | SHET | [8 empty] | SOUTH YELL
SYEL1A | 132 | B-2-2a | SHET | [8 empty] | SOUTH YELL
SYEL1B | 132 | B-2-2a | SHET | [8 empty] | SOUTH YELL
SYEL1M | 132 | B-2-2a | SHET | [8 empty] | SOUTH YELL
SYEL1N | 132 | B-2-2a | SHET | [8 empty] | SOUTH YELL
TADT2A | 275 | B-2-2c | NGET | 53.881 | -1.2655 | P6 | P | T4 |  |  |  | TADCASTER TEE
TADT2B | 275 | B-2-2c | NGET | 53.881 | -1.2655 | P6 | P | T4 |  |  |  | TADCASTER TEE
TARL1Q | 132 | B-2-1a, B-3-1a | SHET | 57.1522 | -2.7877 | T2 | T | T1 |  |  |  | TARLAND
TARL1R | 132 | B-2-1a, B-3-1a | SHET | 57.1522 | -2.7877 | T2 | T | T1 |  |  |  | TARLAND
TARL3- | 33 | B-3-1a | SHET | 57.1522 | -2.7877 | T2 | T | T1 |  |  |  | TARLAND
TAUN11 | 132 | B-3-1c | NGET | 51.017 | -3.1551 | E8 | E | T9 |  | Teed Transformers | Outdoor | TAUNTON
TAUN41 | 400 | B-2-1c, B-2-2c, B-3-1c | NGET | 51.017 | -3.1551 | E8 | E | T9 |  | Teed Transformers | Outdoor | TAUNTON
TAUN42 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-2c | NGET | 51.017 | -3.1551 | E8 | E | T9 |  | Teed Transformers | Outdoor | TAUNTON
TAYN1Q | 132 | B-2-1a, B-3-1a | SHET | 56.4302 | -5.2145 | T3 | T | T1 |  |  |  | TAYNUILT
TAYN1R | 132 | B-2-1a, B-3-1a | SHET | 56.4302 | -5.2145 | T3 | T | T1 |  |  |  | TAYNUILT
TAYN3- | 33 | B-3-1a | SHET | 56.4302 | -5.2145 | T3 | T | T1 |  |  |  | TAYNUILT
TEAL1- | 132 | B-2-1a, B-3-1a, B-4-1a | SHET | 51.5019 | -0.29717 |  |  | T11 |  |  |  | TEALING
TEAL2A | 275 | B-2-1a, B-3-1a | SHET | 51.5019 | -0.29717 |  |  | T11 |  |  |  | TEALING
TEAL2B | 275 | B-2-1a, B-3-1a | SHET | 51.5019 | -0.29717 |  |  | T11 |  |  |  | TEALING
TEAL2J | 275 | B-2-1a, B-3-1a, B-4-1a | SHET | 51.5019 | -0.29717 |  |  | T11 |  |  |  | TEALING
TEAL2K | 275 | B-2-1a, B-3-1a | SHET | 51.5019 | -0.29717 |  |  | T11 |  |  |  | TEALING
TEAL3W | 33 | B-4-1a | SHET | 51.5019 | -0.29717 |  |  | T11 |  |  |  | TEALING
TEAL3Y | 33 | B-4-1a | SHET | 51.5019 | -0.29717 |  |  | T11 |  |  |  | TEALING
TELR1Q | 132 | B-2-2b, B-3-1b | SPT | 55.9618 | -3.2431 | S6 | S | T2 |  |  |  | TELFORD ROAD
TELR1R | 132 | B-2-2b, B-3-1b | SPT | 55.9618 | -3.2431 | S6 | S | T2 |  |  |  | TELFORD ROAD
TELR3- | 33 | B-3-1b | SPT | 55.9618 | -3.2431 | S6 | S | T2 |  |  |  | TELFORD ROAD
TEMP21 | 275 | B-2-1c, B-3-1c | NGET | 53.4121 | -1.3858 | P3 | P | T4 |  | Teed Transformers | Outdoor | TEMPLEBOROUGH
TEMP22 | 275 | B-2-1c, B-2-2c, B-3-1c | NGET | 53.4121 | -1.3858 | P3 | P | T4 |  | Teed Transformers | Outdoor | TEMPLEBOROUGH
TEMP31 | 33 | B-3-1c | NGET | 53.4121 | -1.3858 | P3 | P | T4 |  | Teed Transformers | Outdoor | TEMPLEBOROUGH
THOM21 | 275 | B-2-1c, B-3-1c | NGET | 53.5756 | -1.0891 | P6 | P | T4 |  | Double busbar | Outdoor | THORPE MARSH
THOM2A | 275 | B-2-1c, B-3-1c | NGET | 53.5756 | -1.0891 | P6 | P | T4 |  | Double busbar | Outdoor | THORPE MARSH
THOM41 | 400 | B-2-1c, B-3-1c | NGET | 53.5756 | -1.0891 | P6 | P | T4 |  | Double busbar | Outdoor | THORPE MARSH
THOM42 | 400 | B-2-1c, B-3-1c, B-4-1c | NGET | 53.5756 | -1.0891 | P6 | P | T4 |  | Double busbar | Outdoor | THORPE MARSH
THOM61 | 66 | B-3-1c | NGET | 53.5756 | -1.0891 | P6 | P | T4 |  | Double busbar | Outdoor | THORPE MARSH
THTO41 | 400 | B-2-1c, B-2-2c | NGET | 53.9003 | -0.82212 | P6 | P | T4 |  | Double busbar | Outdoor | THORNTON
THTO42 | 400 | B-2-1c, B-2-2c | NGET | 53.9003 | -0.82212 | P6 | P | T4 |  | Double busbar | Outdoor | THORNTON
THTO43 | 400 | B-2-1c, B-2-2c | NGET | 53.9003 | -0.82212 | P6 | P | T4 |  | Double busbar | Outdoor | THORNTON
THUR21 | 275 | B-2-1c, B-3-1c | NGET | 53.4049 | -1.2685 | P3 | P | T4 |  | Four Switch Mesh | Outdoor | THURCROFT
THUR2A | 275 | B-2-1c, B-2-2c | NGET | 53.4049 | -1.2685 | P3 | P | T4 |  | Four Switch Mesh | Outdoor | THURCROFT
THUR61 | 66 | B-3-1c | NGET | 53.4049 | -1.2685 | P3 | P | T4 |  | Four Switch Mesh | Outdoor | THURCROFT
THUS1J | 132 | B-2-1a, B-2-2a, B-3-1a | SHET | 58.5637 | -3.5102 |  |  | T1 |  |  |  | THURSO SOUTH
THUS1K | 132 | B-2-1a, B-2-2a, B-3-1a | SHET | 58.5637 | -3.5102 |  |  | T1 |  |  |  | THURSO SOUTH
THUS1L | 132 | B-2-2a | SHET | 58.5637 | -3.5102 |  |  | T1 |  |  |  | THURSO SOUTH
THUS1M | 132 | B-2-2a | SHET | 58.5637 | -3.5102 |  |  | T1 |  |  |  | THURSO SOUTH
THUS2J | 275 | B-2-1a, B-2-2a, B-3-1a | SHET | 58.5637 | -3.5102 |  |  | T1 |  |  |  | THURSO SOUTH
THUS2K | 275 | B-2-1a, B-3-1a | SHET | 58.5637 | -3.5102 |  |  | T1 |  |  |  | THURSO SOUTH
THUS3- | 33 | B-3-1a | SHET | 58.5637 | -3.5102 |  |  | T1 |  |  |  | THURSO SOUTH
TILB11 | 132 | B-3-1c | NGET | 51.4603 | 0.39372 | C1 | C | T11 |  | Double busbar | Outdoor | TILBURY
TILB12 | 132 | B-3-1c | NGET | 51.4603 | 0.39372 | C1 | C | T11 |  | Double busbar | Outdoor | TILBURY
TILB13 | 132 | B-3-1c | NGET | 51.4603 | 0.39372 | C1 | C | T11 |  | Double busbar | Outdoor | TILBURY
TILB14 | 132 | B-3-1c | NGET | 51.4603 | 0.39372 | C1 | C | T11 |  | Double busbar | Outdoor | TILBURY
TILB21 | 275 | B-2-1c, B-3-1c | NGET | 51.4603 | 0.39372 | C1 | C | T11 |  | Double busbar | Outdoor | TILBURY
TILB41 | 400 | B-2-1c, B-2-2c, B-3-1c | NGET | 51.4603 | 0.39372 | C1 | C | T11 |  | Double busbar | Outdoor | TILBURY
TILB4A | 400 | B-2-1c, B-3-1c | NGET | 51.4603 | 0.39372 | C1 | C | T11 |  | Double busbar | Outdoor | TILBURY
TILB4B | 400 | B-2-1c, B-3-1c | NGET | 51.4603 | 0.39372 | C1 | C | T11 |  | Double busbar | Outdoor | TILBURY
TINP21 | 275 | B-2-1c, B-3-1c | NGET | 53.4011 | -1.3946 | P3 | P | T4 |  | Teed Transformers | Outdoor | TINSLEY PARK
TINP22 | 275 | B-2-1c, B-3-1c | NGET | 53.4011 | -1.3946 | P3 | P | T4 |  | Teed Transformers | Outdoor | TINSLEY PARK
TINP31 | 33 | B-3-1c | NGET | 53.4011 | -1.3946 | P3 | P | T4 |  | Teed Transformers | Outdoor | TINSLEY PARK
TINP32 | 33 | B-3-1c | NGET | 53.4011 | -1.3946 | P3 | P | T4 |  | Teed Transformers | Outdoor | TINSLEY PARK
TNGF1- | 132 | B-2-2a | SHET | [8 empty] | TANGY IV
TNGF1A | 132 | B-2-2a, B-3-2a | SHET | [8 empty] | TANGY IV
TNGF3- | 33 | B-3-2a | SHET | [8 empty] | TANGY IV
TODD3- | 33 | B-2-1b | SPT | [8 empty] | TODDLEBURN
TODP21 | 275 | B-2-1c, B-3-1c | NGET | 54.6065 | -1.1167 | Q2 | Q | T3 |  | Single Switch Mesh | Outdoor | TOD POINT
TODP61 | 66 | B-3-1c | NGET | 54.6065 | -1.1167 | Q2 | Q | T3 |  | Single Switch Mesh | Outdoor | TOD POINT
TOMT1J | 132 | B-2-1a, B-3-1a | SHET | 57.3014 | -4.0681 |  |  | T1 |  |  |  | TOMATIN
TOMT1K | 132 | B-2-1a, B-3-1a | SHET | 57.3014 | -4.0681 |  |  | T1 |  |  |  | TOMATIN
TOMT1L | 132 | B-2-1a | SHET | 57.3014 | -4.0681 |  |  | T1 |  |  |  | TOMATIN
TOMT1M | 132 | B-2-1a | SHET | 57.3014 | -4.0681 |  |  | T1 |  |  |  | TOMATIN
TOMT2J | 275 | B-2-1a, B-3-1a | SHET | 57.3014 | -4.0681 |  |  | T1 |  |  |  | TOMATIN
TOMT2K | 275 | B-2-1a, B-3-1a | SHET | 57.3014 | -4.0681 |  |  | T1 |  |  |  | TOMATIN
TONG1- | 132 | B-2-2b, B-3-1b | SPT | 54.8616 | -4.0344 | S6 | S | T2 |  |  |  | TONGLAND
TONG1Q | 132 | B-3-1b | SPT | 54.8616 | -4.0344 | S6 | S | T2 |  |  |  | TONGLAND
TONG1R | 132 | B-3-1b | SPT | 54.8616 | -4.0344 | S6 | S | T2 |  |  |  | TONGLAND
TONG3- | 33 | B-3-1b | SPT | 54.8616 | -4.0344 | S6 | S | T2 |  |  |  | TONGLAND
TONG5- | 11 | B-3-1b | SPT | 54.8616 | -4.0344 | S6 | S | T2 |  |  |  | TONGLAND
TORN1- | 132 | B-2-2b, B-3-1b | SPT | 55.9663 | -2.411 |  |  | T2 |  |  |  | TORNESS
TORN4- | 400 | B-2-2b, B-3-1b, B-4-1b | SPT | 55.9663 | -2.411 |  |  | T2 |  |  |  | TORNESS
TOTT11 | 132 | B-3-1c | NGET | 51.6045 | -0.047649 | A1 | A | T11 |  | Four Switch Mesh | Indoor | TOTTENHAM
TOTT12 | 132 | B-3-1c | NGET | 51.6045 | -0.047649 | A1 | A | T11 |  | Four Switch Mesh | Indoor | TOTTENHAM
TOTT21 | 275 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 51.6045 | -0.047649 | A1 | A | T11 |  | Four Switch Mesh | Indoor | TOTTENHAM
TOTT22 | 275 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 51.6045 | -0.047649 | A1 | A | T11 |  | Four Switch Mesh | Indoor | TOTTENHAM
TOTT23 | 275 | B-2-1c, B-3-1c | NGET | 51.6045 | -0.047649 | A1 | A | T11 |  | Four Switch Mesh | Indoor | TOTTENHAM
TOTT24 | 275 | B-2-1c, B-3-1c | NGET | 51.6045 | -0.047649 | A1 | A | T11 |  | Four Switch Mesh | Indoor | TOTTENHAM
TOTT2A | 275 | B-2-1c | NGET | 51.6045 | -0.047649 | A1 | A | T11 |  | Four Switch Mesh | Indoor | TOTTENHAM
TOTT2B | 275 | B-2-1c | NGET | 51.6045 | -0.047649 | A1 | A | T11 |  | Four Switch Mesh | Indoor | TOTTENHAM
TRAW11 | 132 | B-3-1c | NGET | 52.9264 | -3.9455 | M7 | M | T4 |  | Four Switch Mesh | Outdoor | TRAWSFYNYDD
TRAW21 | 275 | B-2-1c, B-3-1c | NGET | 52.9264 | -3.9455 | M7 | M | T4 |  | Four Switch Mesh | Outdoor | TRAWSFYNYDD
TRAW41 | 400 | B-2-2c, B-3-1c | NGET | 52.9264 | -3.9455 | M7 | M | T4 |  | Four Switch Mesh | Outdoor | TRAWSFYNYDD
TREM21 | 275 | B-2-1c, B-3-1c | NGET | 51.4817 | -3.1307 | H2 | H | T8 |  | Single Switch Mesh | Outdoor | TREMORFA
TREM31 | 33 | B-3-1c | NGET | 51.4817 | -3.1307 | H2 | H | T8 |  | Single Switch Mesh | Outdoor | TREMORFA
TREU4A | 400 | B-2-1c, B-2-2c | NGET | 53.111 | -3.1206 | M5 | M | T4 |  |  |  | TREUDDYN
TREU4B | 400 | B-2-1c, B-2-2c | NGET | 53.111 | -3.1206 | M5 | M | T4 |  |  |  | TREUDDYN
TRLO3- | 33 | B-2-2b | SPT | 55.2345 | -4.789 |  |  | T2 |  |  |  | TRALORG
TRSN1- | 132 | B-2-2b, B-3-2b | SPT | [8 empty] | TROSTON
TRSN3- | 33 | B-3-2b | SPT | [8 empty] | TROSTON
TUMB1Q | 132 | B-2-1a | SHET | 56.7068 | -4.0295 | T4 | T | T1 |  |  |  | TUMMEL BRIDGE
TUMB1R | 132 | B-2-1a | SHET | 56.7068 | -4.0295 | T4 | T | T1 |  |  |  | TUMMEL BRIDGE
TUMM1J | 132 | B-2-1a, B-3-2a | SHET | 56.7068 | -4.0295 |  |  | T1 |  |  |  | TUMMEL
TUMM1K | 132 | B-2-1a, B-3-2a | SHET | 56.7068 | -4.0295 |  |  | T1 |  |  |  | TUMMEL
TUMM4- | 400 | B-2-1a | SHET | 56.7068 | -4.0295 |  |  | T1 |  |  |  | TUMMEL
TWIN11 | 132 | B-3-2c | NGET | 52.0018 | 0.68625 | D5 | D | T6 |  |  |  | TWINSTEAD
TWIN4A | 400 | B-2-2c, B-3-2c | NGET | 52.0018 | 0.68625 | D5 | D | T6 |  |  |  | TWINSTEAD
TWIN4B | 400 | B-2-2c, B-3-2c | NGET | 52.0018 | 0.68625 | D5 | D | T6 |  |  |  | TWINSTEAD
TYNE11 | 132 | B-3-1c | NGET | 55.0237 | -1.5006 | Q4 | Q | T3 |  | Single Switch Mesh | Outdoor | TYNEMOUTH
TYNE21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 55.0237 | -1.5006 | Q4 | Q | T3 |  | Single Switch Mesh | Outdoor | TYNEMOUTH
TYNE2A | 275 | B-2-1c, B-3-1c | NGET | 55.0237 | -1.5006 | Q4 | Q | T3 |  | Single Switch Mesh | Outdoor | TYNEMOUTH
TYNE51 | 11 | B-3-1c | NGET | 55.0237 | -1.5006 | Q4 | Q | T3 |  | Single Switch Mesh | Outdoor | TYNEMOUTH
UPPB11 | 132 | B-3-1c | NGET | 51.5741 | -3.3004 | H2 | H | T8 |  | Single Switch Mesh | Outdoor | UPPER BOAT
UPPB21 | 275 | B-2-1c, B-3-1c | NGET | 51.5741 | -3.3004 | H2 | H | T8 |  | Single Switch Mesh | Outdoor | UPPER BOAT
UPPB22 | 275 | B-2-1c, B-3-1c | NGET | 51.5741 | -3.3004 | H2 | H | T8 |  | Single Switch Mesh | Outdoor | UPPER BOAT
UPPB31 | 33 | B-3-1c | NGET | 51.5741 | -3.3004 | H2 | H | T8 |  | Single Switch Mesh | Outdoor | UPPER BOAT
USKM11 | 132 | B-3-1c | NGET | 51.5471 | -2.9786 | H2 | H | T8 |  | Double busbar | Indoor | USKMOUTH
USKM12 | 132 | B-3-1c, B-4-1c | NGET | 51.5471 | -2.9786 | H2 | H | T8 |  | Double busbar | Indoor | USKMOUTH
USKM21 | 275 | B-2-1c, B-3-1c | NGET | 51.5471 | -2.9786 | H2 | H | T8 |  | Double busbar | Indoor | USKMOUTH
USKM2A | 275 | B-2-1c | NGET | 51.5471 | -2.9786 | H2 | H | T8 |  | Double busbar | Indoor | USKMOUTH
USKM2B | 275 | B-2-1c | NGET | 51.5471 | -2.9786 | H2 | H | T8 |  | Double busbar | Indoor | USKMOUTH
UXBR41 | 400 | B-2-2c | NGET | 51.5455 | -0.50209 | A6 | A | T11 |  | Double busbar | Outdoor | Uxbridge Moor
WALE41 | 400 | B-2-2c | NGET | 51.4489 | 0.68023 | C3 | C | T11 |  |  |  | GRAIN WEST (Wallend)
WALH41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 51.8792 | -2.2539 | G1 | G | T8 |  | Four Switch Mesh | Outdoor | WALHAM
WALP11 | 132 | B-3-1c, B-4-1c | NGET | 52.7266 | 0.19804 | J1 | J | T6 |  | Double busbar | Indoor | WALPOLE
WALP41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 52.7266 | 0.19804 | J1 | J | T6 |  | Double busbar | Indoor | WALPOLE
WALX2A | 275 | B-2-2c, B-3-2c | NGET | 51.7148 | -0.011174 | A3 | A | T11 |  | Teed Transformers | Outdoor | WALTHAM CROSS
WALX41 | 400 | B-2-2c, B-3-2c | NGET | 51.7148 | -0.011174 | A3 | A | T11 |  | Teed Transformers | Outdoor | WALTHAM CROSS
WARL11 | 132 | B-3-1c, B-4-1c | NGET | 51.5528 | 0.30137 | C6 | C | T11 |  | Four Switch Mesh | Outdoor | WARLEY
WARL21 | 275 | B-2-1c, B-3-1c | NGET | 51.5528 | 0.30137 | C6 | C | T11 |  | Four Switch Mesh | Outdoor | WARLEY
WASF1A | 132 | B-3-1c | NGET | 53.5626 | -2.8196 | N1 | N | T4 |  | Teed Transformers | Outdoor | WASHWAY FARM
WASF1B | 132 | B-3-1c | NGET | 53.5626 | -2.8196 | N1 | N | T4 |  | Teed Transformers | Outdoor | WASHWAY FARM
WASF2A | 275 | B-2-1c, B-3-1c | NGET | 53.5626 | -2.8196 | N1 | N | T4 |  | Teed Transformers | Outdoor | WASHWAY FARM
WASF2B | 275 | B-2-1c, B-3-1c | NGET | 53.5626 | -2.8196 | N1 | N | T4 |  | Teed Transformers | Outdoor | WASHWAY FARM
WATS11 | 132 | B-3-1c | NGET | 51.643 | -0.40411 | A6 | A | T11 |  | Teed Transformers | Outdoor | WATFORD SOUTH
WATS12 | 132 | B-3-1c | NGET | 51.643 | -0.40411 | A6 | A | T11 |  | Teed Transformers | Outdoor | WATFORD SOUTH
WATS21 | 275 | B-2-1c, B-3-1c | NGET | 51.643 | -0.40411 | A6 | A | T11 |  | Teed Transformers | Outdoor | WATFORD SOUTH
WATS22 | 275 | B-2-1c, B-3-1c | NGET | 51.643 | -0.40411 | A6 | A | T11 |  | Teed Transformers | Outdoor | WATFORD SOUTH
WBOL21 | 275 | B-2-1c, B-3-1c | NGET | 54.9401 | -1.4704 | Q4 | Q | T3 |  | Four Switch Mesh | Outdoor | WEST BOLDON
WBOL61 | 66 | B-3-1c | NGET | 54.9401 | -1.4704 | Q4 | Q | T3 |  | Four Switch Mesh | Outdoor | WEST BOLDON
WBUR11 | 132 | B-3-1c | NGET | 53.3592 | -0.80943 | K6 | K | T5 |  | Double busbar | Indoor | WEST BURTON
WBUR12 | 132 | B-3-1c | NGET | 53.3592 | -0.80943 | K6 | K | T5 |  | Double busbar | Indoor | WEST BURTON
WBUR41 | 400 | B-2-1c, B-2-2c, B-3-1c | NGET | 53.3592 | -0.80943 | K6 | K | T5 |  | Double busbar | Indoor | WEST BURTON
WBUR42 | 400 | B-2-1c, B-2-2c, B-3-1c | NGET | 53.3592 | -0.80943 | K6 | K | T5 |  | Double busbar | Indoor | WEST BURTON
WEAV71 | 25 | B-3-1c | NGET | 53.2417 | -2.5539 | N3 | N | T4 |  |  |  | WEAVER JUNCTION
WESE1- | 132 | B-2-1b, B-3-1b | SPT | [8 empty] | WESTERDOD
WFIB2- | 275 | B-2-1a, B-2-1b | SHET, SPT | 56.1636 | -3.3026 |  |  | T2 |  |  |  | WESTFIELD BOUNDARY
WFIE1A | 132 | B-2-1b, B-3-1b | SPT | 56.1636 | -3.3026 | S5 | S | T2 |  |  |  | WESTFIELD
WFIE1B | 132 | B-2-1b, B-3-1b | SPT | 56.1636 | -3.3026 | S5 | S | T2 |  |  |  | WESTFIELD
WFIE2- | 275 | B-2-1b, B-2-2b, B-3-1b | SPT | 56.1636 | -3.3026 | S5 | S | T2 |  |  |  | WESTFIELD
WFIE3- | 33 | B-3-1b | SPT | 56.1636 | -3.3026 | S5 | S | T2 |  |  |  | WESTFIELD
WGEO2Q | 275 | B-2-1b, B-3-1b | SPT | 55.8631 | -4.2665 | S5 | S | T2 |  |  |  | WEST GEORGE STREET
WGEO2R | 275 | B-2-1b, B-3-2b | SPT | 55.8631 | -4.2665 | S5 | S | T2 |  |  |  | WEST GEORGE STREET
WGEO3- | 33 | B-3-1b, B-3-2b | SPT | 55.8631 | -4.2665 | S5 | S | T2 |  |  |  | WEST GEORGE STREET
WHAM11 | 132 | B-3-1c | NGET | 51.5196 | 0.0007427 | A1 | A | T11 |  | Double busbar | Indoor | WEST HAM
WHAM12 | 132 | B-3-1c | NGET | 51.5196 | 0.0007427 | A1 | A | T11 |  | Double busbar | Indoor | WEST HAM
WHAM41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 51.5196 | 0.0007427 | A1 | A | T11 |  | Double busbar | Indoor | WEST HAM
WHAM4A | 400 | B-2-1c, B-3-1c | NGET | 51.5196 | 0.0007427 | A1 | A | T11 |  | Double busbar | Indoor | WEST HAM
WHAM4B | 400 | B-2-1c, B-3-1c | NGET | 51.5196 | 0.0007427 | A1 | A | T11 |  | Double busbar | Indoor | WEST HAM
WHBR3A | 33 | B-2-2b | SPT | 60.4016 | -1.3479 |  |  | T1 |  |  |  | WHITELAW BRAE
WHBR3B | 33 | B-2-2b | SPT | 60.4016 | -1.3479 |  |  | T1 |  |  |  | WHITELAW BRAE
WHGA11 | 132 | B-3-1c | NGET | 53.5288 | -2.1672 | N4 | N | T4 |  | Four Switch Mesh | Outdoor | WHITEGATE
WHGA21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 53.5288 | -2.1672 | N4 | N | T4 |  | Four Switch Mesh | Outdoor | WHITEGATE
WHHO2Q | 275 | B-2-1b, B-3-1b | SPT | 55.9311 | -3.2014 | S6 | S | T2 |  |  |  | WHITEHOUSE
WHHO2R | 275 | B-2-1b, B-3-1b | SPT | 55.9311 | -3.2014 | S6 | S | T2 |  |  |  | WHITEHOUSE
WHHO3- | 33 | B-3-1b | SPT | 55.9311 | -3.2014 | S6 | S | T2 |  |  |  | WHITEHOUSE
WHIB1A | 132 | B-2-1a | SHET | [8 empty] | WHITE BRIDGE
WHIB1B | 132 | B-2-1a | SHET | [8 empty] | WHITE BRIDGE
WHIB1C | 132 | B-2-1a | SHET | [8 empty] | WHITE BRIDGE
WHIB1D | 132 | B-2-1a | SHET | [8 empty] | WHITE BRIDGE
WHIB1E | 132 | B-2-1a | SHET | [8 empty] | WHITE BRIDGE
WHIB1F | 132 | B-2-1a | SHET | [8 empty] | WHITE BRIDGE
WHIB1G | 132 | B-2-1a | SHET | [8 empty] | WHITE BRIDGE
WHIB1H | 132 | B-2-1a | SHET | [8 empty] | WHITE BRIDGE
WHLL3- | 33 | B-2-1b | SPT | [8 empty] | WHITESIDE HILL
WHSO21 | 275 | B-2-1c, B-3-1c | NGET | 51.5648 | -2.9087 | H2 | H | T8 |  | Double busbar | Indoor | WHITSON
WHSO22 | 275 | B-2-1c, B-3-1c | NGET | 51.5648 | -2.9087 | H2 | H | T8 |  | Double busbar | Indoor | WHITSON
WHSO2A | 275 | B-2-1c, B-3-1c | NGET | 51.5648 | -2.9087 | H2 | H | T8 |  | Double busbar | Indoor | WHITSON
WHSO2B | 275 | B-2-1c, B-3-1c | NGET | 51.5648 | -2.9087 | H2 | H | T8 |  | Double busbar | Indoor | WHITSON
WHSO31 | 33 | B-3-1c | NGET | 51.5648 | -2.9087 | H2 | H | T8 |  | Double busbar | Indoor | WHITSON
WHSO32 | 33 | B-3-1c | NGET | 51.5648 | -2.9087 | H2 | H | T8 |  | Double busbar | Indoor | WHITSON
WHSO41 | 400 | B-2-1c, B-3-1c | NGET | 51.5648 | -2.9087 | H2 | H | T8 |  | Double busbar | Indoor | WHITSON
WHSO4A | 400 | B-2-1c | NGET | 51.5648 | -2.9087 | H2 | H | T8 |  | Double busbar | Indoor | WHITSON
WHTB1S | 132 | B-2-1b, B-2-2a | SHET, SPT | 56.0896 | -4.8401 |  |  | T2 |  |  |  | WHISTLEFIELD BOUNDARY
WHTB1T | 132 | B-2-1b, B-2-2a | SHET, SPT | 56.0896 | -4.8401 |  |  | T2 |  |  |  | WHISTLEFIELD BOUNDARY
WHTL1S | 132 | B-2-1b, B-3-1b | SPT | 56.0896 | -4.8401 |  |  | T2 |  |  |  | WHISTLEFIELD
WHTL1T | 132 | B-2-1b, B-3-1b | SPT | 56.0896 | -4.8401 |  |  | T2 |  |  |  | WHISTLEFIELD
WHTL3- | 33 | B-3-1b | SPT | 56.0896 | -4.8401 |  |  | T2 |  |  |  | WHISTLEFIELD
WIBA21 | 275 | B-2-2c, B-3-1c | NGET | 53.4159 | -1.4139 | P3 | P | T4 |  | Single Switch Mesh | Outdoor | WINCOBANK
WIBA31 | 33 | B-3-1c | NGET | 53.4159 | -1.4139 | P3 | P | T4 |  | Single Switch Mesh | Outdoor | WINCOBANK
WIEN11 | 132 | B-3-1c | NGET | 52.5778 | -2.0495 | L2 | L | T5 |  |  |  | WILLENHALL
WIEN2A | 275 | B-2-1c, B-3-1c | NGET | 52.5778 | -2.0495 | L2 | L | T5 |  |  |  | WILLENHALL
WIEN2B | 275 | B-2-1c, B-3-1c | NGET | 52.5778 | -2.0495 | L2 | L | T5 |  |  |  | WILLENHALL
WILE41 | 400 | B-2-1c, B-3-1c, B-4-2c | NGET | 52.8556 | -1.5527 | L5 | L | T5 |  | Double busbar | Outdoor | WILLINGTON EAST
WILL11 | 132 | B-3-1c | NGET | 52.8554 | -1.5467 | L5 | L | T5 |  | Double busbar | Outdoor | WILLINGTON
WILL12 | 132 | B-3-1c | NGET | 52.8554 | -1.5467 | L5 | L | T5 |  | Double busbar | Outdoor | WILLINGTON
WILT2A | 275 | B-2-1c, B-3-1c | NGET | 54.5758 | -1.1318 | Q2 | Q | T3 |  | Teed Transformers | Outdoor | WILTON
WILT2B | 275 | B-2-1c, B-3-1c | NGET | 54.5758 | -1.1318 | Q2 | Q | T3 |  | Teed Transformers | Outdoor | WILTON
WILT2C | 275 | B-2-1c, B-3-1c | NGET | 54.5758 | -1.1318 | Q2 | Q | T3 |  | Teed Transformers | Outdoor | WILTON
WILT2D | 275 | B-2-1c, B-3-1c | NGET | 54.5758 | -1.1318 | Q2 | Q | T3 |  | Teed Transformers | Outdoor | WILTON
WIMB11 | 132 | B-3-1c | NGET | 51.4311 | -0.18917 | A4 | A | T11 |  | Four Switch Mesh | Indoor | WIMBLEDON
WIMB21 | 275 | B-2-1c, B-3-1c | NGET | 51.4311 | -0.18917 | A4 | A | T11 |  | Four Switch Mesh | Indoor | WIMBLEDON
WIMB41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 51.4311 | -0.18917 | A4 | A | T11 |  | Four Switch Mesh | Indoor | WIMBLEDON
WIOW1- | 132 | B-2-2a | SHET | 57.1539 | -2.0964 | T2 | T | T1 |  |  |  | WILLOWDALE
WIOW1Q | 132 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.1539 | -2.0964 | T2 | T | T1 |  |  |  | WILLOWDALE
WIOW1R | 132 | B-2-1a, B-2-2a, B-3-1a | SHET | 57.1539 | -2.0964 | T2 | T | T1 |  |  |  | WILLOWDALE
WIOW3- | 33 | B-3-1a | SHET | 57.1539 | -2.0964 | T2 | T | T1 |  |  |  | WILLOWDALE
WISD11 | 132 | B-3-1c | NGET | 51.5346 | -0.25716 | A7 | A | T11 |  | Double busbar | Indoor | WILLESDEN
WISD21 | 275 | B-3-1c, B-4-1c | NGET | 51.5346 | -0.25716 | A7 | A | T11 |  | Double busbar | Indoor | WILLESDEN
WISD2A | 275 | B-2-1c, B-3-1c | NGET | 51.5346 | -0.25716 | A7 | A | T11 |  | Double busbar | Indoor | WILLESDEN
WISD41 | 400 | B-2-1c, B-3-1c | NGET | 51.5346 | -0.25716 | A7 | A | T11 |  | Double busbar | Indoor | WILLESDEN
WISD42 | 400 | B-2-1c, B-3-1c | NGET | 51.5346 | -0.25716 | A7 | A | T11 |  | Double busbar | Indoor | WILLESDEN
WISD61 | 66 | B-3-1c | NGET | 51.5346 | -0.25716 | A7 | A | T11 |  | Double busbar | Indoor | WILLESDEN
WISH1- | 132 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.765 | -3.93 | S6 | S | T2 |  |  |  | WISHAW
WISH2- | 275 | B-2-1b, B-3-1b | SPT | 55.765 | -3.93 | S6 | S | T2 |  |  |  | WISHAW
WISH3- | 33 | B-3-1b | SPT | 55.765 | -3.93 | S6 | S | T2 |  |  |  | WISHAW
WISH3S | 33 | B-2-1b, B-3-1b | SPT | 55.765 | -3.93 | S6 | S | T2 |  |  |  | WISHAW
WISH3T | 33 | B-2-1b, B-2-2b, B-3-1b | SPT | 55.765 | -3.93 | S6 | S | T2 |  |  |  | WISHAW
WISH3W | 33 | B-4-1b | SPT | 55.765 | -3.93 | S6 | S | T2 |  |  |  | WISHAW
WISH4- | 400 | B-2-2b, B-3-1b | SPT | 55.765 | -3.93 | S6 | S | T2 |  |  |  | WISHAW
WIYH1- | 132 | B-2-1b, B-3-1b | SPT | 55.9315 | -4.3753 |  |  | T2 |  |  |  | WINDYHILL
WIYH2- | 275 | B-2-1b, B-2-2b, B-3-1b, B-3-2b, B-4-1b | SPT | 55.9315 | -4.3753 |  |  | T2 |  |  |  | WINDYHILL
WIYH2R | 275 | B-2-1b, B-2-2b | SPT | 55.9315 | -4.3753 |  |  | T2 |  |  |  | WINDYHILL
WIYH3W | 33 | B-4-1b | SPT | 55.9315 | -4.3753 |  |  | T2 |  |  |  | WINDYHILL
WIYH4Q | 400 | B-2-2b, B-3-1b, B-3-2b | SPT | 55.9315 | -4.3753 |  |  | T2 |  |  |  | WINDYHILL
WLEE2- | 275 | B-2-1b, B-3-1b | SPT | 55.6955 | -4.1725 |  |  | T2 |  |  |  | WHITELEE
WLEE3A | 33 | B-3-1b | SPT | 55.6955 | -4.1725 |  |  | T2 |  |  |  | WHITELEE
WLEE3B | 33 | B-3-1b | SPT | 55.6955 | -4.1725 |  |  | T2 |  |  |  | WHITELEE
WLEE3C | 33 | B-3-1b | SPT | 55.6955 | -4.1725 |  |  | T2 |  |  |  | WHITELEE
WLER2- | 275 | B-2-2b, B-3-2b | SPT | [8 empty] | WHITELEE REPOWERING
WLER3A | 33 | B-3-2b | SPT | [8 empty] | WHITELEE REPOWERING
WLER3C | 33 | B-3-2b | SPT | [8 empty] | WHITELEE REPOWERING
WLER3E | 33 | B-3-2b | SPT | [8 empty] | WHITELEE REPOWERING
WLEX2- | 275 | B-2-1b, B-3-1b | SPT | [8 empty] | WHITELEE EXTENSION
WLEX3A | 33 | B-3-1b | SPT | [8 empty] | WHITELEE EXTENSION
WLEX3B | 33 | B-3-1b | SPT | [8 empty] | WHITELEE EXTENSION
WLEX3C | 33 | B-3-1b | SPT | [8 empty] | WHITELEE EXTENSION
WMEL11 | 132 | B-3-1c | NGET | 53.5015 | -1.377 | P3 | P | T4 |  | Four Switch Mesh | Outdoor | WEST MELTON
WMEL12 | 132 | B-3-1c, B-4-1c | NGET | 53.5015 | -1.377 | P3 | P | T4 |  | Four Switch Mesh | Outdoor | WEST MELTON
WMEL21 | 275 | B-2-1c, B-3-1c | NGET | 53.5015 | -1.377 | P3 | P | T4 |  | Four Switch Mesh | Outdoor | WEST MELTON
WNUK1- | 132 | B-2-2b | SPT | [8 empty] | WHITENEUK
WOHI1Q | 132 | B-2-1a, B-3-1a | SHET | 57.1544 | -2.1469 | T2 | T | T1 |  |  |  | WOODHILL
WOHI1R | 132 | B-2-1a, B-3-1a | SHET | 57.1544 | -2.1469 | T2 | T | T1 |  |  |  | WOODHILL
WOHI3- | 33 | B-3-1a | SHET | 57.1544 | -2.1469 | T2 | T | T1 |  |  |  | WOODHILL
WTHU31 | 33 | B-3-1c | NGET | 51.4709 | 0.288 | A1 | A | T11 |  | Teed Transformers | Outdoor | WEST THURROCK
WTHU4A | 400 | B-2-1c, B-3-1c | NGET | 51.4709 | 0.288 | A1 | A | T11 |  | Teed Transformers | Outdoor | WEST THURROCK
WTHU4B | 400 | B-2-1c, B-3-1c | NGET | 51.4709 | 0.288 | A1 | A | T11 |  | Teed Transformers | Outdoor | WEST THURROCK
WTHU4C | 400 | B-2-1c | NGET | 51.4709 | 0.288 | A1 | A | T11 |  | Teed Transformers | Outdoor | WEST THURROCK
WTHU4D | 400 | B-2-1c | NGET | 51.4709 | 0.288 | A1 | A | T11 |  | Teed Transformers | Outdoor | WEST THURROCK
WTHU4E | 400 | B-2-1c | NGET | 51.4709 | 0.288 | A1 | A | T11 |  | Teed Transformers | Outdoor | WEST THURROCK
WTHU4F | 400 | B-2-1c | NGET | 51.4709 | 0.288 | A1 | A | T11 |  | Teed Transformers | Outdoor | WEST THURROCK
WWEY11 | 132 | B-3-1c | NGET | 51.3534 | -0.47958 | A8 | A | T11 |  | Teed Transformers | Outdoor | WEST WEYBRIDGE
WWEY12 | 132 | B-3-1c | NGET | 51.3534 | -0.47958 | A8 | A | T11 |  | Teed Transformers | Outdoor | WEST WEYBRIDGE
WWEY21 | 275 | B-2-1c, B-3-1c, B-4-1c | NGET | 51.3534 | -0.47958 | A8 | A | T11 |  | Teed Transformers | Outdoor | WEST WEYBRIDGE
WWEY22 | 275 | B-2-1c, B-3-1c | NGET | 51.3534 | -0.47958 | A8 | A | T11 |  | Teed Transformers | Outdoor | WEST WEYBRIDGE
WWEY2A | 275 | B-2-1c, B-3-1c | NGET | 51.3534 | -0.47958 | A8 | A | T11 |  | Teed Transformers | Outdoor | WEST WEYBRIDGE
WWEY4A | 400 | B-2-1c, B-3-1c | NGET | 51.3534 | -0.47958 | A8 | A | T11 |  | Teed Transformers | Outdoor | WEST WEYBRIDGE
WWEY4B | 400 | B-2-1c, B-3-1c | NGET | 51.3534 | -0.47958 | A8 | A | T11 |  | Teed Transformers | Outdoor | WEST WEYBRIDGE
WYLF11 | 132 | B-3-1c | NGET | 53.4152 | -4.4802 | M8 | M | T4 |  | Double busbar | Indoor | WYLFA
WYLF41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 53.4152 | -4.4802 | M8 | M | T4 |  | Double busbar | Indoor | WYLFA
WYLS41 | 400 | B-2-2c | NGET | 53.4162 | -4.4806 | M8 | M | T4 |  |  |  | WYLFA SOUTH
WYMO11 | 132 | B-3-1c | NGET | 51.9272 | -0.25028 | D5 | D | T6 |  | Double busbar | Outdoor | WYMONDLEY
WYMO41 | 400 | B-2-1c, B-2-2c, B-3-1c, B-4-1c | NGET | 51.9272 | -0.25028 | D5 | D | T6 |  | Double busbar | Outdoor | WYMONDLEY
YAXL41 | 400 | B-2-1c | NGET | 52.333 | 1.1046 | J7 | J | T7 |  |  |  | YAXLEY
YORK4A | 400 | B-2-2c, B-3-2c | NGET | 53.9566 | -1.0226 | P6 | P | T4 |  |  |  | YORK NORTH (Overton)
YORK4B | 400 | B-2-2c, B-3-2c | NGET | 53.9566 | -1.0226 | P6 | P | T4 |  |  |  | YORK NORTH (Overton)

## Cable
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Sheet_Name | Year | Status
ABBA1- | DYCE1J | 0 | 7.8 | Cable | 0.1092 | 1.2324 | 10.14 | 173 | 158 | 158 | 158 | B-2-1a
ABNE1Q | ABNE1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
ALNE1Q | FYRI1J | 0 | 2.1 | Cable | 0.06 | 0.202 | 2.547 | 156 | 142 | 142 | 142 | B-2-1a
ALNE1R | FYRI1K | 0 | 2.1 | Cable | 0.06 | 0.202 | 2.547 | 156 | 142 | 142 | 142 | B-2-1a
AMUL1E | AMUL1F | 0 | 8.62 | Cable | 0.2518 | 0.8041 | 10.215 | 153 | 129 | 129 | 129 | B-2-1a
AMUL1G | AMUL1H | 0 | 8.62 | Cable | 0.2518 | 0.8041 | 10.215 | 153 | 129 | 129 | 129 | B-2-1a
ARDK1- | INVE1J | 0 | 9 | Cable | 0.92 | 2.1 | 0.44 | 132 | 123 | 106 | 123 | B-2-1a
BEAT4- | BLHI4- | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
BEAU1J | BEAU1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
BEAU1J | BEAU1R | 0 | 2.4 | Cable | 0.0315 | 0.197 | 3.941 | 265 | 263 | 263 | 263 | B-2-1a
BEAU1J | BEAU1T | 0 | 0.22 | Cable | 0.01 | 0.0147 | 0.268 | 141 | 136 | 136 | 136 | B-2-1a
BEAU1J | DUCC1J | 0 | 3.1 | Cable | 0.0219 | 0.1198 | 10.47 | 444 | 403 | 403 | 403 | B-2-1a
BEAU1K | BEAU1N | 0 | 0.25 | Cable | 0.01 | 0.0167 | 0.305 | 141 | 136 | 136 | 136 | B-2-1a
BEAU1K | BEAU1S | 0 | 2.4 | Cable | 0.0315 | 0.197 | 3.941 | 265 | 263 | 263 | 263 | B-2-1a
BEAU1K | DUCC1K | 0 | 3.1 | Cable | 0.0219 | 0.1198 | 10.47 | 444 | 403 | 403 | 403 | B-2-1a
BEAU1L | BEAU1P | 0 | 1.74 | Cable | 0.0634 | 0.1599 | 2.062 | 152 | 140 | 140 | 140 | B-2-1a
BEAU1M | BEAU1Q | 0 | 1.74 | Cable | 0.0634 | 0.1599 | 2.062 | 152 | 140 | 140 | 140 | B-2-1a
BEAU2J | BEAU2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
BHLA11 | GLEN1Q | 0 | 7.8 | Cable | 0.1425 | 0.6104 | 28.363 | 208 | 187 | 187 | 187 | B-2-1a
BLHI1J | BLHI1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
BLHI1J | KEIT1K | 0 | 3.26 | Cable | 0.0429 | 0.2582 | 4.733 | 176 | 176 | 176 | 176 | B-2-1a
BLHI1K | KEIT1J | 0 | 3.26 | Cable | 0.0429 | 0.2582 | 4.733 | 176 | 176 | 176 | 176 | B-2-1a
BLHI2J | BLHI2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
BLHI2J | KEIT2Q | 0 | 2.41 | Cable | 0.01 | 0.044 | 13.793 | 580 | 546 | 546 | 546 | B-2-1a
BLHI2K | KEIT2R | 0 | 2.49 | Cable | 0.01 | 0.0456 | 14.286 | 580 | 546 | 546 | 546 | B-2-1a
BLHI4- | BLHI4R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 1272 | 1272 | 1272 | 1272 | B-2-1a
BLHI4- | MOWO4- | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
BOAG1L | BOAG1Q | 0 | 5.7 | Cable | 0.0362 | 0.8819 | 7.98 | 227 | 209 | 209 | 209 | B-2-1a
BOAG1M | BOAG1R | 0 | 5.7 | Cable | 0.0362 | 0.8819 | 7.98 | 227 | 209 | 209 | 209 | B-2-1a
BOAG1P | BOAG1Q | 0 | 8.4 | Cable | 0.0558 | 1.271 | 11.48 | 227 | 209 | 209 | 209 | B-2-1a
BOAG1P | GLFA1- | 0 | 24.82 | Cable | 2.5189 | 5.7753 | 1.228 | 126 | 117 | 101 | 117 | B-2-1a
BREC1Q | BREC1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
BUMU1Q | BUMU1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
BUMU1Q | CHAR1- | 0 | 42.2 | Cable | 4.29 | 9.76 | 2.1 | 132 | 123 | 106 | 123 | B-2-1a
CHAR1- | CHAR1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 229 | 211 | 183 | 211 | B-2-1a
CHAR1- | CHAR1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117 | B-2-1a
CHAR1- | CHAR1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117 | B-2-1a
CLAY1Q | WIOW1Q | 0 | 2.1 | Cable | 0.0474 | 0.1253 | 2.897 | 155 | 129 | 129 | 129 | B-2-1a
CLAY1R | WIOW1R | 0 | 2.1 | Cable | 0.0474 | 0.1253 | 2.897 | 155 | 129 | 129 | 129 | B-2-1a
CLUN1Q | CLUN1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117 | B-2-1a
CLUN1R | CLUN1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117 | B-2-1a
COGA1C | FARI1J | 0 | 4.11 | Cable | 0.065 | 0.334 | 6.245 | 210 | 196 | 196 | 196 | B-2-1a
CORI1J | CORI1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
CORI1J | CORI1P | 0 | 0.71 | Cable | 0.0216 | 0.0662 | 0.84 | 126 | 116 | 116 | 116 | B-2-1a
CORI1K | CORI1Q | 0 | 0.63 | Cable | 0.0191 | 0.0586 | 0.742 | 126 | 116 | 116 | 116 | B-2-1a
CRAI1- | CRAI1P | 0 | 1.1 | Cable | 0.0309 | 0.0973 | 1.456 | 149 | 137 | 137 | 137 | B-2-1a
CRAI1- | CRAI1Q | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 145 | 131 | 116 | 131 | B-2-1a
CRAI1- | CRAI1R | 0 | 1.1 | Cable | 0.0309 | 0.0973 | 1.456 | 149 | 137 | 137 | 137 | B-2-1a
CRAI1- | WOHI1Q | 0 | 3.5 | Cable | 0.15 | 0.22 | 7.5 | 130 | 120 | 120 | 120 | B-2-1a
CRAI1- | WOHI1R | 0 | 3.5 | Cable | 0.15 | 0.22 | 7.5 | 130 | 120 | 120 | 120 | B-2-1a
CREA1A | CREA1B | 0 | 1.4 | Cable | 0.0149 | 0.0892 | 2.161 | 306 | 253 | 253 | 253 | B-2-1a
CRSS1J | CRSS1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
CRSS2A | CRSS2C | 0 | 1.61 | Cable | 0.0178 | 0.0531 | 4.45 | 240 | 240 | 240 | 240 | B-2-1a
CRSS2B | CRSS2D | 0 | 1.66 | Cable | 0.0178 | 0.056 | 4.57 | 240 | 240 | 240 | 240 | B-2-1a
CRSS2C | HUNN2C | 0 | 38.1 | Cable | 0.6045 | 1.1463 | 76.848 | 240 | 240 | 240 | 240 | B-2-1a
CRSS2D | HUNN2D | 0 | 38.5 | Cable | 0.6157 | 1.1674 | 78.263 | 240 | 240 | 240 | 240 | B-2-1a
DLCH1A | DLCH1B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
DLCH1A | LAIR1- | 0 | 4.52 | Cable | 0.458 | 1.089 | 0.215 | 111 | 103 | 89 | 103 | B-2-1a
DLCH1A | LAIR1- | 0 | 4.52 | Cable | 0.458 | 1.089 | 0.215 | 111 | 103 | 89 | 103 | B-2-1a
DUNM1C | FARI1K | 0 | 4.07 | Cable | 0.064 | 0.28 | 6.175 | 210 | 196 | 196 | 196 | B-2-1a
DYCE1Q | DYCE1T | 0 | 1.3 | Cable | 0.0455 | 0.0543 | 2.428 | 150 | 143 | 143 | 143 | B-2-1a
DYCE1R | DYCE1U | 0 | 1.3 | Cable | 0.0455 | 0.0543 | 2.428 | 150 | 143 | 143 | 143 | B-2-1a
ELGI1L | ELGI1Q | 0 | 1.8 | Cable | 0.0236 | 0.1477 | 2.956 | 251 | 252 | 252 | 252 | B-2-1a
ELGI1M | ELGI1R | 0 | 1.8 | Cable | 0.0236 | 0.1477 | 2.956 | 251 | 252 | 252 | 252 | B-2-1a
ERRO1A | ERRO1J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 240 | 240 | 240 | 240 | B-2-1a
ERRO1A | TUMM1J | 0 | 1.33 | Cable | 0.014 | 0.098 | 2.572 | 300 | 280 | 280 | 280 | B-2-1a
ERRO1B | ERRO1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 240 | 240 | 240 | 240 | B-2-1a
ERRO1B | TUMM1K | 0 | 1.3 | Cable | 0.013 | 0.095 | 2.51 | 300 | 280 | 280 | 280 | B-2-1a
ERRO1J | ERRO1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
ERRO1J | ERRO1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
FAUG1- | FAUG1Q | 0 | 1 | Cable | 0.01 | 0.012 | 0.002 | 126 | 117 | 101 | 117 | B-2-1a
FAUG1- | GLDO1G | 0 | 6 | Cable | 0.21 | 0.47 | 5.91 | 127 | 127 | 127 | 127 | B-2-1a
FAUG1J | FAUG1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
FAUG4J | FAUG4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
FIDD1A | FIDD1Q | 0 | 0.55 | Cable | 0.0192 | 0.02 | 1.03 | 180 | 180 | 171 | 180 | B-2-1a
FIDD1B | FIDD1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
FIDD1Q | FIDD1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
FYRI1J | FYRI1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
GLKO1- | TOMT1K | 0 | 3 | Cable | 0.417 | 0.627 | 0.156 | 83 | 77 | 67 | 77 | B-2-1a
INNE1J | INNE1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
INNE1J | KNOC1J | 0 | 4.57 | Cable | 0.1051 | 0.3818 | 6.326 | 155 | 150 | 150 | 150 | B-2-1a
INNE1K | INNE1L | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
INNE1L | KNOC1J | 0 | 4.48 | Cable | 0.1042 | 0.3784 | 6.27 | 155 | 150 | 150 | 150 | B-2-1a
INRU1S | PEHE1- | 0 | 3 | Cable | 0.0687 | 0.2536 | 4.105 | 186 | 186 | 186 | 186 | B-2-1a
INVE1J | INVE1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
INVR1A | INVR1C | 0 | 4.4 | Cable | 0.1393 | 0.4267 | 5.615 | 130 | 126 | 126 | 126 | B-2-1a
INVR1B | INVR1D | 0 | 4.4 | Cable | 0.1396 | 0.4277 | 5.627 | 130 | 126 | 126 | 126 | B-2-1a
KEIT3- | KEIT3A | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
KERG1- | KERG1J | 0 | 0.17 | Cable | 0.0019 | 0.0098 | 0.298 | 370 | 370 | 370 | 370 | B-2-1a
KERG1- | KERG1J | 0 | 0.17 | Cable | 0.0019 | 0.0098 | 0.298 | 370 | 370 | 370 | 370 | B-2-1a
KERG1J | KERG1K | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
KERG1J | KERG1K | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
KERG1J | KERG1P | 0 | 0.09 | Cable | 0.0017 | 0.0085 | 0.149 | 234 | 234 | 234 | 234 | B-2-1a
KERG1J | KERG1Q | 0 | 0.15 | Cable | 0.0027 | 0.0137 | 0.241 | 234 | 234 | 234 | 234 | B-2-1a
KERG1J | KERG1T | 0 | 0.12 | Cable | 0.0013 | 0.0069 | 0.21 | 220 | 220 | 220 | 220 | B-2-1a
KERG1K | KERG1R | 0 | 0.08 | Cable | 0.0014 | 0.0072 | 0.127 | 234 | 234 | 234 | 234 | B-2-1a
KINT1- | KINT1B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
KINT1- | KINT1P | 0 | 0.27 | Cable | 0.01 | 0.0154 | 0.354 | 148 | 140 | 140 | 140 | B-2-1a
KINT1- | KINT1R | 0 | 0.26 | Cable | 0.01 | 0.0148 | 0.341 | 148 | 140 | 140 | 140 | B-2-1a
KINT1- | KINT1T | 0 | 0.6 | Cable | 0.0135 | 0.0343 | 0.787 | 165 | 141 | 141 | 141 | B-2-1a
KINT1- | KINT1U | 0 | 0.6 | Cable | 0.0135 | 0.0343 | 0.787 | 165 | 141 | 141 | 141 | B-2-1a
KINT2J | KINT2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
KNOC2J | KNOC2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
KNOC2J | KNOC2L | 0 | 1.47 | Cable | 0.01 | 0.042 | 8.36 | 930 | 900 | 900 | 900 | B-2-1a
KNOC2J | KNOC2N | 0 | 0.51 | Cable | 0.01 | 0.0157 | 3.005 | 850 | 793 | 793 | 793 | B-2-1a
KNOC2K | KNOC2M | 0 | 1.29 | Cable | 0.01 | 0.037 | 7.336 | 930 | 900 | 900 | 900 | B-2-1a
KNOC2K | KNOC2P | 0 | 0.17 | Cable | 0.01 | 0.01 | 1.006 | 850 | 793 | 793 | 793 | B-2-1a
LOCB1J | LOCB1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
LOCB1J | LOCB1L | 0 | 0.83 | Cable | 0.01 | 0.0635 | 1.489 | 373 | 373 | 373 | 373 | B-2-1a
LOCB1J | LOCB1S | 0 | 0.79 | Cable | 0.022 | 0.0694 | 1.039 | 149 | 137 | 137 | 137 | B-2-1a
LOCB1J | LOCB1S | 0 | 0.785 | Cable | 0.022 | 0.0694 | 1.0394 | 149 | 137 | 137 | 137 | B-2-1a
LOCB1J | LOCB1U | 0 | 0.38 | Cable | 0.0105 | 0.0332 | 0.496 | 149 | 137 | 137 | 137 | B-2-1a
LOCB1K | LOCB1M | 0 | 0.92 | Cable | 0.01 | 0.0704 | 1.651 | 373 | 373 | 373 | 373 | B-2-1a
LOCB1K | LOCB1R | 0 | 0.73 | Cable | 0.0204 | 0.0641 | 0.96 | 149 | 137 | 137 | 137 | B-2-1a
LOCB1K | LOCB1T | 0 | 0.28 | Cable | 0.008 | 0.0252 | 0.377 | 149 | 137 | 137 | 137 | B-2-1a
LOCB2J | LOCB2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
MELG1J | MELG1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
MELG1J | STRL1- | 0 | 10 | Cable | 0.0752 | 0.806 | 18.176 | 317 | 277 | 277 | 277 | B-2-1a
MELG4J | MELG4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
MILC1R | MILC1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
MILC1R | MILC1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
MILC1S | MILC1V | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
MORF4- | NEDE4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
MYBS3M | MYBS3N | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
NEDE4J | NEDE4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
ORRI1Q | ORRI1S | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117 | B-2-1a
ORRI1R | ORRI1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 126 | 117 | 101 | 117 | B-2-1a
PEHE4J | PEHE4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
PERS1Q | PERS1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
PERS1Q | WIOW1R | 0 | 3.7 | Cable | 0.084 | 0.221 | 5.104 | 155 | 129 | 129 | 129 | B-2-1a
PERS1R | WIOW1Q | 0 | 3.7 | Cable | 0.084 | 0.221 | 5.104 | 155 | 129 | 129 | 129 | B-2-1a
PERS2Q | PERS2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
ROTI4J | ROTI4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
SFEE1A | SFEE1C | 0 | 0.27 | Cable | 0.0077 | 0.0304 | 0.351 | 47 | 47 | 47 | 47 | B-2-1a
SFEE1B | SFEE1D | 0 | 0.29 | Cable | 0.0084 | 0.0303 | 0.383 | 47 | 47 | 47 | 47 | B-2-1a
SFEG1Q | SFEV1S | 0 | 0.4 | Cable | 0.01 | 0.034 | 0.46 | 160 | 135 | 135 | 135 | B-2-1a
SFEG1R | SFEV1T | 0 | 0.4 | Cable | 0.01 | 0.034 | 0.46 | 160 | 135 | 135 | 135 | B-2-1a
SFER1J | SFER1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
SFER1J | SFER1M | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
SFER1K | SFER1L | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
SFER1L | SFER1M | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 100 | 100 | 100 | 100 | B-2-1a
SFEV1S | SFEV1T | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 100 | 100 | 100 | 100 | B-2-1a
SGRX2- | TEAL2K | 0 | 1 | Cable | 0.01 | 0.1 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
SLKB1J | SLKB1L | 0 | 1.5 | Cable | 0.0159 | 0.0956 | 2.316 | 306 | 253 | 253 | 253 | B-2-1a
SLKB1K | SLKB1M | 0 | 1.5 | Cable | 0.0159 | 0.0956 | 2.316 | 306 | 253 | 253 | 253 | B-2-1a
SLOY1A | SLOY1K | 0 | 0.92 | Cable | 0.0279 | 0.0856 | 1.126 | 120 | 112 | 112 | 112 | B-2-1a
SLOY1B | SLOY1K | 0 | 0.91 | Cable | 0.0277 | 0.0848 | 1.1158 | 120 | 112 | 112 | 112 | B-2-1a
SLOY1C | SLOY1J | 0 | 0.835 | Cable | 0.0254 | 0.0778 | 1.0238 | 120 | 112 | 112 | 112 | B-2-1a
SLOY1D | SLOY1J | 0 | 0.867 | Cable | 0.0264 | 0.0808 | 1.0631 | 120 | 112 | 112 | 112 | B-2-1a
SLOY1E | SLOY1J | 0 | 1.28 | Cable | 0.0389 | 0.1193 | 1.5695 | 140 | 132 | 132 | 132 | B-2-1a
SLOY1F | SLOY1K | 0 | 1.37 | Cable | 0.0417 | 0.1277 | 1.6798 | 140 | 132 | 132 | 132 | B-2-1a
SLOY1J | SLOY1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
SPIT2J | SPIT2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
SPIT2K | SPIT2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 960 | 960 | 960 | 960 | B-2-1a
STRW1- | STRW1A | 0 | 0.35 | Cable | 0.01 | 0.0631 | 0.48 | 200 | 178 | 178 | 178 | B-2-1a
TEAL2A | TEAL2J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
TEAL2B | TEAL2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
TEAL2J | TEAL2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
TEAL2J | WFIB2- | 0 | 38.8 | Cable | 0.19 | 1.67 | 10.2 | 1090 | 1030 | 925 | 1030 | B-2-1a
THUS1J | THUS1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
TOMT1J | TOMT1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1a
TOMT1J | TOMT1M | 0 | 0.14 | Cable | 0.29 | 1.59 | 18.77 | 261 | 237 | 237 | 237 | B-2-1a
TOMT1K | TOMT1L | 0 | 0.13 | Cable | 0.27 | 1.5 | 17.6 | 261 | 237 | 237 | 237 | B-2-1a
WHIB1A | WHIB1C | 0 | 2.93 | Cable | 0.0896 | 0.2773 | 3.437 | 153 | 140 | 140 | 140 | B-2-1a
WHIB1B | WHIB1D | 0 | 2.93 | Cable | 0.0896 | 0.2773 | 3.437 | 153 | 140 | 140 | 140 | B-2-1a
WHIB1E | WHIB1G | 0 | 0.44 | Cable | 0.0134 | 0.0416 | 0.515 | 153 | 140 | 140 | 140 | B-2-1a
WHIB1F | WHIB1H | 0 | 0.44 | Cable | 0.0134 | 0.0416 | 0.515 | 153 | 140 | 140 | 140 | B-2-1a
WIOW1Q | WOHI1Q | 0 | 3.4 | Cable | 0.075 | 0.29 | 3.908 | 174 | 147 | 147 | 147 | B-2-1a
WIOW1R | WOHI1R | 0 | 3.4 | Cable | 0.075 | 0.29 | 3.908 | 174 | 147 | 147 | 147 | B-2-1a
AUCW1- | HADH1- | 0 | 18 | Cable | 1.83 | 3.88 | 0.96 | 140 | 140 | 140 | 140 | B-2-1b
AUCW1- | MAYB1- | 0 | 0.07 | Cable | 0 | 0.009 | 0.0682 | 140 | 140 | 140 | 140 | B-2-1b
BRAP1- | GOVA1R | 0 | 6.13 | Cable | 0.2168 | 0.45 | 11.0073 | 125 | 113 | 110 | 113 | B-2-1b
BROT1- | COAL1- | 0 | 3.2 | Cable | 0.0261 | 0.2614 | 5.959 | 293 | 293 | 293 | 293 | B-2-1b
BUSB2- | GIFF2Q | 0 | 5 | Cable | 0.037 | 0.134 | 19.636 | 276 | 240 | 240 | 240 | B-2-1b
BUSB2- | GIFF2R | 0 | 5 | Cable | 0.037 | 0.134 | 19.636 | 276 | 240 | 240 | 240 | B-2-1b
CATY1Q | DALM1- | 0 | 4.65 | Cable | 0.1313 | 0.3018 | 6.1089 | 122 | 107 | 107 | 107 | B-2-1b
CATY1R | DALM1- | 0 | 4.65 | Cable | 0.1313 | 0.3018 | 6.1089 | 122 | 107 | 107 | 107 | B-2-1b
CCSS1- | COAL1- | 0 | 6.97 | Cable | 0.10961 | 0.60003 | 11.4841 | 210 | 210 | 210 | 210 | B-2-1b
CHAS2Q | DALM2Q | 0 | 4.05 | Cable | 0.049 | 0.065 | 20.456 | 186 | 186 | 186 | 186 | B-2-1b
CHAS2R | DALM2R | 0 | 4.05 | Cable | 0.049 | 0.065 | 20.456 | 186 | 186 | 186 | 186 | B-2-1b
CLYN2Q | ELVA2Q | 0 | 6.2 | Cable | 0.032 | 0.174 | 26.956 | 476 | 415 | 415 | 415 | B-2-1b
CLYS2R | ELVA2R | 0 | 7.17 | Cable | 0.0445 | 0.1289 | 23.8486 | 291 | 245 | 245 | 245 | B-2-1b
CLYS3B | CLYS3X | 0 | 0.05 | Cable | 0.0084 | 0.0315 | 0.0106 | 52 | 52 | 52 | 52 | B-2-1b
COAL1B | CCSS1- | 0 | 6.97 | Cable | 0.10961 | 0.60003 | 11.4841 | 210 | 210 | 210 | 210 | B-2-1b
COAL1B | KYPE1- | 0 | 17.09 | Cable | 0.3286 | 1.5387 | 24.4568 | 194 | 180 | 180 | 180 | B-2-1b
CRYR1A | WESE1- | 0 | 3.989 | Cable | 0.0559 | 0.3473 | 5.1163 | 155 | 155 | 155 | 155 | B-2-1b
DALM1- | SANX1Q | 0 | 5.16 | Cable | 0.1457 | 0.1955 | 6.7791 | 181 | 164 | 164 | 164 | B-2-1b
DALM1- | SANX1R | 0 | 5.78 | Cable | 0.1632 | 0.2189 | 7.5936 | 181 | 164 | 164 | 164 | B-2-1b
DEWP2Q | WHHO2Q | 0 | 2.48 | Cable | 0.0159 | 0.0559 | 7.7539 | 276 | 240 | 240 | 240 | B-2-1b
DEWP2R | WHHO2R | 0 | 2.55 | Cable | 0.0164 | 0.0575 | 7.9728 | 276 | 240 | 240 | 240 | B-2-1b
DONO3A | HAGH3- | 0 | 7.5 | Cable | 1.0376 | 3.279 | 1.7603 | 40 | 38 | 38 | 38 | B-2-1b
DUNE3- | TODD3- | 0 | 6.07 | Cable | 2.245 | 5.682 | 0.73 | 42 | 42 | 42 | 42 | B-2-1b
DUNH1Q | DUNH1S | 0 | 0.336 | Cable | 0.0168 | 0.037 | 0.2759 | 159 | 147 | 147 | 147 | B-2-1b
DUNH1R | DUNH1T | 0 | 0.372 | Cable | 0.0186 | 0.0409 | 0.3054 | 159 | 147 | 147 | 147 | B-2-1b
EKIS2- | WLEE2- | 0 | 6 | Cable | 0.034 | 0.101 | 25.635 | 378 | 378 | 378 | 378 | B-2-1b
EKIS2- | WLEX2- | 0 | 16.68 | Cable | 0.088 | 0.346 | 70.948 | 340 | 340 | 340 | 340 | B-2-1b
ENHI1- | NECU1C | 0 | 4.4 | Cable | 0.1242 | 0.2856 | 5.7805 | 134 | 123 | 123 | 123 | B-2-1b
ESST1- | PART1Q | 0 | 6.9 | Cable | 0.137 | 0.641 | 9.143 | 210 | 200 | 190 | 200 | B-2-1b
ESST1- | WIYH1- | 0 | 3.59 | Cable | 0.0711 | 0.3255 | 5.0111 | 233 | 200 | 200 | 200 | B-2-1b
ESST1Q | PART1R | 0 | 6.84 | Cable | 0.136 | 0.635 | 9.062 | 203 | 190 | 190 | 190 | B-2-1b
ESST1Q | WIYH1- | 0 | 3.16 | Cable | 0.178 | 0.334 | 7.691 | 203 | 190 | 190 | 190 | B-2-1b
FINN1Q | PART1Q | 0 | 2.813 | Cable | 0.0563 | 0.1582 | 4.0035 | 171 | 152 | 152 | 152 | B-2-1b
FINN1R | PART1R | 0 | 2.845 | Cable | 0.057 | 0.16 | 4.0491 | 171 | 152 | 152 | 152 | B-2-1b
GAWH3- | HAHA3- | 0 | 5 | Cable | 1.6871 | 4.5198 | 0.5324 | 36 | 34 | 34 | 34 | B-2-1b
GLGL1Q | SAKN1- | 0 | 9 | Cable | 0.2541 | 0.5842 | 11.0847 | 166 | 166 | 166 | 166 | B-2-1b
GLGL3- | SNQR3- | 0 | 2.3 | Cable | 0.6364 | 2.0111 | 0.2699 | 30 | 30 | 30 | 30 | B-2-1b
GLGL3- | WHLL3- | 0 | 1.2 | Cable | 0.332 | 1.5811 | 0.1408 | 30 | 30 | 30 | 30 | B-2-1b
GOVA1Q | HAGR1Q | 0 | 4.04 | Cable | 0.2097 | 0.252 | 6.0812 | 70 | 64 | 64 | 64 | B-2-1b
GOVA1R | HAGR1R | 0 | 4.11 | Cable | 0.187 | 0.225 | 3.587 | 69 | 64 | 64 | 64 | B-2-1b
GRMO3A | GRMO3C | 0 | 1 | Cable | 0.017 | 0.047 | 0.066 | 1000 | 1000 | 1000 | 1000 | B-2-1b
GRMO3A | GRMO3C | 0 | 1 | Cable | 0.012 | 0.035 | 0.049 | 1000 | 1000 | 1000 | 1000 | B-2-1b
HARR3- | KYPE3A | 0 | 0.5 | Cable | 0.0692 | 0.2186 | 0.1174 | 40 | 38 | 38 | 38 | B-2-1b
HUER4- | HUNE4- | 0 | 0.25 | Cable | 0.0001 | 0.001 | 0.7263 | 2770 | 2770 | 2770 | 2770 | B-2-1b
HUER4- | HUNE4- | 0 | 0.25 | Cable | 0.0001 | 0.001 | 0.7263 | 2770 | 2770 | 2770 | 2770 | B-2-1b
HUNE4- | HUNN4A | 0 | 0.259 | Cable | 0.0008 | 0.0027 | 1.7445 | 607 | 607 | 607 | 607 | B-2-1b
HUNE4- | HUNN4B | 0 | 0.177 | Cable | 0.0005 | 0.0019 | 1.1922 | 607 | 607 | 607 | 607 | B-2-1b
HUNN2A | HUNN2C | 0 | 3.356 | Cable | 0.0212 | 0.1068 | 11.7957 | 240 | 240 | 240 | 240 | B-2-1b
HUNN2B | HUNN2D | 0 | 3.413 | Cable | 0.0216 | 0.1087 | 11.9781 | 240 | 240 | 240 | 240 | B-2-1b
INVB2A | INVR2- | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 1000 | 1000 | 1000 | B-2-1b
INVB2B | INVR2- | 0 | 1 | Cable | 0 | 0.011 | 0 | 1000 | 1000 | 1000 | 1000 | B-2-1b
KAIM2- | WHHO2Q | 0 | 6.455 | Cable | 0.0415 | 0.1456 | 20.1821 | 276 | 240 | 240 | 240 | B-2-1b
KAIM2- | WHHO2R | 0 | 6.297 | Cable | 0.0405 | 0.1421 | 19.6881 | 276 | 240 | 240 | 240 | B-2-1b
KILB1Q | WIYH1- | 0 | 3.38 | Cable | 0.098 | 0.209 | 4.333 | 139 | 126 | 113 | 126 | B-2-1b
KILB1R | WIYH1- | 0 | 3.29 | Cable | 0.115 | 0.199 | 8.02 | 139 | 126 | 113 | 126 | B-2-1b
KILG2- | MAHI2- | 0 | 14 | Cable | 0.0719 | 0.2998 | 53.9497 | 352 | 290 | 290 | 290 | B-2-1b
MEAD1- | MEAD1Q | 0 | 1 | Cable | 0.023 | 0.032 | 0.314 | 100 | 100 | 100 | 100 | B-2-1b
MEAD1- | MEAD1R | 0 | 1 | Cable | 0.023 | 0.032 | 0.314 | 100 | 100 | 100 | 100 | B-2-1b
MINN3- | MOFF3A | 0 | 12.34 | Cable | 4.1636 | 17.1281 | 1.314 | 31 | 29 | 29 | 29 | B-2-1b
MOSH1Q | MOSM1A | 0 | 1.03 | Cable | 0.048 | 0.063 | 2.012 | 132 | 123 | 106 | 123 | B-2-1b
MOSH1R | MOSM1B | 0 | 0.96 | Cable | 0.044 | 0.057 | 1.826 | 132 | 123 | 106 | 123 | B-2-1b
NECU1- | SOKY1- | 0 | 4.2 | Cable | 0.0458 | 0.2435 | 7.265 | 242 | 223 | 192 | 223 | B-2-1b
NEIL1- | NEIL1C | 0 | 0.32 | Cable | 0 | 0.0126 | 0 | 416 | 389 | 389 | 389 | B-2-1b
NEIL2- | NEIL2C | 0 | 0.2 | Cable | 0.0007 | 0.003 | 1.492 | 1140 | 945 | 945 | 945 | B-2-1b
NOKY1- | NECU1- | 0 | 1.3 | Cable | 0.0084 | 0.0773 | 2.2771 | 261 | 261 | 261 | 261 | B-2-1b
POOB2Q | SHRU2Q | 0 | 4.96 | Cable | 0.032 | 0.103 | 30.572 | 270 | 270 | 270 | 270 | B-2-1b
POOB2R | SHRU2R | 0 | 4.96 | Cable | 0.032 | 0.103 | 30.572 | 270 | 270 | 270 | 270 | B-2-1b
PORD2Q | WGEO2Q | 0 | 1.83 | Cable | 0.017 | 0.056 | 12.236 | 305 | 198 | 198 | 198 | B-2-1b
PORD2R | WGEO2R | 0 | 2.15 | Cable | 0.014 | 0.049 | 10.691 | 305 | 198 | 198 | 198 | B-2-1b
RAVE3S | WISH3S | 0 | 4.1 | Cable | 0.9601 | 1.9766 | 0.01 | 32 | 32 | 32 | 32 | B-2-1b
RAVE3T | WISH3T | 0 | 4.1 | Cable | 0.9601 | 1.9766 | 0.01 | 32 | 32 | 32 | 32 | B-2-1b
BEDD4A | ROWD42 | 0 | 10.1 | Cable | 0.0071 | 0.1292 | 121.8435 | 1309 | 1309 | 1309 | 1309 | B-2-1c
BEDD4B | ROWD41 | 0 | 10.1 | Cable | 0.0069 | 0.1275 | 124.3819 | 1417 | 1417 | 1220 | 1294 | B-2-1c
BIRK21 | LISD2A | 0 | 12.891 | Cable | 0.0271 | 0.2978 | 125.0427 | 817 | 817 | 739 | 739 | B-2-1c
CAMA11 | IROA13 | 0 | 1 | Cable | 0.815 | 5.549 | 1.802 | 246 | 228 | 198 | 228 | B-2-1c
CAMA12 | IROA12 | 0 | 1 | Cable | 0.815 | 5.549 | 1.802 | 246 | 228 | 198 | 228 | B-2-1c
CANT41 | CANT41 | 0 | 0.1 | Cable | 0.0001 | 0.0012 | 1.0915 | 3102 | 3102 | 3102 | 3102 | B-2-1c
CANT41 | CANT41 | 0 | 0.1 | Cable | 0.0001 | 0.0012 | 1.0915 | 3102 | 3102 | 3102 | 3102 | B-2-1c
CANT41 | CANT41 | 0 | 0.1 | Cable | 0.0001 | 0.0012 | 1.0915 | 3102 | 3102 | 3102 | 3102 | B-2-1c
CAPE1A | INCE11 | 0 | 1 | Cable | 0.2226 | 2.0652 | 3.2486 | 258 | 258 | 240 | 240 | B-2-1c
CAPE1B | INCE11 | 0 | 1 | Cable | 0.2204 | 2.0451 | 3.2416 | 240 | 240 | 240 | 240 | B-2-1c
CHIL41 | FAWL41 | 0 | 3.73 | Cable | 0.0037 | 0.0235 | 56.9944 | 970 | 928 | 800 | 928 | B-2-1c
CHIL41 | FAWL41 | 0 | 3.69 | Cable | 0.0037 | 0.0232 | 56.3832 | 970 | 928 | 800 | 928 | B-2-1c
CITR41 | CITR41 | 0 | 0.1 | Cable | 0.0001 | 0.0008 | 1.8 | 1733 | 1492 | 1362 | 1492 | B-2-1c
CITR41 | CITR41 | 0 | 0.1 | Cable | 0.0001 | 0.0008 | 1.8 | 1566 | 1538 | 1351 | 1424 | B-2-1c
CITR41 | PUDM41 | 0 | 7.29 | Cable | 0.0066 | 0.0598 | 131.22 | 1282 | 1136 | 984 | 1136 | B-2-1c
CITR41 | SJOW41 | 0 | 7.243 | Cable | 0.0065 | 0.0594 | 130.374 | 1282 | 1136 | 984 | 1136 | B-2-1c
CITR41 | SJOW41 | 0 | 6.776 | Cable | 0.0061 | 0.0556 | 121.968 | 1282 | 1136 | 984 | 1136 | B-2-1c
CITR41 | WHAM4B | 0 | 9.39 | Cable | 0.0085 | 0.077 | 169.02 | 1282 | 1136 | 984 | 1136 | B-2-1c
CONQ41 | FLIB41 | 0 | 3.495 | Cable | 0.0022 | 0.05 | 43.9195 | 1438 | 1438 | 1389 | 1389 | B-2-1c
CONQ41 | FLIB41 | 0 | 3.388 | Cable | 0.0022 | 0.0485 | 42.5749 | 1438 | 1438 | 1389 | 1389 | B-2-1c
DAMC41 | KINO41 | 0 | 0.919 | Cable | 0.0001 | 0.0005 | 2.6467 | 1528 | 1528 | 1528 | 1528 | B-2-1c
DINO41 | PENT41 | 0 | 10.605 | Cable | 0.0056 | 0.153 | 133.2664 | 1604 | 1571 | 1571 | 1571 | B-2-1c
DINO41 | PENT41 | 0 | 10.762 | Cable | 0.0057 | 0.1552 | 135.2393 | 1604 | 1604 | 1557 | 1557 | B-2-1c
EALI21 | LALE21 | 0 | 19.658 | Cable | 0.0531 | 0.3912 | 167.2896 | 524 | 518 | 401 | 401 | B-2-1c
EALI21 | LALE21 | 0 | 19.658 | Cable | 0.0531 | 0.3912 | 167.2896 | 525 | 525 | 426 | 426 | B-2-1c
EALI21 | WISD2A | 0 | 6.075 | Cable | 0.0121 | 0.1391 | 61.5397 | 750 | 750 | 735 | 735 | B-2-1c
ELST12 | HEND11 | 0 | 1 | Cable | 0.081 | 0.634 | 16.01 | 299 | 275 | 218 | 275 | B-2-1c
ELST41 | SJOW41 | 0 | 20 | Cable | 0.014 | 0.176 | 244.29 | 1767 | 1732 | 1663 | 1732 | B-2-1c
FRIN4A | FRIS41 | 0 | 0.3 | Cable | 0.0002 | 0.0035 | 3.2746 | 2779 | 2779 | 2779 | 2779 | B-2-1c
FRIN4B | FRIS4C | 0 | 0.1 | Cable | 0 | 0 | 0 | 2780 | 2780 | 2780 | 2780 | B-2-1c
FRIS4A | FRIS41 | 0 | 0.2 | Cable | 0.0001 | 0.0024 | 2.183 | 2779 | 2779 | 2779 | 2779 | B-2-1c
FRIS4B | FRIS41 | 0 | 0.15 | Cable | 0.0001 | 0.0018 | 1.6373 | 2779 | 2779 | 2779 | 2779 | B-2-1c
FRIS4D | FRIS41 | 0 | 0.2 | Cable | 0 | 0 | 0 | 2779 | 2779 | 2779 | 2779 | B-2-1c
GRST2A | WILT2A | 0 | 1 | Cable | 0 | 0.011 | 0 | 207 | 196 | 183 | 196 | B-2-1c
GRST2A | WILT2B | 0 | 1 | Cable | 0 | 0.011 | 0 | 207 | 198 | 185 | 198 | B-2-1c
GRST2B | WILT2C | 0 | 1 | Cable | 0 | 0.011 | 0 | 198 | 198 | 180 | 180 | B-2-1c
GRST2B | WILT2D | 0 | 1 | Cable | 0 | 0.011 | 0 | 206 | 204 | 190 | 204 | B-2-1c
HACK41 | HIBU41 | 0 | 6.858 | Cable | 0.0043 | 0.0827 | 72.4072 | 1770 | 1730 | 1600 | 1730 | B-2-1c
HACK41 | HIBU41 | 0 | 6.858 | Cable | 0.0043 | 0.0827 | 72.4072 | 1770 | 1730 | 1600 | 1730 | B-2-1c
HACK41 | WHAM41 | 0 | 6.148 | Cable | 0.0049 | 0.0904 | 101.6264 | 1857 | 1729 | 1587 | 1729 | B-2-1c
HACK41 | WHAM41 | 0 | 6.148 | Cable | 0.0049 | 0.0904 | 101.6264 | 1857 | 1729 | 1587 | 1729 | B-2-1c
HAMH1A | LEMR11 | 0 | 1 | Cable | 0.016 | 0.098 | 1.942 | 226 | 209 | 209 | 209 | B-2-1c
HAMH1B | LEMR11 | 0 | 1 | Cable | 0.027 | 0.129 | 0.424 | 211 | 170 | 170 | 170 | B-2-1c
HIBU41 | SJOW41 | 0 | 5.814 | Cable | 0.0037 | 0.0701 | 61.3846 | 1770 | 1730 | 1600 | 1730 | B-2-1c
HIBU41 | SJOW41 | 0 | 5.814 | Cable | 0.0037 | 0.0701 | 61.3846 | 1770 | 1730 | 1600 | 1730 | B-2-1c
IVER21 | NHYD2A | 0 | 13.63 | Cable | 0.06 | 0.3489 | 91.1847 | 419 | 419 | 381 | 381 | B-2-1c
IVER22 | NHYD2B | 0 | 13.63 | Cable | 0.06 | 0.3489 | 91.1847 | 419 | 419 | 381 | 381 | B-2-1c
JORD21 | NORL2B | 0 | 2.843 | Cable | 0.0109 | 0.0719 | 20.1177 | 419 | 419 | 381 | 381 | B-2-1c
KENG41 | SJOW41 | 0 | 4.756 | Cable | 0.0032 | 0.0562 | 51.9127 | 1770 | 1730 | 1600 | 1730 | B-2-1c
KENG41 | SJOW41 | 0 | 4.769 | Cable | 0.0032 | 0.0564 | 52.0546 | 1770 | 1730 | 1600 | 1730 | B-2-1c
KENG41 | WIMB41 | 0 | 12.329 | Cable | 0.0085 | 0.1557 | 134.5735 | 1770 | 1730 | 1600 | 1730 | B-2-1c
KENG41 | WIMB41 | 0 | 12.2 | Cable | 0.0084 | 0.1541 | 133.1654 | 1770 | 1730 | 1600 | 1730 | B-2-1c
KENG41 | WISD41 | 0 | 2.939 | Cable | 0.002 | 0.0347 | 32.0798 | 1770 | 1730 | 1600 | 1730 | B-2-1c
KENG41 | WISD42 | 0 | 2.989 | Cable | 0.002 | 0.0353 | 32.6255 | 1770 | 1730 | 1600 | 1730 | B-2-1c
KIBY21 | LISD21 | 0 | 10.239 | Cable | 0.0173 | 0.2966 | 60.8154 | 762 | 762 | 698 | 698 | B-2-1c
KIBY21 | LISD21 | 0 | 9.518 | Cable | 0.0228 | 0.2008 | 86.3283 | 762 | 762 | 619 | 619 | B-2-1c
KIRK2A | SKLG21 | 0 | 8.608 | Cable | 0.0146 | 0.2402 | 93.5689 | 762 | 762 | 619 | 619 | B-2-1c
LEIS11 | SIZE11 | 0 | 2.149 | Cable | 0.0196 | 0.2155 | 4.8028 | 301 | 301 | 243 | 243 | B-2-1c
LEIS11 | SIZE11 | 0 | 2.148 | Cable | 0.0195 | 0.2154 | 4.8006 | 301 | 301 | 243 | 243 | B-2-1c
LEIS11 | SIZE1A | 0 | 1.65 | Cable | 0.015 | 0.1655 | 3.6876 | 301 | 301 | 243 | 243 | B-2-1c
LEIS11 | SIZE1B | 0 | 1.65 | Cable | 0.015 | 0.1655 | 3.6876 | 301 | 301 | 243 | 243 | B-2-1c
NORL2A | SHEC21 | 0 | 4.372 | Cable | 0.0192 | 0.1119 | 29.2487 | 419 | 419 | 381 | 381 | B-2-1c
NORL2B | PITS21 | 0 | 10.751 | Cable | 0.0473 | 0.2752 | 71.9242 | 419 | 419 | 381 | 381 | B-2-1c
PITS21 | TEMP21 | 0 | 6.69 | Cable | 0.0294 | 0.1713 | 44.7561 | 419 | 419 | 381 | 381 | B-2-1c
PUDM41 | WHAM4A | 0 | 2.17 | Cable | 0.002 | 0.0178 | 39.06 | 1282 | 1136 | 984 | 1136 | B-2-1c
PYLE21 | PYLE21 | 0 | 0.25 | Cable | 0.0004 | 0.0063 | 1.69 | 1204 | 1115 | 1018 | 1115 | B-2-1c
SELL4A | SELL4C | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 2369 | 2369 | 1642 | 1642 | B-2-1c
SELL4A | SELL4D | 0 | 0.257 | Cable | 0.0001 | 0.0013 | 9.9716 | 2369 | 2369 | 1642 | 1642 | B-2-1c
SELL4A | SELL4E | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 2369 | 2369 | 1642 | 1642 | B-2-1c
SELL4A | SELL4F | 0 | 0.415 | Cable | 0.0002 | 0.0022 | 14.94 | 2369 | 2369 | 1642 | 1642 | B-2-1c
SPEN42 | SPEN42 | 0 | 0.131 | Cable | 0.0001 | 0.0015 | 1.4299 | 278 | 265 | 248 | 250 | B-2-1c
CLAY1Q | REDM1Q | 0 | 4.8 | Cable | 0.1402 | 0.4475 | 5.686 | 153 | 129 | 129 | 129 | B-2-2a | 2025 | Change
CLAY1R | REDM1R | 0 | 4.8 | Cable | 0.1402 | 0.4475 | 5.686 | 153 | 129 | 129 | 129 | B-2-2a | 2025 | Change
CONN1J | CONN1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2025 | Addition
CRSS1K | HICL1- | 0 | 0.4 | Cable | 0.0072 | 0.056 | 0.48 | 158 | 146 | 146 | 146 | B-2-2a | 2025 | Addition
DOUN1- | LIMK1A | 0 | 0.9 | Cable | 0.01 | 0.058 | 1.389 | 306 | 253 | 253 | 253 | B-2-2a | 2025 | Addition
GLAG1Q | GLAG1S | 0 | 2.25 | Cable | 0.0671 | 0.133 | 3.356 | 160 | 145 | 145 | 145 | B-2-2a | 2025 | Addition
GLAG1R | GLAG1T | 0 | 2.25 | Cable | 0.0671 | 0.133 | 3.356 | 160 | 145 | 145 | 145 | B-2-2a | 2025 | Addition
GREM1J | GREM1L | 0 | 3.83 | Cable | 0.02 | 0.305 | 6.898 | 272 | 272 | 250 | 272 | B-2-2a | 2025 | Addition
GREM1K | GREM1N | 0 | 1.72 | Cable | 0.0106 | 0.1372 | 3.098 | 272 | 272 | 272 | 272 | B-2-2a | 2025 | Addition
GREM1M | GREM1N | 0 | 2.3 | Cable | 0.0141 | 0.1834 | 4.143 | 272 | 272 | 272 | 272 | B-2-2a | 2025 | Addition
GREM1P | GREM1Q | 0 | 0.93 | Cable | 0.0057 | 0.0742 | 1.675 | 272 | 272 | 272 | 272 | B-2-2a | 2025 | Addition
KERG1J | KERG1L | 0 | 5.85 | Cable | 0.0359 | 0.4662 | 10.53 | 272 | 272 | 272 | 272 | B-2-2a | 2025 | Addition
KERG1K | KERG1M | 0 | 5.85 | Cable | 0.0359 | 0.4662 | 10.53 | 272 | 272 | 272 | 272 | B-2-2a | 2025 | Addition
AIGN1- | AIGN1A | 0 | 0.43 | Cable | 0.0121 | 0.0381 | 0.569 | 149 | 137 | 137 | 137 | B-2-2a | 2027 | Addition
ALYT4J | ALYT4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2027 | Addition
BLEX1- | BLEX1B | 0 | 3 | Cable | 0.0315 | 0.168 | 2.851 | 199 | 199 | 199 | 199 | B-2-2a | 2027 | Addition
BLEX1A | FAUG1J | 0 | 2.2 | Cable | 0.0231 | 0.1232 | 2.09 | 199 | 199 | 199 | 199 | B-2-2a | 2027 | Addition
CRSS1K | HICL1- | 0 | 0.4 | Cable | 0.0072 | 0.056 | 0.48 | 158 | 146 | 146 | 146 | B-2-2a | 2027 | Addition
CULL1A | CULL1Q | 0 | 0.43 | Cable | 0.0046 | 0.0274 | 0.664 | 149 | 137 | 137 | 137 | B-2-2a | 2027 | Addition
DEAW1- | DEAW1A | 0 | 3.8 | Cable | 0.1067 | 0.3362 | 5.031 | 149 | 137 | 137 | 137 | B-2-2a | 2027 | Addition
DELL1- | DELL1B | 0 | 7.4 | Cable | 0.1902 | 0.4122 | 5.212 | 127 | 127 | 127 | 127 | B-2-2a | 2027 | Addition
DELL1A | MELG1K | 0 | 0.7 | Cable | 0.018 | 0.039 | 0.493 | 127 | 127 | 127 | 127 | B-2-2a | 2027 | Addition
DOUN1- | OWFD1- | 0 | 1 | Cable | 0.0206 | 0.0849 | 1.349 | 190 | 147 | 147 | 147 | B-2-2a | 2027 | Addition
FETT4J | FETT4Q | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2027 | Addition
FETT4Q | KINT4J | 0 | 32.19 | Cable | 0.0644 | 0.6052 | 19.977 | 2000 | 1920 | 1790 | 1920 | B-2-2a | 2027 | Addition
FETT4R | KINT4K | 0 | 32.19 | Cable | 0.0644 | 0.6052 | 19.977 | 2000 | 1920 | 1790 | 1920 | B-2-2a | 2027 | Addition
FOYE2- | FOYE2J | 0 | 0.8 | Cable | 0.0053 | 0.0152 | 3.23 | 319 | 319 | 319 | 319 | B-2-2a | 2027 | Change
GILB1J | GILB1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2027 | Addition
GILB1J | GILB1L | 0 | 7.06 | Cable | 0.0419 | 0.5395 | 12.655 | 348 | 348 | 348 | 348 | B-2-2a | 2027 | Addition
GILB1J | MEYG1- | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2027 | Addition
GILB1K | GILB1M | 0 | 7.06 | Cable | 0.0419 | 0.5395 | 12.655 | 348 | 348 | 348 | 348 | B-2-2a | 2027 | Addition
GLAG1Q | STNG1D | 0 | 2.21 | Cable | 0.0663 | 0.1304 | 3.094 | 124 | 114 | 114 | 114 | B-2-2a | 2027 | Addition
GLAG1R | STNG1C | 0 | 2.21 | Cable | 0.0663 | 0.1304 | 3.094 | 124 | 114 | 114 | 114 | B-2-2a | 2027 | Addition
KINT4J | KINT4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2027 | Addition
KION1- | KION1A | 0 | 0.28 | Cable | 0.0079 | 0.0248 | 0.371 | 149 | 137 | 137 | 137 | B-2-2a | 2027 | Addition
MILC1R | STNG1B | 0 | 1.53 | Cable | 0.0813 | 0.1409 | 1.691 | 131 | 113 | 113 | 113 | B-2-2a | 2027 | Addition
MILC1V | STNG1A | 0 | 1.53 | Cable | 0.0813 | 0.1409 | 1.691 | 131 | 113 | 113 | 113 | B-2-2a | 2027 | Addition
STNG1A | STNG1E | 0 | 0.63 | Cable | 0.0189 | 0.0372 | 0.882 | 160 | 145 | 145 | 145 | B-2-2a | 2027 | Addition
STNG1B | STNG1E | 0 | 0.63 | Cable | 0.0189 | 0.0372 | 0.882 | 160 | 145 | 145 | 145 | B-2-2a | 2027 | Addition
STNG1C | STNG1E | 0 | 0.81 | Cable | 0.0243 | 0.0478 | 1.134 | 160 | 145 | 145 | 145 | B-2-2a | 2027 | Addition
STNG1D | STNG1E | 0 | 0.81 | Cable | 0.0243 | 0.0478 | 1.134 | 160 | 145 | 145 | 145 | B-2-2a | 2027 | Addition
STRW1A | STWO1- | 0 | 5 | Cable | 0.455 | 1.08 | 0.27 | 126 | 119 | 108 | 119 | B-2-2a | 2027 | Addition
STSO1A | STSO1B | 0 | 0.27 | Cable | 0.0056 | 0.0226 | 0.37 | 200 | 178 | 178 | 178 | B-2-2a | 2027 | Addition
THUS1J | THUS1L | 0 | 3.03 | Cable | 0.018 | 0.2316 | 5.431 | 348 | 348 | 348 | 348 | B-2-2a | 2027 | Addition
THUS1K | THUS1M | 0 | 3.03 | Cable | 0.018 | 0.2316 | 5.431 | 348 | 348 | 348 | 348 | B-2-2a | 2027 | Addition
WIOW1- | WIOW1Q | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2027 | Addition
WIOW1- | WIOW1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2027 | Addition
ALYT4J | ASBS4B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
ANSN2- | ERED2- | 0 | 0.6 | Cable | 0.0016 | 0.011 | 3.435 | 580 | 546 | 546 | 546 | B-2-2a | 2029 | Addition
BANN4J | BANN4K | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
BANN4J | OWPL4- | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
BEWF1- | SYEL1- | 0 | 1.5 | Cable | 0.0315 | 0.1265 | 2.054 | 206 | 206 | 206 | 206 | B-2-2a | 2029 | Addition
BLGH1- | CRDH1J | 0 | 10 | Cable | 0.91 | 2.16 | 0.54 | 126 | 119 | 108 | 119 | B-2-2a | 2029 | Addition
BLHI2A | BLHI2J | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
BLHI2B | BLHI2K | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
BREC1Q | FASQ1- | 0 | 4 | Cable | 0.065 | 0.334 | 6.245 | 176 | 176 | 176 | 176 | B-2-2a | 2029 | Addition
BROA1- | BROA1J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
BROA1- | BROA1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
BROA1A | BROA1J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
BROA1B | BROA1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
BROA1C | EDIN1C | 0 | 15 | Cable | 0.1481 | 1.2148 | 27.585 | 207 | 207 | 207 | 207 | B-2-2a | 2029 | Addition
BROA1C | EDIN1C | 0 | 15 | Cable | 0.1481 | 1.2148 | 27.585 | 207 | 207 | 207 | 207 | B-2-2a | 2029 | Addition
BROA1D | EDIN1D | 0 | 15 | Cable | 0.1481 | 1.2148 | 27.585 | 207 | 207 | 207 | 207 | B-2-2a | 2029 | Addition
BROA1D | EDIN1D | 0 | 15 | Cable | 0.1481 | 1.2148 | 27.585 | 207 | 207 | 207 | 207 | B-2-2a | 2029 | Addition
BROA1J | BROA1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
CLOI1A | MELG1K | 0 | 0.7 | Cable | 0.0093 | 0.0536 | 0.95 | 220 | 211 | 211 | 211 | B-2-2a | 2029 | Addition
CMBS4A | CMBS4B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
COST1- | COST1A | 0 | 2.6 | Cable | 0.0346 | 0.1992 | 4.3 | 292 | 292 | 292 | 292 | B-2-2a | 2029 | Addition
COST1A | ELIB1- | 0 | 11.5 | Cable | 0.575 | 2.3805 | 0.644 | 292 | 292 | 292 | 292 | B-2-2a | 2029 | Addition
CRDH1J | CRDH1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
CRDH2J | CRDH2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
CRMU2J | CRMU2K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
CRSN1Q | CRSN1R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
CRSN1Q | CRSS1J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
CRSN1R | CRSS1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
CRSN2Q | CRSN2R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
DOUN2A | DOUN2B | 0 | 0.79 | Cable | 0.0048 | 0.0255 | 2.87 | 292 | 292 | 292 | 292 | B-2-2a | 2029 | Addition
DOUN2B | DOUN2C | 0 | 1.85 | Cable | 0.0141 | 0.0459 | 5.201 | 294 | 294 | 294 | 294 | B-2-2a | 2029 | Addition
DOUN2C | FINS2C | 0 | 48.3 | Cable | 0.5558 | 1.3971 | 104.968 | 231 | 231 | 231 | 231 | B-2-2a | 2029 | Addition
EDIN1A | EDIN1J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
EDIN1B | EDIN1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
EDIN1J | EDIN1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
EDIN1J | GLUE1- | 0 | 2.8 | Cable | 0.0166 | 0.214 | 5.019 | 348 | 348 | 348 | 348 | B-2-2a | 2029 | Addition
EDIN1K | EDIN1J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
ELIB1A | FINS1- | 0 | 3.1 | Cable | 0.0502 | 0.318 | 4.584 | 208 | 187 | 187 | 187 | B-2-2a | 2029 | Addition
ENEI1- | ENEI1N | 0 | 1 | Cable | 0.0133 | 0.0766 | 1.654 | 250 | 250 | 250 | 250 | B-2-2a | 2029 | Addition
FASN1A | FASN1B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
FAUG1- | FAUG1R | 0 | 9 | Cable | 0.0889 | 0.7289 | 16.551 | 207 | 207 | 207 | 207 | B-2-2a | 2029 | Addition
FAUG1- | FAUG1R | 0 | 9 | Cable | 0.0889 | 0.7289 | 16.551 | 207 | 207 | 207 | 207 | B-2-2a | 2029 | Addition
FAUG1- | FAUG1S | 0 | 9 | Cable | 0.0889 | 0.7289 | 16.551 | 207 | 207 | 207 | 207 | B-2-2a | 2029 | Addition
FAUG1- | FAUG1S | 0 | 9 | Cable | 0.0889 | 0.7289 | 16.551 | 207 | 207 | 207 | 207 | B-2-2a | 2029 | Addition
FETT4J | FETT4K | 0 | 1 | Cable | 0 | 0.01 | 0 | 100 | 100 | 100 | 100 | B-2-2a | 2029 | Addition
FETT4K | FETT4R | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
FINS2A | FINS2B | 0 | 13.61 | Cable | 0.0827 | 0.4387 | 49.435 | 292 | 292 | 292 | 292 | B-2-2a | 2029 | Addition
FINS2B | FINS2C | 0 | 2.2 | Cable | 0.0167 | 0.0545 | 6.185 | 294 | 294 | 294 | 294 | B-2-2a | 2029 | Addition
GRNV4- | NEDE4J | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
KERG1A | KERG1W | 0 | 4 | Cable | 0.0246 | 0.319 | 7.205 | 272 | 272 | 272 | 272 | B-2-2a | 2029 | Addition
KERG1A | SYEL1A | 0 | 12 | Cable | 0.4007 | 0.7573 | 16.422 | 189 | 189 | 189 | 189 | B-2-2a | 2029 | Addition
KERG1B | KERG1W | 0 | 4 | Cable | 0.0246 | 0.319 | 7.205 | 272 | 272 | 272 | 272 | B-2-2a | 2029 | Addition
KERG1B | SYEL1B | 0 | 12 | Cable | 0.4007 | 0.7573 | 16.422 | 189 | 189 | 189 | 189 | B-2-2a | 2029 | Addition
KERG1K | KERG1N | 0 | 0.35 | Cable | 0.0021 | 0.0279 | 0.63 | 272 | 272 | 272 | 272 | B-2-2a | 2029 | Addition
KERG1N | KERG1U | 0 | 3 | Cable | 0.1551 | 0.651 | 0.158 | 295 | 295 | 295 | 295 | B-2-2a | 2029 | Addition
KERG1U | KERG1V | 0 | 2 | Cable | 0.0123 | 0.1595 | 3.602 | 272 | 272 | 272 | 272 | B-2-2a | 2029 | Addition
KERG1V | KERG1W | 0 | 12.5 | Cable | 0.6463 | 2.7125 | 0.659 | 295 | 295 | 295 | 295 | B-2-2a | 2029 | Addition
KINA4A | KINA4B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
KINM2A | KINM2C | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
KINM2B | KINM2C | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
LOCL1J | LOCL1K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
LOCL4J | LOCL4K | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
PEHE4J | PEHE4L | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
SALM1A | SALM1C | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
SALM1B | SALM1C | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
STCS1A | STCS1B | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
STCS1A | STRW1A | 0 | 1 | Cable | 0.01 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
STCS1B | STSO1A | 0 | 6 | Cable | 0.1181 | 0.1733 | 4.7 | 251 | 252 | 252 | 252 | B-2-2a | 2029 | Addition
SYEL1- | SYEL1M | 0 | 1 | Cable | 0 | 0.01 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2a | 2029 | Addition
SYEL1- | SYEL1N | 0 | 2.5 | Cable | 0.0333 | 0.1915 | 4.135 | 250 | 250 | 250 | 250 | B-2-2a | 2029 | Addition
SYEL1A | SYEL1M | 0 | 2 | Cable | 0.0123 | 0.1595 | 3.602 | 272 | 272 | 272 | 272 | B-2-2a | 2029 | Addition
SYEL1B | SYEL1M | 0 | 2 | Cable | 0.0123 | 0.1595 | 3.602 | 272 | 272 | 272 | 272 | B-2-2a | 2029 | Addition
AYRS4- | HBES4- | 0 | 0.1 | Cable | 0.0001 | 0.0013 | 1.1119 | 2770 | 2770 | 2770 | 2770 | B-2-2b | 2025 | Addition
AYRS4- | HESF4- | 0 | 0.1 | Cable | 0.0001 | 0.0013 | 1.1119 | 2770 | 2770 | 2770 | 2770 | B-2-2b | 2025 | Addition
AYRS4- | HUNE4- | 0 | 0.9 | Cable | 0.0005 | 0.012 | 10.0073 | 1247 | 1247 | 1247 | 1247 | B-2-2b | 2025 | Addition
BLAH3B | PLOE3- | 0 | 1.01 | Cable | 0.2795 | 0.8831 | 0.1185 | 40 | 38 | 38 | 38 | B-2-2b | 2025 | Addition
BLAH3B | PLOE3- | 0 | 1.01 | Cable | 0.2795 | 0.8831 | 0.1185 | 40 | 38 | 38 | 38 | B-2-2b | 2025 | Addition
COAB4- | COAL4- | 0 | 2.5 | Cable | 0.0017 | 0.032 | 27.7981 | 1247 | 1247 | 1247 | 1247 | B-2-2b | 2025 | Addition
DONO3A | DWEX3- | 0 | 4 | Cable | 0.5534 | 1.7488 | 0.9388 | 40 | 38 | 38 | 38 | B-2-2b | 2025 | Addition
FIGS2- | KINC2- | 0 | 0.7 | Cable | 0.0018 | 0.0075 | 5.395 | 352 | 352 | 352 | 352 | B-2-2b | 2025 | Addition
GLGL1- | SANQ1- | 0 | 4 | Cable | 0.0629 | 0.3444 | 6.5906 | 283 | 277 | 269 | 277 | B-2-2b | 2025 | Addition
HOLM1- | HOLM1T | 0 | 0.28 | Cable | 0.0025 | 0.0233 | 0.5242 | 293 | 293 | 293 | 293 | B-2-2b | 2025 | Addition
HUCR4- | HUNE4- | 0 | 0.4 | Cable | 0.0002 | 0.0053 | 4.4477 | 1247 | 1247 | 1247 | 1247 | B-2-2b | 2025 | Addition
HUNE1- | HUNF1Q | 0 | 0.18 | Cable | 0.003 | 0.016 | 0.396 | 146 | 146 | 146 | 146 | B-2-2b | 2025 | Addition
HUNE1- | HUNF1R | 0 | 0.1 | Cable | 0.003 | 0.016 | 0.264 | 146 | 146 | 146 | 146 | B-2-2b | 2025 | Addition
HUNE1- | JUNA1T | 0 | 3.62 | Cable | 0.052 | 0.365 | 12.94 | 175 | 175 | 175 | 175 | B-2-2b | 2025 | Addition
NECU1B | OHLL1- | 0 | 3 | Cable | 0.0534 | 0.2861 | 3.5006 | 180 | 180 | 180 | 180 | B-2-2b | 2025 | Addition
NECU1C | SOKY1- | 0 | 4.5 | Cable | 0.0458 | 0.2435 | 7.265 | 242 | 223 | 192 | 223 | B-2-2b | 2025 | Change
ARCR2- | MAHI2- | 0 | 9.5 | Cable | 0.0488 | 0.2034 | 36.6087 | 352 | 352 | 352 | 352 | B-2-2b | 2027 | Addition
COAN4- | COBA4- | 0 | 2.5 | Cable | 0.0017 | 0.032 | 27.7981 | 1247 | 1247 | 1247 | 1247 | B-2-2b | 2027 | Addition
HARE1- | MOFF1- | 0 | 15.33 | Cable | 0.3071 | 0.8622 | 21.8179 | 184 | 184 | 184 | 184 | B-2-2b | 2027 | Change
AREX1- | AREX1A | 0 | 1.7 | Cable | 0.048 | 0.1103 | 2.0938 | 181 | 164 | 164 | 164 | B-2-2b | 2029 | Change
BLCW3- | BLKS3- | 0 | 2.801 | Cable | 0.3875 | 1.2246 | 0.6574 | 35 | 35 | 35 | 35 | B-2-2b | 2029 | Change
BRNX4- | BRNX4A | 0 | 0.25 | Cable | 0 | 0 | 0 | 2770 | 2770 | 2770 | 2770 | B-2-2b | 2029 | Addition
BRNX4- | TORN4- | 0 | 1.94 | Cable | 0.0005 | 0.013 | 43.1426 | 945 | 800 | 800 | 800 | B-2-2b | 2029 | Addition
BRNX4- | TORN4- | 0 | 2.1 | Cable | 0.0005 | 0.014 | 46.7008 | 1040 | 900 | 900 | 900 | B-2-2b | 2029 | Addition
BRNX4Q | TORN4- | 0 | 1.97 | Cable | 0.002 | 0.0326 | 38.612 | 935 | 785 | 785 | 785 | B-2-2b | 2029 | Addition
BRNX4R | TORN4- | 0 | 1.94 | Cable | 0.0019 | 0.0321 | 38.024 | 900 | 760 | 760 | 760 | B-2-2b | 2029 | Addition
BROC1- | BROT1- | 0 | 0.22 | Cable | 0.0044 | 0.0183 | 0.3167 | 234 | 234 | 234 | 234 | B-2-2b | 2029 | Change
BUSB2- | WLER2- | 0 | 12 | Cable | 0.0372 | 0.2829 | 51.3179 | 450 | 450 | 450 | 450 | B-2-2b | 2029 | Addition
CCSS1- | COAL1B | 0 | 6.97 | Cable | 0.1096 | 0.6 | 11.4841 | 241 | 241 | 241 | 241 | B-2-2b | 2029 | Change
CCSS1- | GAWH1Q | 0 | 2.6 | Cable | 0.0409 | 0.2238 | 4.2839 | 241 | 241 | 241 | 241 | B-2-2b | 2029 | Change
CCSS3- | CUMH3- | 0 | 2.3 | Cable | 0.3182 | 1.0055 | 0.5398 | 38 | 38 | 38 | 38 | B-2-2b | 2029 | Change
CLAU1- | MAHI1C | 0 | 4 | Cable | 0.0583 | 0.3646 | 5.0764 | 161 | 161 | 161 | 161 | B-2-2b | 2029 | Change
CLAW1- | NECU1- | 0 | 2.21 | Cable | 0.0438 | 0.2004 | 3.0848 | 133 | 133 | 133 | 133 | B-2-2b | 2029 | Change
COAL1A | LEGO1Q | 0 | 4 | Cable | 0.1129 | 0.2596 | 4.9265 | 134 | 123 | 123 | 123 | B-2-2b | 2029 | Addition
COAL1A | LEGO1R | 0 | 4 | Cable | 0.1129 | 0.2596 | 4.9265 | 134 | 123 | 123 | 123 | B-2-2b | 2029 | Addition
COAL1B | CUMW1- | 0 | 11.1 | Cable | 0.3134 | 0.7205 | 14.5825 | 122 | 107 | 107 | 107 | B-2-2b | 2029 | Change
COAL1B | DONO1- | 0 | 4.806 | Cable | 0.0662 | 0.3007 | 6.9978 | 165 | 165 | 165 | 165 | B-2-2b | 2029 | Change
DEBS2- | LOAN2- | 0 | 5 | Cable | 0.0102 | 0.1381 | 30.4106 | 820 | 736 | 674 | 736 | B-2-2b | 2029 | Addition
DONO1- | MIDM1- | 0 | 1.065 | Cable | 0.0208 | 0.0978 | 1.4807 | 211 | 211 | 211 | 211 | B-2-2b | 2029 | Addition
DUNB1Q | DUNB1S | 0 | 0.15 | Cable | 0.003 | 0.0136 | 0.2094 | 133 | 133 | 133 | 133 | B-2-2b | 2029 | Change
DUNB1R | DUNB1T | 0 | 0.15 | Cable | 0.003 | 0.0136 | 0.2094 | 133 | 133 | 133 | 133 | B-2-2b | 2029 | Change
DUNE3- | KEIH3- | 0 | 4.746 | Cable | 5.1628 | 4.7962 | 0.3798 | 23 | 23 | 23 | 23 | B-2-2b | 2029 | Change
DUNE3- | POGB3- | 0 | 3.809 | Cable | 4.4533 | 3.8497 | 0.3048 | 57 | 57 | 57 | 57 | B-2-2b | 2029 | Change
ELDE1Q | JOHN1Q | 0 | 4.37 | Cable | 0.1229 | 0.4314 | 4.832 | 1 | 1 | 1 | 1 | B-2-2b | 2029 | Change
ELDE1R | JOHN1R | 0 | 4.37 | Cable | 0.1229 | 0.4314 | 4.832 | 1 | 1 | 1 | 1 | B-2-2b | 2029 | Change
GHPS1- | LETH1- | 0 | 3 | Cable | 0.0404 | 0.2597 | 9.3604 | 229 | 229 | 229 | 229 | B-2-2b | 2029 | Change
GLGL1B | SAKN1- | 0 | 9 | Cable | 0.2541 | 0.5842 | 11.0847 | 181 | 164 | 164 | 164 | B-2-2b | 2029 | Change
GLGL1B | SANQ1- | 0 | 4 | Cable | 0.0629 | 0.3444 | 6.5906 | 241 | 241 | 241 | 241 | B-2-2b | 2029 | Change
GLGL3- | GLMU3- | 0 | 10 | Cable | 2.7669 | 8.7439 | 1.1735 | 40 | 38 | 38 | 38 | B-2-2b | 2029 | Addition
GORG1Q | TELR1Q | 0 | 4.6 | Cable | 0.0433 | 0.0995 | 18.1296 | 72 | 72 | 72 | 72 | B-2-2b | 2029 | Change
GORG1R | TELR1R | 0 | 4.6 | Cable | 0.0433 | 0.0995 | 18.1296 | 72 | 72 | 72 | 72 | B-2-2b | 2029 | Change
HUCS4- | HUNE4- | 0 | 0.665 | Cable | 0.0003 | 0.0089 | 7.3943 | 1448 | 1448 | 1448 | 1448 | B-2-2b | 2029 | Change
HUCS4- | HUNE4- | 0 | 0.675 | Cable | 0.0003 | 0.009 | 7.5055 | 1448 | 1448 | 1448 | 1448 | B-2-2b | 2029 | Change
INWI1Q | TORN1- | 0 | 1.15 | Cable | 0.038 | 0.061 | 2.365 | 110 | 110 | 110 | 110 | B-2-2b | 2029 | Change
INWI1R | TORN1- | 0 | 1.12 | Cable | 0.038 | 0.061 | 2.365 | 110 | 110 | 110 | 110 | B-2-2b | 2029 | Change
KINC2- | KINN2B | 0 | 1.9 | Cable | 0.0023 | 0.0168 | 17.1535 | 403 | 403 | 403 | 403 | B-2-2b | 2029 | Change
NECU1C | NOKY1- | 0 | 1.3 | Cable | 0.0084 | 0.0773 | 2.2771 | 242 | 242 | 242 | 242 | B-2-2b | 2029 | Change
NEIL2- | NEIL2D | 0 | 0.2 | Cable | 0.0002 | 0.0028 | 2.4328 | 820 | 736 | 674 | 736 | B-2-2b | 2029 | Change
NETH3- | WISH3T | 0 | 0.98 | Cable | 0.1354 | 0.45 | 0.2253 | 29 | 29 | 29 | 29 | B-2-2b | 2029 | Change
BENR41 | NEWX41 | 0 | 4.272 | Cable | 0.0029 | 0.0571 | 34.5413 | 1100 | 1100 | 1100 | 1100 | B-2-2c | 2025 | Addition
BENR41 | WIMB41 | 0 | 8.429 | Cable | 0.0058 | 0.1128 | 68.1528 | 1250 | 1250 | 1250 | 1250 | B-2-2c | 2025 | Addition
NEWX41 | WIMB41 | 0 | 12.688 | Cable | 0.0087 | 0.1697 | 102.5891 | 1100 | 1100 | 1100 | 1100 | B-2-2c | 2025 | Addition
CREB41 | CREB41 | 0 | 0.1 | Cable | 0.0001 | 0.0012 | 1.0915 | 1386 | 1386 | 1386 | 1386 | B-2-2c | 2027 | Addition
CREB41 | CREB41 | 0 | 0.1 | Cable | 0.0001 | 0.0012 | 1.0915 | 1386 | 1386 | 1386 | 1386 | B-2-2c | 2027 | Addition
HURS21 | NEWX21 | 0 | 18.504 | Cable | 0.027 | 0.5237 | 70.7162 | 1200 | 1200 | 1200 | 1200 | B-2-2c | 2027 | Change
HURS21 | NEWX21 | 0 | 18.442 | Cable | 0.0269 | 0.5219 | 70.4793 | 1200 | 1200 | 1200 | 1200 | B-2-2c | 2027 | Change
PITS21 | WIBA21 | 0 | 2.324 | Cable | 0.0036 | 0.0621 | 13.8036 | 530 | 530 | 445 | 530 | B-2-2c | 2027 | Change
TEMP22 | WIBA21 | 0 | 3.607 | Cable | 0.0055 | 0.0964 | 21.424 | 530 | 530 | 530 | 530 | B-2-2c | 2027 | Change
DINO41 | PENI4A | 0 | 7.31 | Cable | 0.0051 | 0.0804 | 146.1 | 1623 | 1623 | 1571 | 1571 | B-2-2c | 2029 | Addition
ELST41 | SJOW41 | 0 | 20 | Cable | 0.014 | 0.176 | 244.29 | 1767 | 2640 | 2640 | 2640 | B-2-2c | 2029 | Addition
ELST4A | ELST41 | 0 | 0.1 | Cable | 0 | 0 | 0 | 1590 | 1500 | 1346 | 1500 | B-2-2c | 2029 | Addition

## OHL
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Sheet_Name | Year | Status
ABNE1Q | CHAR1- | 24.5 | 0 | OHL | 2.49 | 5.66 | 1.22 | 132 | 123 | 106 | 123 | B-2-1a
ALYT2A | TEAL2J | 16.2 | 0 | OHL | 0.0733 | 0.6724 | 4.406 | 1090 | 1030 | 925 | 1030 | B-2-1a
ALYT2B | TEAL2K | 16.2 | 0 | OHL | 0.0733 | 0.6724 | 4.406 | 1090 | 1030 | 925 | 1030 | B-2-1a
AMUL1E | BUMU1R | 17.8 | 0 | OHL | 1.8184 | 4.1692 | 0.885 | 132 | 123 | 106 | 123 | B-2-1a
AMUL1F | GRIF1S | 6.85 | 0 | OHL | 0.7002 | 1.6054 | 0.341 | 132 | 123 | 106 | 123 | B-2-1a
AMUL1H | GRIF1T | 6.85 | 0 | OHL | 0.7002 | 1.6054 | 0.341 | 132 | 123 | 106 | 123 | B-2-1a
ARBR1Q | DENS1Q | 14.5 | 0 | OHL | 1.3195 | 3.364 | 0.725 | 132 | 123 | 106 | 123 | B-2-1a
ARBR1R | DENS1R | 14.5 | 0 | OHL | 1.3195 | 3.364 | 0.725 | 132 | 123 | 106 | 123 | B-2-1a
ARDK1- | SLOY1T | 0 | 10 | OHL | 1.02 | 2.33 | 0.49 | 132 | 123 | 106 | 123 | B-2-1a
BEAU1J | CULL1Q | 14 | 0 | OHL | 1.43 | 3.28 | 0.69 | 126 | 117 | 101 | 117 | B-2-1a
BEAU1L | MOTA1R | 29.67 | 0 | OHL | 3.0145 | 6.9027 | 1.469 | 126 | 117 | 101 | 117 | B-2-1a
BEAU1M | MOTA1Q | 29.67 | 0 | OHL | 3.0145 | 6.9027 | 1.469 | 132 | 123 | 106 | 123 | B-2-1a
BEAU1N | KNOC1J | 17.1 | 0 | OHL | 1.5561 | 3.9843 | 0.855 | 132 | 123 | 106 | 123 | B-2-1a
BEAU1R | INNE1Q | 13.4 | 0 | OHL | 0.6834 | 3.0016 | 0.697 | 241 | 230 | 210 | 230 | B-2-1a
BEAU1S | INNE1R | 13.4 | 0 | OHL | 0.6834 | 3.0016 | 0.697 | 241 | 230 | 210 | 230 | B-2-1a
BEAU1T | KNOC1J | 17.1 | 0 | OHL | 1.5561 | 3.9843 | 0.855 | 132 | 123 | 106 | 123 | B-2-1a
BEAU2J | KNOC2L | 16.8 | 0 | OHL | 0.099 | 0.687 | 4.672 | 935 | 880 | 790 | 880 | B-2-1a
BEAU2K | KNOC2M | 16.8 | 0 | OHL | 0.099 | 0.687 | 4.672 | 935 | 880 | 790 | 880 | B-2-1a
BEAU4- | FAUG4J | 48.6 | 0 | OHL | 0.063 | 0.931 | 29.386 | 2780 | 2670 | 2480 | 2670 | B-2-1a
BEIN11 | CEAN1Q | 0.87 | 0 | OHL | 0.099 | 0.205 | 0.042 | 263 | 257 | 248 | 257 | B-2-1a
BEIN11 | MILW1S | 2.8 | 0 | OHL | 0.319 | 0.66 | 0.135 | 263 | 257 | 248 | 257 | B-2-1a
BERB2Q | BLHI2J | 46.26 | 0 | OHL | 0.2619 | 1.9044 | 12.613 | 935 | 880 | 790 | 880 | B-2-1a
BIHI1Q | CHAR1R | 3.9 | 0 | OHL | 0.17 | 0.851 | 0.206 | 229 | 211 | 183 | 211 | B-2-1a
BIHI1Q | COUA1Q | 14.6 | 0 | OHL | 0.7446 | 3.2704 | 0.753 | 241 | 230 | 210 | 230 | B-2-1a
BIHI1Q | TEAL1- | 5.6 | 0 | OHL | 0.239 | 1.199 | 0.29 | 229 | 211 | 183 | 211 | B-2-1a
BIHI1R | CHAR1- | 3.9 | 0 | OHL | 0.17 | 0.851 | 0.206 | 229 | 211 | 183 | 211 | B-2-1a
BIHI1R | COUA1R | 14.6 | 0 | OHL | 0.7446 | 3.2704 | 0.753 | 241 | 230 | 210 | 230 | B-2-1a
BIHI1R | TEAL1- | 5.6 | 0 | OHL | 0.239 | 1.199 | 0.29 | 229 | 211 | 183 | 211 | B-2-1a
BLHI1J | DORE11 | 23.45 | 0 | OHL | 1.171 | 5.295 | 1.286 | 241 | 230 | 210 | 230 | B-2-1a
BLHI1K | DORE12 | 23.45 | 0 | OHL | 1.171 | 5.297 | 1.318 | 241 | 230 | 210 | 230 | B-2-1a
BLHI2J | KINT2K | 50.85 | 0 | OHL | 0.298 | 2.08 | 14.14 | 935 | 880 | 790 | 880 | B-2-1a
BLHI2K | CAIN2- | 9.77 | 0 | OHL | 0.0573 | 0.3997 | 2.717 | 935 | 880 | 790 | 880 | B-2-1a
BLHI4- | ROTI4J | 35.4 | 0 | OHL | 0.0708 | 0.6832 | 20.826 | 2000 | 1920 | 1790 | 1920 | B-2-1a
BLHI4- | ROTI4K | 35.4 | 0 | OHL | 0.0708 | 0.6832 | 20.826 | 2000 | 1920 | 1790 | 1920 | B-2-1a
BOAG1L | TOMT1L | 19.19 | 0 | OHL | 2.1877 | 4.3562 | 0.96 | 215 | 211 | 203 | 211 | B-2-1a
BOAG1M | TOMT1M | 19.19 | 0 | OHL | 2.1877 | 4.3562 | 0.96 | 215 | 211 | 203 | 211 | B-2-1a
BONB4- | TUMM4- | 72.9 | 0 | OHL | 0.094 | 1.396 | 44.078 | 2780 | 2670 | 2480 | 2670 | B-2-1a
BREC1Q | BRID1Q | 5.1 | 0 | OHL | 0.61 | 1.21 | 0.25 | 112 | 104 | 90 | 104 | B-2-1a
BREC1Q | FIDD1B | 30.4 | 0 | OHL | 3.13 | 6.52 | 2.66 | 112 | 104 | 90 | 104 | B-2-1a
BREC1R | BRID1R | 5.1 | 0 | OHL | 0.61 | 1.21 | 0.25 | 112 | 104 | 90 | 104 | B-2-1a
BREC1R | DENS1Q | 26.1 | 0 | OHL | 3.08 | 6.33 | 1.29 | 112 | 104 | 90 | 104 | B-2-1a
BROR1- | BROR1Q | 1.1 | 0 | OHL | 0.1004 | 0.2561 | 0.0546 | 126 | 117 | 101 | 117 | B-2-1a
BROR1Q | DUBE1Q | 38.58 | 0 | OHL | 3.522 | 8.9813 | 1.914 | 126 | 117 | 101 | 117 | B-2-1a
BROR1Q | LOCB1T | 25.88 | 0 | OHL | 2.3626 | 6.0248 | 1.2842 | 126 | 117 | 101 | 117 | B-2-1a
CAAD1R | CRSS1K | 13.08 | 0 | OHL | 0.3091 | 2.7749 | 0.721 | 448 | 430 | 398 | 430 | B-2-1a
CAIN2- | KINT2J | 41.08 | 0 | OHL | 0.2407 | 1.6803 | 11.423 | 935 | 880 | 790 | 880 | B-2-1a
CASS1Q | DLCH1A | 28 | 0 | OHL | 2.562 | 6.09 | 1.2 | 111 | 103 | 89 | 103 | B-2-1a
CHAR1S | LYND1Q | 1.9 | 0 | OHL | 0.2 | 0.45 | 0.1 | 126 | 117 | 101 | 117 | B-2-1a
CHAR1T | LYND1R | 1.9 | 0 | OHL | 0.2 | 0.45 | 0.1 | 126 | 117 | 101 | 117 | B-2-1a
CLAC1Q | INVE1J | 8.4 | 0 | OHL | 0.85 | 1.95 | 0.41 | 126 | 117 | 101 | 117 | B-2-1a
CLAC1Q | SLOY1F | 13.05 | 0 | OHL | 1.1875 | 3.0406 | 0.653 | 132 | 123 | 106 | 123 | B-2-1a
CLUN1S | COUA1Q | 38.1 | 0 | OHL | 1.9301 | 8.5468 | 1.966 | 241 | 230 | 210 | 230 | B-2-1a
CLUN1T | COUA1R | 38.1 | 0 | OHL | 1.9301 | 8.5468 | 1.966 | 241 | 230 | 210 | 230 | B-2-1a
COGA1- | COGA1C | 13.9 | 0 | OHL | 0.7002 | 2.8782 | 0.778 | 241 | 230 | 210 | 230 | B-2-1a
CORI1J | LUIC1Q | 10.43 | 0 | OHL | 0.2443 | 2.2748 | 0.551 | 464 | 446 | 414 | 446 | B-2-1a
CORI1K | LUIC1R | 10.35 | 0 | OHL | 0.2425 | 2.2577 | 0.547 | 464 | 446 | 414 | 446 | B-2-1a
CORI1P | MOSS1S | 1.45 | 0 | OHL | 0.074 | 0.3248 | 0.075 | 224 | 211 | 189 | 211 | B-2-1a
CORI1Q | MOSS1T | 1.45 | 0 | OHL | 0.074 | 0.3248 | 0.075 | 224 | 211 | 189 | 211 | B-2-1a
CRAI1- | FOGG1Q | 4.7 | 0 | OHL | 0.485 | 1.057 | 0.221 | 132 | 123 | 106 | 123 | B-2-1a
CRAI1- | FOGG1R | 4.7 | 0 | OHL | 0.485 | 1.057 | 0.221 | 132 | 123 | 106 | 123 | B-2-1a
CRAI1- | REDM1R | 6.8 | 0 | OHL | 0.48 | 1.53 | 0.34 | 157 | 146 | 126 | 146 | B-2-1a
CRAI1P | KINT1P | 17.5 | 0 | OHL | 0.8925 | 3.92 | 0.903 | 241 | 230 | 210 | 230 | B-2-1a
CRAI1Q | REDM1Q | 6.8 | 0 | OHL | 0.48 | 1.53 | 0.34 | 157 | 146 | 126 | 146 | B-2-1a
CRAI1R | KINT1R | 17.5 | 0 | OHL | 0.8925 | 3.92 | 0.903 | 241 | 230 | 210 | 230 | B-2-1a
CREA1- | CREA1B | 4 | 0 | OHL | 0.2 | 0.828 | 0.224 | 203 | 193 | 176 | 193 | B-2-1a
CREA1A | DLCH1B | 16.6 | 0 | OHL | 0.83 | 3.4362 | 0.93 | 203 | 193 | 176 | 193 | B-2-1a
DENS1Q | TEAL1- | 8.7 | 0 | OHL | 0.3393 | 1.9053 | 0.461 | 183 | 160 | 149 | 160 | B-2-1a
DENS1R | TEAL1- | 8.7 | 0 | OHL | 0.3393 | 1.9053 | 0.461 | 183 | 160 | 149 | 160 | B-2-1a
DLCH1A | LOCB1L | 17 | 0 | OHL | 0.3992 | 3.7085 | 0.898 | 464 | 446 | 414 | 446 | B-2-1a
DOUN2- | THUS2K | 15.4 | 0 | OHL | 0.077 | 0.847 | 3.28 | 965 | 925 | 865 | 925 | B-2-1a
DUBE1Q | MYBS1R | 20.84 | 0 | OHL | 1.9025 | 4.8515 | 1.034 | 126 | 117 | 101 | 117 | B-2-1a
DUCC1J | ORRI1S | 10.76 | 0 | OHL | 0.2526 | 2.3466 | 0.568 | 464 | 446 | 414 | 446 | B-2-1a
DUCC1K | ORRI1T | 10.76 | 0 | OHL | 0.2526 | 2.3466 | 0.568 | 464 | 446 | 414 | 446 | B-2-1a
DUNM1- | DUNM1T | 2.76 | 0 | OHL | 0.1391 | 0.5715 | 0.155 | 203 | 193 | 176 | 193 | B-2-1a
DUNM1- | DUNM1T | 2.76 | 0 | OHL | 0.1391 | 0.5715 | 0.155 | 203 | 193 | 176 | 193 | B-2-1a
DUNM1C | DUNM1T | 3.24 | 0 | OHL | 0.1632 | 0.6709 | 0.181 | 203 | 193 | 176 | 193 | B-2-1a
DUNM1C | DUNM1T | 3.24 | 0 | OHL | 0.1632 | 0.6709 | 0.181 | 203 | 193 | 176 | 193 | B-2-1a
DYCE1J | DYCE1Q | 1.93 | 0 | OHL | 0.0978 | 0.4332 | 0.33 | 241 | 230 | 210 | 230 | B-2-1a
DYCE1T | KINT1T | 10.17 | 0 | OHL | 0.5187 | 2.2781 | 0.525 | 241 | 230 | 210 | 230 | B-2-1a
DYCE1U | KINT1U | 10.17 | 0 | OHL | 0.6335 | 2.2972 | 0.519 | 145 | 131 | 116 | 131 | B-2-1a
ELGI1L | NAIR1Q | 33.9 | 0 | OHL | 1.7289 | 7.5936 | 1.763 | 241 | 230 | 210 | 230 | B-2-1a
ELGI1M | NAIR1R | 33.9 | 0 | OHL | 1.7289 | 7.5936 | 1.763 | 241 | 230 | 210 | 230 | B-2-1a
ELGI1Q | KEIT1- | 27.4 | 0 | OHL | 1.3974 | 6.1376 | 1.425 | 241 | 230 | 210 | 230 | B-2-1a
ELGI1R | KEIT1- | 27.4 | 0 | OHL | 1.3974 | 6.1376 | 1.425 | 241 | 230 | 210 | 230 | B-2-1a
ERRO1J | TUMB1R | 1 | 0 | OHL | 0.1 | 0.22 | 0.05 | 126 | 117 | 101 | 117 | B-2-1a
ERRO1J | WHIB1A | 4.87 | 0 | OHL | 0.4973 | 1.1403 | 0.242 | 132 | 123 | 106 | 123 | B-2-1a
ERRO1K | TUMB1Q | 1 | 0 | OHL | 0.1 | 0.22 | 0.05 | 126 | 117 | 101 | 117 | B-2-1a
ERRO1K | WHIB1B | 4.87 | 0 | OHL | 0.4973 | 1.1403 | 0.242 | 132 | 123 | 106 | 123 | B-2-1a
ERRO1T | KIIN1- | 36.9 | 0 | OHL | 3.75 | 8.58 | 1.82 | 132 | 123 | 106 | 123 | B-2-1a
FAAR1Q | TOMT1K | 7.2 | 0 | OHL | 0.6544 | 1.6631 | 0.361 | 132 | 123 | 106 | 123 | B-2-1a
FAAR1R | TOMT1J | 7.2 | 0 | OHL | 0.6544 | 1.6631 | 0.361 | 132 | 123 | 106 | 123 | B-2-1a
FARI2J | FOYE2- | 8.4 | 0 | OHL | 0.0479 | 0.3363 | 2.358 | 935 | 880 | 790 | 880 | B-2-1a
FARI2J | KNOC2J | 14.9 | 0 | OHL | 0.0851 | 0.5967 | 4.182 | 935 | 880 | 790 | 880 | B-2-1a
FARI2K | FOYE2- | 8.4 | 0 | OHL | 0.0479 | 0.3363 | 2.358 | 935 | 880 | 790 | 880 | B-2-1a
FARI2K | KNOC2K | 14.9 | 0 | OHL | 0.0851 | 0.5967 | 4.182 | 935 | 880 | 790 | 880 | B-2-1a
FAUG1J | LAGG1Q | 6.49 | 0 | OHL | 0.739 | 1.477 | 0.325 | 221 | 216 | 208 | 216 | B-2-1a
FAUG1K | LAGG1R | 6.49 | 0 | OHL | 0.739 | 1.477 | 0.325 | 221 | 216 | 208 | 216 | B-2-1a
FAUG4J | MELG4J | 24.01 | 0 | OHL | 0.0311 | 0.4597 | 14.517 | 2780 | 2670 | 2480 | 2670 | B-2-1a
FERO1- | FERO1S | 5.1 | 0 | OHL | 0.7089 | 1.0659 | 0.265 | 99 | 92 | 79 | 92 | B-2-1a
FERO1S | TAYN1R | 7.49 | 0 | OHL | 1.063 | 1.759 | 0.366 | 99 | 92 | 79 | 92 | B-2-1a
FIDD1A | FOGG1R | 25 | 0 | OHL | 2.96 | 6.06 | 1.22 | 112 | 104 | 90 | 104 | B-2-1a
FINL1Q | KIIN1- | 2.1 | 0 | OHL | 0.21 | 0.5 | 0.1 | 126 | 117 | 101 | 117 | B-2-1a
FOGG1Q | KINT1- | 15.6 | 0 | OHL | 1.826 | 3.742 | 0.752 | 112 | 104 | 90 | 104 | B-2-1a
FOGG1Q | TARL1Q | 34.6 | 0 | OHL | 3.12 | 7.98 | 1.7 | 132 | 123 | 106 | 123 | B-2-1a
FOGG1R | TARL1R | 34.6 | 0 | OHL | 3.12 | 7.98 | 1.7 | 132 | 123 | 106 | 123 | B-2-1a
FRAS1Q | LUMB1Q | 10.1 | 0 | OHL | 0.9 | 2.34 | 0.502 | 126 | 117 | 101 | 117 | B-2-1a
FRAS1R | LUMB1R | 10.1 | 0 | OHL | 0.9 | 2.34 | 0.502 | 126 | 117 | 101 | 117 | B-2-1a
FWIL1R | LUND1- | 9.3 | 0 | OHL | 0.849 | 2.16 | 0.463 | 136 | 129 | 118 | 129 | B-2-1a
GLEN1Q | LAGG1Q | 4.8 | 0 | OHL | 0.546 | 1.132 | 0.232 | 263 | 257 | 248 | 257 | B-2-1a
GLFA1- | KEIT1- | 29.6 | 0 | OHL | 3.0087 | 6.8969 | 1.466 | 126 | 117 | 101 | 117 | B-2-1a
GLRB2- | TEAL2K | 38.8 | 0 | OHL | 0.19 | 1.67 | 10.2 | 1090 | 1030 | 925 | 1030 | B-2-1a
GRIF1S | WHIB1H | 14.17 | 0 | OHL | 1.4476 | 3.3191 | 0.704 | 132 | 123 | 106 | 123 | B-2-1a
GRIF1T | WHIB1G | 14.17 | 0 | OHL | 1.4476 | 3.3191 | 0.704 | 132 | 123 | 106 | 123 | B-2-1a
GRUB1Q | MOSS1S | 2.73 | 0 | OHL | 0.1392 | 0.6115 | 0.142 | 224 | 211 | 189 | 211 | B-2-1a
GRUB1R | MOSS1T | 2.73 | 0 | OHL | 0.1392 | 0.6115 | 0.142 | 224 | 211 | 189 | 211 | B-2-1a
INNE1Q | SLKB1J | 1.97 | 0 | OHL | 0.1005 | 0.4413 | 0.102 | 241 | 230 | 210 | 230 | B-2-1a
INNE1R | SLKB1K | 1.97 | 0 | OHL | 0.1005 | 0.4413 | 0.102 | 241 | 230 | 210 | 230 | B-2-1a
INRU1Q | PEHG1Q | 1.8 | 0 | OHL | 0.0918 | 0.4032 | 0.094 | 241 | 230 | 210 | 230 | B-2-1a
INRU1R | PEHG1R | 1.8 | 0 | OHL | 0.0918 | 0.4032 | 0.094 | 241 | 230 | 210 | 230 | B-2-1a
INRU1S | SFER1J | 11.3 | 0 | OHL | 0.6 | 2.379 | 0.617 | 195 | 181 | 157 | 181 | B-2-1a
INVE1K | SLOY1E | 21.3 | 0 | OHL | 1.9383 | 4.9629 | 1.065 | 126 | 117 | 101 | 117 | B-2-1a
INVR1- | INVR1A | 6.18 | 0 | OHL | 0.6294 | 1.4386 | 0.305 | 132 | 126 | 106 | 126 | B-2-1a
INVR1- | INVR1B | 6.18 | 0 | OHL | 0.6294 | 1.4386 | 0.305 | 132 | 126 | 106 | 126 | B-2-1a
INVR1- | SLOY1K | 11.22 | 0 | OHL | 1.14 | 2.614 | 0.55 | 132 | 126 | 106 | 126 | B-2-1a
INVR1- | SLOY1T | 5.82 | 0 | OHL | 0.59 | 1.356 | 0.285 | 132 | 126 | 106 | 126 | B-2-1a
INVR1C | KIIN1- | 23 | 0 | OHL | 2.3423 | 5.3538 | 1.134 | 132 | 126 | 106 | 126 | B-2-1a
INVR1D | KIIN1- | 23 | 0 | OHL | 2.3423 | 5.3538 | 1.134 | 132 | 126 | 106 | 126 | B-2-1a
KEIT1J | MACD1Q | 37.8 | 0 | OHL | 3.84 | 8.8 | 1.87 | 132 | 123 | 106 | 123 | B-2-1a
KEIT1K | MACD1R | 37.77 | 0 | OHL | 3.84 | 8.8 | 1.87 | 132 | 123 | 106 | 123 | B-2-1a
KIIN1- | LOCH1- | 2.4 | 0 | OHL | 0.25 | 0.58 | 0.12 | 126 | 117 | 101 | 117 | B-2-1a
KIIN1- | SFIL1Q | 21.6 | 0 | OHL | 2.19 | 5.2 | 1.03 | 126 | 117 | 101 | 117 | B-2-1a
KILC1Q | NANT1Q | 4.2 | 0 | OHL | 0.59 | 1.03 | 0.19 | 99 | 92 | 79 | 92 | B-2-1a
KILC1Q | TAYN1Q | 7.6 | 0 | OHL | 1.07 | 1.78 | 0.37 | 99 | 92 | 79 | 92 | B-2-1a
KILO1- | LUND1- | 15.2 | 0 | OHL | 1.054 | 3.441 | 0.775 | 126 | 117 | 101 | 117 | B-2-1a
KINT2J | PERS2R | 28.2 | 0 | OHL | 0.14 | 1.23 | 7.42 | 1090 | 1030 | 920 | 1030 | B-2-1a
KINT2J | TEAL2A | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640 | B-2-1a
KINT2K | PEHE2- | 50.4 | 0 | OHL | 0.26 | 2.19 | 13.22 | 1090 | 1030 | 920 | 1030 | B-2-1a
KINT2K | TEAL2B | 100.6 | 0 | OHL | 0.61 | 5.36 | 22.142 | 695 | 640 | 550 | 640 | B-2-1a
KINT4J | ROTI4J | 23.2 | 0 | OHL | 0.0464 | 0.4478 | 13.649 | 2000 | 1920 | 1790 | 1920 | B-2-1a
KINT4K | ROTI4K | 23.2 | 0 | OHL | 0.0464 | 0.4478 | 13.649 | 2000 | 1920 | 1790 | 1920 | B-2-1a
KNOC2N | TOMT2K | 18.6 | 0 | OHL | 0.093 | 1.023 | 3.962 | 810 | 765 | 685 | 765 | B-2-1a
KNOC2P | TOMT2J | 18.6 | 0 | OHL | 0.093 | 1.023 | 3.962 | 810 | 765 | 685 | 765 | B-2-1a
LAGG1R | MILW1S | 5.7 | 0 | OHL | 0.648 | 1.344 | 0.276 | 263 | 257 | 248 | 257 | B-2-1a
LOCB1R | SHIN1- | 8.34 | 0 | OHL | 0.7614 | 1.9415 | 0.414 | 126 | 117 | 101 | 117 | B-2-1a
LOCB1U | MYBS1Q | 85.3 | 0 | OHL | 7.7872 | 19.8576 | 4.2327 | 126 | 117 | 101 | 117 | B-2-1a
LUIC1Q | ORRI1S | 5.4 | 0 | OHL | 0.1271 | 1.1789 | 0.285 | 464 | 446 | 414 | 446 | B-2-1a
LUIC1R | ORRI1T | 5.53 | 0 | OHL | 0.1301 | 1.2064 | 0.292 | 464 | 446 | 414 | 446 | B-2-1a
LUMB1Q | SFER1K | 6.3 | 0 | OHL | 0.64 | 1.46 | 0.31 | 126 | 117 | 101 | 117 | B-2-1a
LUMB1Q | STRI1Q | 7.9 | 0 | OHL | 0.71 | 1.84 | 0.395 | 126 | 117 | 101 | 117 | B-2-1a
LUMB1R | SFER1J | 6.3 | 0 | OHL | 0.64 | 1.46 | 0.31 | 126 | 117 | 101 | 117 | B-2-1a
LUMB1R | STRI1R | 7.9 | 0 | OHL | 0.71 | 1.84 | 0.395 | 126 | 117 | 101 | 117 | B-2-1a
LUNA1Q | TEAL1- | 17.9 | 0 | OHL | 0.78 | 3.91 | 0.94 | 183 | 160 | 149 | 160 | B-2-1a
LUNA1R | TEAL1- | 17.9 | 0 | OHL | 0.78 | 3.91 | 0.94 | 183 | 160 | 149 | 160 | B-2-1a
MELG4J | TUMM4- | 53.19 | 0 | OHL | 0.0689 | 1.0183 | 32.161 | 2780 | 2670 | 2480 | 2670 | B-2-1a
MILC1S | TEAL1- | 6.8 | 0 | OHL | 0.29 | 1.48 | 0.36 | 183 | 160 | 149 | 160 | B-2-1a
MILC1T | TEAL1- | 6.8 | 0 | OHL | 0.29 | 1.48 | 0.36 | 183 | 160 | 149 | 160 | B-2-1a
MILW1Q | MILW1S | 1.3 | 0 | OHL | 0.065 | 0.2691 | 0.073 | 203 | 193 | 176 | 193 | B-2-1a
MOSS1Q | MOSS1S | 0.21 | 0 | OHL | 0.0191 | 0.0504 | 0.01 | 132 | 123 | 106 | 123 | B-2-1a
MOSS1R | MOSS1T | 0.21 | 0 | OHL | 0.0191 | 0.0504 | 0.01 | 132 | 123 | 106 | 123 | B-2-1a
MOTA1Q | SHIN1- | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 132 | 123 | 106 | 123 | B-2-1a
MOTA1R | SHIN1- | 31.2 | 0 | OHL | 3.37 | 7.72 | 1.64 | 126 | 117 | 101 | 117 | B-2-1a
MYBS1Q | SPIT1J | 3.99 | 0 | OHL | 0.3643 | 0.9289 | 0.198 | 126 | 117 | 101 | 117 | B-2-1a
MYBS1R | SPIT1J | 3.99 | 0 | OHL | 0.3643 | 0.9289 | 0.198 | 126 | 117 | 101 | 117 | B-2-1a
MYBS1S | SPIT1M | 5 | 0 | OHL | 0.1182 | 1.0607 | 0.276 | 465 | 445 | 415 | 445 | B-2-1a
MYBS1T | SPIT1K | 5 | 0 | OHL | 0.1182 | 1.0607 | 0.276 | 465 | 445 | 415 | 445 | B-2-1a
NAIR1Q | SLKB1L | 26.33 | 0 | OHL | 1.3428 | 5.8979 | 1.369 | 241 | 230 | 210 | 230 | B-2-1a
NAIR1R | SLKB1M | 26.33 | 0 | OHL | 1.3428 | 5.8979 | 1.369 | 241 | 230 | 210 | 230 | B-2-1a
NEDE4J | PEHE4J | 30.04 | 0 | OHL | 0.0601 | 0.5798 | 17.673 | 2000 | 1920 | 1790 | 1920 | B-2-1a
NEDE4J | ROTI4J | 17.3 | 0 | OHL | 0.0346 | 0.3339 | 10.178 | 2000 | 1920 | 1790 | 1920 | B-2-1a
NEDE4K | PEHE4K | 30.04 | 0 | OHL | 0.0601 | 0.5798 | 17.673 | 2000 | 1920 | 1790 | 1920 | B-2-1a
NEDE4K | ROTI4K | 17.3 | 0 | OHL | 0.0346 | 0.3339 | 10.178 | 2000 | 1920 | 1790 | 1920 | B-2-1a
PORA1S | PORA1U | 6.14 | 0 | OHL | 0.8535 | 1.3692 | 0.301 | 99 | 92 | 79 | 92 | B-2-1a
QUOI1- | QUOI1Q | 1.6 | 0 | OHL | 0.12 | 0.28 | 0.05 | 150 | 142 | 128 | 142 | B-2-1a
RANN1Q | TUMB1Q | 23.8 | 0 | OHL | 2.42 | 5.51 | 1.18 | 126 | 117 | 101 | 117 | B-2-1a
RANN1R | TUMB1R | 23.8 | 0 | OHL | 2.42 | 5.51 | 1.18 | 126 | 117 | 101 | 117 | B-2-1a
SFEE1A | SFEG1Q | 0.39 | 0 | OHL | 0.0469 | 0.092 | 0.019 | 126 | 117 | 101 | 117 | B-2-1a
SFEE1A | SFER1L | 1.71 | 0 | OHL | 0.2031 | 0.398 | 0.081 | 126 | 117 | 101 | 117 | B-2-1a
SFEE1B | SFEG1R | 0.39 | 0 | OHL | 0.0469 | 0.092 | 0.019 | 126 | 117 | 101 | 117 | B-2-1a
SFEE1B | SFER1M | 1.71 | 0 | OHL | 0.2031 | 0.398 | 0.081 | 126 | 117 | 101 | 117 | B-2-1a
SLOY1A | SLOY1M | 0.617 | 0 | OHL | 0.0561 | 0.1438 | 0.0309 | 126 | 117 | 101 | 117 | B-2-1a
SLOY1B | SLOY1L | 0.617 | 0 | OHL | 0.0561 | 0.1438 | 0.0309 | 126 | 117 | 101 | 117 | B-2-1a
SLOY1C | SLOY1N | 0.627 | 0 | OHL | 0.0571 | 0.1461 | 0.0313 | 126 | 117 | 101 | 117 | B-2-1a
SLOY1D | SLOY1P | 0.627 | 0 | OHL | 0.0571 | 0.1461 | 0.0313 | 126 | 117 | 101 | 117 | B-2-1a
SLOY1J | SLOY1T | 5.4 | 0 | OHL | 0.547 | 1.254 | 0.266 | 132 | 123 | 106 | 123 | B-2-1a
SPIT2J | THUS2J | 10.54 | 0 | OHL | 0.0527 | 0.5586 | 2.319 | 965 | 925 | 865 | 925 | B-2-1a
SPIT2K | THUS2K | 10.54 | 0 | OHL | 0.0527 | 0.5586 | 2.319 | 965 | 925 | 865 | 925 | B-2-1a
WHIB1C | WHIB1E | 3.57 | 0 | OHL | 0.3644 | 0.8355 | 0.177 | 132 | 123 | 106 | 123 | B-2-1a
WHIB1D | WHIB1F | 3.57 | 0 | OHL | 0.3644 | 0.8355 | 0.177 | 132 | 123 | 106 | 123 | B-2-1a
AUCH2- | MAHI2- | 14.5 | 0 | OHL | 0.109 | 0.8301 | 2.9503 | 570 | 570 | 570 | 570 | B-2-1b
BLAH1- | DUNH1Q | 1.15 | 0 | OHL | 0.0294 | 0.2043 | 0.0733 | 418 | 386 | 386 | 386 | B-2-1b
BLAH1- | DUNH1R | 1.15 | 0 | OHL | 0.0294 | 0.2043 | 0.0733 | 466 | 430 | 418 | 430 | B-2-1b
BONN1- | CUMB1Q | 10.89 | 0 | OHL | 0.4305 | 2.4371 | 0.5639 | 135 | 135 | 135 | 135 | B-2-1b
BONN1- | CUMB1R | 10.89 | 0 | OHL | 0.4305 | 2.4371 | 0.5639 | 135 | 135 | 135 | 135 | B-2-1b
BROX1Q | CURR1A | 10.34 | 0 | OHL | 0.8009 | 2.4722 | 0.505 | 132 | 123 | 106 | 123 | B-2-1b
BROX1R | CURR1B | 10.34 | 0 | OHL | 0.8009 | 2.4722 | 0.505 | 132 | 123 | 106 | 123 | B-2-1b
BUSB2- | NEIL2- | 20.24 | 0 | OHL | 0.0856 | 0.8267 | 5.625 | 1120 | 1060 | 990 | 1060 | B-2-1b
BUSB2- | STHA2A | 15.14 | 0 | OHL | 0.064 | 0.6181 | 4.2097 | 750 | 690 | 630 | 690 | B-2-1b
CLYM2- | DALM2Q | 4.21 | 0 | OHL | 0.019 | 0.1713 | 1.1692 | 750 | 690 | 630 | 690 | B-2-1b
CLYM2- | EERH2- | 8.75 | 0 | OHL | 0.0197 | 0.3069 | 2.8023 | 1500 | 1500 | 1500 | 1500 | B-2-1b
CLYM2- | EKIL2Q | 5.62 | 0 | OHL | 0.0253 | 0.2391 | 1.4927 | 1120 | 1060 | 990 | 1060 | B-2-1b
CLYM2- | EKIL2R | 5.62 | 0 | OHL | 0.0253 | 0.2391 | 1.4927 | 1120 | 1060 | 990 | 1060 | B-2-1b
COAL4- | STHA4B | 21.73 | 0 | OHL | 0.038 | 0.4118 | 13.0101 | 2210 | 2130 | 1980 | 2130 | B-2-1b
COCK2- | KAIM2- | 18.29 | 0 | OHL | 0.0779 | 0.756 | 5.0669 | 1120 | 1060 | 990 | 1060 | B-2-1b
COCK2- | SMEA2- | 9.51 | 0 | OHL | 0.0405 | 0.3931 | 2.6346 | 1120 | 1060 | 990 | 1060 | B-2-1b
COYL2- | COYW2T | 1.32 | 0 | OHL | 0.0058 | 0.0522 | 0.3778 | 1500 | 1500 | 1500 | 1500 | B-2-1b
COYW2S | KILS2- | 13.37 | 0 | OHL | 0.0588 | 0.5269 | 3.8357 | 1500 | 1500 | 1500 | 1500 | B-2-1b
COYW2T | KILS2- | 13.37 | 0 | OHL | 0.0588 | 0.5269 | 3.8357 | 1500 | 1500 | 1500 | 1500 | B-2-1b
CUPA1Q | LEVT1Q | 13.27 | 0 | OHL | 1.2026 | 2.9807 | 0.6715 | 143 | 142 | 128 | 142 | B-2-1b
CUPA1R | LEVT1R | 13.27 | 0 | OHL | 1.2026 | 2.9807 | 0.6715 | 143 | 142 | 128 | 142 | B-2-1b
CURR2- | GRMO2- | 42.2 | 0 | OHL | 0.1916 | 1.7399 | 11.6642 | 1090 | 1030 | 925 | 1030 | B-2-1b
CURR2- | KAIM2- | 9.35 | 0 | OHL | 0.0398 | 0.3865 | 2.5902 | 1380 | 1320 | 1230 | 1320 | B-2-1b
CURR2- | KAIM2- | 9.35 | 0 | OHL | 0.0398 | 0.3865 | 2.5902 | 1380 | 1320 | 1230 | 1320 | B-2-1b
CURR2- | KINC2- | 55.76 | 0 | OHL | 0.2531 | 2.2958 | 15.4272 | 1090 | 1030 | 925 | 1030 | B-2-1b
DEVM4- | NEIL4R | 28.474 | 0 | OHL | 0.058184 | 0.59672 | 15.8233 | 2000 | 1920 | 1790 | 1920 | B-2-1b
DEVO1- | WFIE1B | 31.8 | 0 | OHL | 2.8944 | 7.5329 | 1.5454 | 162 | 154 | 141 | 154 | B-2-1b
DRUM2R | WIYH2- | 2.46 | 0 | OHL | 0.0111 | 0.1001 | 0.6832 | 120 | 120 | 120 | 120 | B-2-1b
DUNF1Q | MOSM1A | 10.46 | 0 | OHL | 0.5557 | 2.2694 | 0.5549 | 215 | 215 | 198 | 215 | B-2-1b
DUNF1R | MOSM1B | 10.46 | 0 | OHL | 0.5557 | 2.2694 | 0.5549 | 215 | 215 | 198 | 215 | B-2-1b
DUNH1Q | NECU1- | 13.65 | 0 | OHL | 0.3486 | 2.4244 | 0.8703 | 484 | 458 | 418 | 458 | B-2-1b
DUNH1R | NECU1- | 13.65 | 0 | OHL | 0.3486 | 2.4244 | 0.8703 | 484 | 458 | 418 | 458 | B-2-1b
ECCL4C | STWB4Q | 7.39 | 0 | OHL | 0.0063 | 0.1209 | 5.1175 | 2770 | 2770 | 2660 | 2770 | B-2-1b
ECCL4D | STWB4R | 7.39 | 0 | OHL | 0.0063 | 0.1209 | 5.1175 | 2770 | 2770 | 2660 | 2770 | B-2-1b
EERH2- | NEAR2Q | 15.34 | 0 | OHL | 0.077 | 0.632 | 4.283 | 950 | 885 | 760 | 885 | B-2-1b
EKIL2Q | EKIL2S | 5.17 | 0 | OHL | 0.0138 | 0.1834 | 1.6594 | 865 | 825 | 750 | 825 | B-2-1b
EKIL2Q | STHA2A | 4.79 | 0 | OHL | 0.0216 | 0.2038 | 1.2722 | 1050 | 965 | 880 | 965 | B-2-1b
EKIL2R | STHA2B | 4.79 | 0 | OHL | 0.0216 | 0.2038 | 1.2722 | 1050 | 965 | 880 | 965 | B-2-1b
EKIS2- | NEIL2- | 29.58 | 0 | OHL | 0.1251 | 1.2082 | 8.2207 | 1110 | 1030 | 885 | 1030 | B-2-1b
ELVA3A | PRST3A | 1.01 | 0 | OHL | 0.8089 | 2.9543 | 0.004 | 49 | 45 | 39 | 45 | B-2-1b
ELVA4- | GRNA4C | 65.54 | 0 | OHL | 0.1155 | 1.2673 | 38.8356 | 2210 | 2130 | 1980 | 2130 | B-2-1b
ELVA4- | MOFF4- | 23.5 | 0 | OHL | 0.0414 | 0.4544 | 13.9258 | 2210 | 2130 | 1980 | 2130 | B-2-1b
GARB1Q | HELE1Q | 15.313 | 0 | OHL | 1.3875 | 3.4126 | 0.7803 | 132 | 123 | 106 | 123 | B-2-1b
GARB1R | STLE1Q | 26.909 | 0 | OHL | 2.4383 | 5.997 | 1.3713 | 132 | 123 | 106 | 123 | B-2-1b
GARB1S | GARE1S | 5.03 | 0 | OHL | 0.4558 | 1.1211 | 0.2564 | 132 | 123 | 106 | 123 | B-2-1b
GARB1T | GARE1T | 5.061 | 0 | OHL | 0.4586 | 1.1279 | 0.2579 | 132 | 123 | 106 | 123 | B-2-1b
GARE1S | WHTL1S | 1.68 | 0 | OHL | 0.2125 | 0.3513 | 0.0919 | 100 | 94 | 80 | 94 | B-2-1b
GARE1T | WHTL1T | 1.67 | 0 | OHL | 0.2112 | 0.3492 | 0.0913 | 100 | 94 | 80 | 94 | B-2-1b
GLLU1Q | NETS1- | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 49 | 49 | 49 | 49 | B-2-1b
GLNI1- | WFIE1B | 7.11 | 0 | OHL | 0.5359 | 1.6524 | 0.3546 | 264 | 246 | 212 | 246 | B-2-1b
GLRB2- | GLRO2- | 14.68 | 0 | OHL | 0.0664 | 0.6181 | 3.956 | 1090 | 1030 | 925 | 1030 | B-2-1b
GLRO2- | WFIE2- | 12.08 | 0 | OHL | 0.0547 | 0.5102 | 3.2488 | 1090 | 1030 | 925 | 1030 | B-2-1b
GRMO2- | KINC2- | 14.96 | 0 | OHL | 0.068 | 0.6184 | 4.1277 | 1050 | 965 | 880 | 965 | B-2-1b
HUNE4- | NEIL4Q | 35.43 | 0 | OHL | 0.0706 | 0.7289 | 20.0655 | 1390 | 1280 | 1110 | 1280 | B-2-1b
HUNE4- | NEIL4R | 35.43 | 0 | OHL | 0.0706 | 0.7289 | 20.0655 | 1390 | 1280 | 1110 | 1280 | B-2-1b
INVR2- | WIYH2- | 55.6 | 0 | OHL | 0.2351 | 2.2709 | 15.4613 | 570 | 570 | 570 | 570 | B-2-1b
JUNA1T | KILW1Q | 12.418 | 0 | OHL | 0.4909 | 2.779 | 0.643 | 146 | 146 | 146 | 146 | B-2-1b
JUNA1T | SACO1Q | 8.14 | 0 | OHL | 0.3086 | 1.8332 | 0.4224 | 151 | 151 | 151 | 151 | B-2-1b
KILS1- | MEAD1- | 12.57 | 0 | OHL | 0.874 | 2.581 | 2.166 | 162 | 154 | 141 | 154 | B-2-1b
KILS4- | STHA4A | 34.948 | 0 | OHL | 0.0712 | 0.7173 | 19.8386 | 2000 | 1920 | 1790 | 1920 | B-2-1b
KILS4T | STHA4B | 34.948 | 0 | OHL | 0.0712 | 0.7173 | 19.8386 | 2000 | 1920 | 1790 | 1920 | B-2-1b
KILW1Q | MEAD1- | 13.8 | 0 | OHL | 0.7331 | 2.9941 | 0.732 | 146 | 146 | 138 | 146 | B-2-1b
KILW1R | MEAD1- | 13.8 | 0 | OHL | 0.7331 | 2.9941 | 0.732 | 146 | 146 | 138 | 146 | B-2-1b
LAMB2- | PORD2Q | 3.94 | 0 | OHL | 0.0182 | 0.1701 | 1.0531 | 955 | 885 | 760 | 885 | B-2-1b
LEVE1Q | LEVT1Q | 2.16 | 0 | OHL | 0.1957 | 0.4852 | 0.1093 | 143 | 142 | 128 | 142 | B-2-1b
LEVE1R | LEVT1R | 2.26 | 0 | OHL | 0.2048 | 0.5083 | 0.1143 | 143 | 142 | 128 | 142 | B-2-1b
LEVT1Q | REDH1- | 8.61 | 0 | OHL | 0.7803 | 1.9339 | 0.4357 | 143 | 142 | 128 | 142 | B-2-1b
LEVT1R | WFIE1B | 18.707 | 0 | OHL | 1.588 | 4.18 | 0.9537 | 143 | 142 | 128 | 142 | B-2-1b
MOSM2- | WFIE2- | 8.243 | 0 | OHL | 0.0378 | 0.3641 | 2.1507 | 1090 | 1030 | 925 | 1030 | B-2-1b
NEAR2Q | WISH2- | 16.1 | 0 | OHL | 0.0726 | 0.655 | 4.4712 | 955 | 885 | 760 | 885 | B-2-1b
NEAR2R | WISH2- | 16.1 | 0 | OHL | 0.0726 | 0.655 | 4.4712 | 285 | 285 | 285 | 285 | B-2-1b
PAIS1Q | PAIS1S | 1.87 | 0 | OHL | 0.0366 | 0.3302 | 0.1197 | 460 | 425 | 365 | 425 | B-2-1b
PAIS1R | PAIS1T | 1.87 | 0 | OHL | 0.0366 | 0.3302 | 0.1197 | 460 | 425 | 365 | 425 | B-2-1b
REDH1- | WFIE1A | 10.097 | 0 | OHL | 0.8077 | 2.2461 | 0.5179 | 157 | 152 | 141 | 152 | B-2-1b
WFIB2- | WFIE2- | 22.48 | 0 | OHL | 0.1014 | 0.933 | 6.1144 | 1090 | 1030 | 925 | 1030 | B-2-1b
WHTB1S | WHTL1S | 2.05 | 0 | OHL | 0.2593 | 0.4287 | 0.1121 | 100 | 94 | 80 | 94 | B-2-1b
WHTB1T | WHTL1T | 2.05 | 0 | OHL | 0.2593 | 0.4287 | 0.1121 | 100 | 94 | 80 | 94 | B-2-1b
HAKB1- | HARK13 | 1 | 0 | OHL | 0.7047 | 2.0317 | 0.451 | 132 | 123 | 106 | 123 | B-2-1b
ABHA4A | EXET41 | 48.785 | 0 | OHL | 0.0778 | 0.9831 | 27.9792 | 2078 | 2078 | 2078 | 2078 | B-2-1c
ABHA4A | LAGA41 | 26.121 | 0 | OHL | 0.0417 | 0.5027 | 15.6941 | 2423 | 2327 | 2168 | 2327 | B-2-1c
ABHA4B | EXET41 | 49.051 | 0 | OHL | 0.0783 | 0.9885 | 28.1313 | 2423 | 2327 | 2168 | 2327 | B-2-1c
ABHA4B | LAGA41 | 26.121 | 0 | OHL | 0.0417 | 0.5027 | 15.6941 | 2423 | 2327 | 2168 | 2327 | B-2-1c
ABTH21 | COWT2A | 13.318 | 0 | OHL | 0.0503 | 0.5449 | 3.758 | 932 | 879 | 790 | 879 | B-2-1c
ABTH21 | PYLE21 | 35.388 | 0 | OHL | 0.1819 | 1.4523 | 9.9528 | 932 | 879 | 790 | 879 | B-2-1c
ABTH21 | TREM21 | 46.451 | 0 | OHL | 0.2267 | 2.1393 | 11.8321 | 682 | 629 | 538 | 629 | B-2-1c
ABTH21 | UPPB21 | 26.996 | 0 | OHL | 0.1234 | 1.1426 | 7.3237 | 955 | 882 | 762 | 882 | B-2-1c
ALDW21 | BRIN21 | 17.961 | 0 | OHL | 0.1442 | 0.7628 | 4.8487 | 626 | 591 | 535 | 591 | B-2-1c
ALDW21 | WMEL21 | 8.96 | 0 | OHL | 0.0409 | 0.3891 | 2.3695 | 955 | 882 | 762 | 882 | B-2-1c
AMEM4A | ECLA41 | 35.315 | 0 | OHL | 0.0642 | 0.7026 | 20.4666 | 2009 | 1911 | 1746 | 1911 | B-2-1c
AMEM4B | ECLA41 | 35.315 | 0 | OHL | 0.0642 | 0.7026 | 20.4666 | 2032 | 1933 | 1766 | 1933 | B-2-1c
AXMI41 | EXET41 | 36.184 | 0 | OHL | 0.0404 | 0.6915 | 21.9115 | 2779 | 2568 | 2217 | 2568 | B-2-1c
BARK21 | REBR22 | 10.879 | 0 | OHL | 0.0411 | 0.4451 | 3.0706 | 1129 | 1081 | 1000 | 1081 | B-2-1c
BARK22 | REBR21 | 10.854 | 0 | OHL | 0.041 | 0.4441 | 3.0636 | 1205 | 1127 | 1044 | 1127 | B-2-1c
BARK41 | CHUE4A | 13.654 | 0 | OHL | 0.0213 | 0.2629 | 8.1589 | 3102 | 3048 | 2958 | 3048 | B-2-1c
BARK41 | CHUE4B | 13.654 | 0 | OHL | 0.0213 | 0.2629 | 8.1589 | 3102 | 3048 | 2958 | 3048 | B-2-1c
BARK41 | WTHU4A | 15.872 | 0 | OHL | 0.0289 | 0.3158 | 9.1985 | 2009 | 1911 | 1746 | 1911 | B-2-1c
BARK41 | WTHU4B | 15.872 | 0 | OHL | 0.0289 | 0.3158 | 9.1985 | 2009 | 1911 | 1746 | 1911 | B-2-1c
BESW21 | COVE21 | 18.668 | 0 | OHL | 0.0853 | 0.7901 | 5.0645 | 955 | 882 | 762 | 882 | B-2-1c
BESW21 | COVE21 | 18.668 | 0 | OHL | 0.0853 | 0.7901 | 5.0645 | 955 | 882 | 762 | 882 | B-2-1c
BESW21 | FECK21 | 35.814 | 0 | OHL | 0.1425 | 1.5095 | 9.7917 | 955 | 882 | 762 | 882 | B-2-1c
BICF41 | SPLN41 | 20.109 | 0 | OHL | 0.0191 | 0.355 | 13.187 | 3156 | 3032 | 2823 | 3032 | B-2-1c
BICF41 | WALP41 | 37.775 | 0 | OHL | 0.0335 | 0.6488 | 25.3895 | 3189 | 3063 | 2853 | 3063 | B-2-1c
BICF41 | WBUR41 | 65.55 | 0 | OHL | 0.0581 | 1.1259 | 44.059 | 3326 | 3160 | 2971 | 3160 | B-2-1c
BICF41 | WBUR42 | 65.55 | 0 | OHL | 0.0581 | 1.1259 | 44.059 | 3326 | 3160 | 2971 | 3160 | B-2-1c
BIGG41 | EASO41 | 16.5 | 0 | OHL | 0.0146 | 0.2834 | 11.1085 | 3326 | 2790 | 3320 | 3320 | B-2-1c
BIGG41 | WYMO41 | 18.772 | 0 | OHL | 0.0166 | 0.3225 | 12.6381 | 3326 | 2790 | 3320 | 3320 | B-2-1c
BIRK21 | CAPE21 | 15.448 | 0 | OHL | 0.0703 | 0.6839 | 4.0052 | 955 | 882 | 762 | 882 | B-2-1c
BIRK21 | CAPE21 | 15.448 | 0 | OHL | 0.0703 | 0.6839 | 4.0052 | 955 | 882 | 762 | 882 | B-2-1c
BISW21 | FECK21 | 22.83 | 0 | OHL | 0.0938 | 0.9633 | 6.2301 | 955 | 882 | 762 | 882 | B-2-1c
BISW21 | KITW21 | 24.226 | 0 | OHL | 0.0932 | 1.0024 | 6.7545 | 955 | 882 | 762 | 882 | B-2-1c
BISW21 | KITW21 | 27.111 | 0 | OHL | 0.1054 | 1.1236 | 7.5448 | 955 | 882 | 762 | 882 | B-2-1c
BISW21 | PENN21 | 30.172 | 0 | OHL | 0.1233 | 1.2726 | 8.2379 | 1040 | 1031 | 762 | 762 | B-2-1c
BLYT21 | STEW21 | 26.779 | 0 | OHL | 0.1472 | 1.3916 | 5.9965 | 682 | 629 | 538 | 629 | B-2-1c
BLYT21 | STEW21 | 26.711 | 0 | OHL | 0.1469 | 1.388 | 5.9813 | 682 | 629 | 538 | 629 | B-2-1c
BLYT22 | TYNE21 | 16.818 | 0 | OHL | 0.0742 | 0.7144 | 4.5642 | 1360 | 1310 | 1220 | 1310 | B-2-1c
BLYT23 | TYNE2A | 16.866 | 0 | OHL | 0.0744 | 0.7164 | 4.5772 | 1360 | 1310 | 1220 | 1310 | B-2-1c
BLYT41 | MEDB4A | 27 | 0 | OHL | 0.023914 | 0.46363 | 18.1479 | 3326 | 3326 | 3326 | 3326 | B-2-1c
BLYT41 | MEDB4B | 27 | 0 | OHL | 0.023914 | 0.46363 | 18.1479 | 3326 | 3326 | 3326 | 3326 | B-2-1c
BOLN41 | LOVE41 | 64.774 | 0 | OHL | 0.0703 | 1.1266 | 42.6998 | 3102 | 2935 | 2765 | 2935 | B-2-1c
BOLN41 | LOVE41 | 64.774 | 0 | OHL | 0.0703 | 1.1266 | 42.6998 | 2771 | 2771 | 2765 | 2771 | B-2-1c
BOTW41 | CHIL41 | 7.479 | 0 | OHL | 0.0066 | 0.1285 | 5.027 | 3341 | 3160 | 2971 | 3160 | B-2-1c
BOTW41 | LOVE41 | 14.672 | 0 | OHL | 0.013 | 0.252 | 9.8617 | 3341 | 3160 | 2971 | 3160 | B-2-1c
BRAI4A | BULL41 | 12.343 | 0 | OHL | 0.0121 | 0.2133 | 8.2261 | 3066 | 2830 | 2418 | 2830 | B-2-1c
BRAI4B | RAYL41 | 33.03 | 0 | OHL | 0.0325 | 0.5709 | 22.0036 | 2779 | 2568 | 2217 | 2568 | B-2-1c
BRAW21 | MONF21 | 51.155 | 0 | OHL | 0.1174 | 1.8824 | 15.9388 | 1204 | 1115 | 1018 | 1115 | B-2-1c
BRAW4A | PADI41 | 59.3 | 0 | OHL | 0.0754 | 1.1321 | 35.9226 | 2470 | 2350 | 2146 | 2350 | B-2-1c
BRED21 | MACC21 | 19.612 | 0 | OHL | 0.0768 | 0.8127 | 5.4608 | 948 | 882 | 753 | 753 | B-2-1c
BRED21 | STAL21 | 15.054 | 0 | OHL | 0.0665 | 0.6343 | 4.1113 | 1093 | 1031 | 925 | 1031 | B-2-1c
BRFO41 | FRIS4A | 35.557 | 0 | OHL | 0.0386 | 0.6184 | 23.4396 | 2779 | 2568 | 2217 | 2568 | B-2-1c
BRFO41 | FRIS4B | 35.557 | 0 | OHL | 0.0386 | 0.6184 | 23.4396 | 2779 | 2568 | 2217 | 2568 | B-2-1c
BRFO41 | FRIS4C | 35.557 | 0 | OHL | 0.0386 | 0.6184 | 23.4396 | 2779 | 2569 | 2217 | 2569 | B-2-1c
BRFO41 | FRIS4D | 35.557 | 0 | OHL | 0.0386 | 0.6184 | 23.4396 | 2779 | 2568 | 2217 | 2568 | B-2-1c
BRIN21 | TEMP21 | 2.757 | 0 | OHL | 0.0126 | 0.117 | 0.7458 | 955 | 882 | 762 | 882 | B-2-1c
BRIN21 | TEMP22 | 2.757 | 0 | OHL | 0.0126 | 0.117 | 0.7458 | 955 | 882 | 762 | 882 | B-2-1c
BRIN22 | THUR21 | 5.704 | 0 | OHL | 0.0599 | 0.2384 | 1.5621 | 626 | 591 | 535 | 591 | B-2-1c
BRIN22 | TINP21 | 3.17 | 0 | OHL | 0.0145 | 0.1342 | 0.86 | 955 | 882 | 762 | 882 | B-2-1c
BRIN22 | TINP22 | 3.17 | 0 | OHL | 0.0145 | 0.1342 | 0.86 | 919 | 869 | 762 | 869 | B-2-1c
BRIN41 | THOM41 | 36.299 | 0 | OHL | 0.0394 | 0.6316 | 23.9221 | 2518 | 2395 | 2188 | 2395 | B-2-1c
BRIN41 | THOM42 | 36.299 | 0 | OHL | 0.0394 | 0.6316 | 23.9221 | 2545 | 2421 | 2211 | 2421 | B-2-1c
BRLE41 | WWEY4A | 49.375 | 0 | OHL | 0.0789 | 0.9495 | 29.6914 | 2199 | 2092 | 1911 | 2092 | B-2-1c
BRLE41 | WWEY4B | 49.375 | 0 | OHL | 0.0789 | 0.9495 | 29.6914 | 2199 | 2092 | 1911 | 2092 | B-2-1c
BRWA41 | BRWA4A | 4.371 | 0 | OHL | 0.0079 | 0.087 | 2.5326 | 2030 | 1930 | 1770 | 1930 | B-2-1c
BRWA4A | MELK41 | 77.004 | 0 | OHL | 0.1368 | 1.5195 | 45.0234 | 2009 | 1911 | 1746 | 1911 | B-2-1c
BRWA4A | SHUR41 | 14.02 | 0 | OHL | 0.0218 | 0.269 | 8.4136 | 3100 | 3050 | 2960 | 3050 | B-2-1c
BRWA4B | MELK41 | 76.264 | 0 | OHL | 0.1356 | 1.5048 | 44.5918 | 2009 | 2009 | 2009 | 2009 | B-2-1c
BRWA4B | SHUR41 | 14.02 | 0 | OHL | 0.0218 | 0.269 | 8.4136 | 3100 | 3050 | 2960 | 3050 | B-2-1c
BULL41 | RAYL41 | 20.646 | 0 | OHL | 0.0203 | 0.3568 | 13.7565 | 2779 | 2569 | 2217 | 2569 | B-2-1c
BURW41 | PELH41 | 42.782 | 0 | OHL | 0.0379 | 0.7348 | 28.7545 | 3326 | 3159 | 2971 | 3159 | B-2-1c
BURW41 | PELH41 | 42.934 | 0 | OHL | 0.0381 | 0.7374 | 28.8562 | 3035 | 2876 | 2238 | 2515 | B-2-1c
BURW41 | WALP41 | 51.189 | 0 | OHL | 0.0454 | 0.8792 | 34.4056 | 3326 | 3160 | 2971 | 3160 | B-2-1c
BURW41 | WALP41 | 51.183 | 0 | OHL | 0.0454 | 0.8791 | 34.4016 | 3326 | 3160 | 2971 | 3160 | B-2-1c
BUSH21 | DRAK21 | 38.153 | 0 | OHL | 0.146 | 1.6016 | 10.4839 | 1204 | 1115 | 1018 | 1115 | B-2-1c
BUSH21 | PENN21 | 21.653 | 0 | OHL | 0.0824 | 0.9078 | 5.9595 | 1038 | 1038 | 762 | 762 | B-2-1c
BUST4A | DRAK41 | 34.592 | 0 | OHL | 0.0375 | 0.6017 | 22.8026 | 1203 | 1203 | 1103 | 1119 | B-2-1c
BUST4B | DRAK41 | 34.537 | 0 | OHL | 0.0375 | 0.6007 | 22.7664 | 2779 | 2568 | 2217 | 2568 | B-2-1c
CANT41 | CLEH41 | 14.7 | 0 | OHL | 0.0229 | 0.282 | 8.8214 | 3102 | 3048 | 2853 | 3048 | B-2-1c
CANT41 | KEMS4A | 28.2 | 0 | OHL | 0.0439 | 0.5411 | 16.9228 | 3102 | 2935 | 2765 | 2935 | B-2-1c
CANT41 | RICH41 | 25 | 0 | OHL | 0.0399 | 0.4808 | 15.0336 | 2038 | 2038 | 1801 | 1801 | B-2-1c
CANT41 | RICH41 | 25 | 0 | OHL | 0.0399 | 0.4808 | 15.0336 | 2038 | 2038 | 1801 | 1801 | B-2-1c
CANT41 | SELL4C | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 3102 | 3048 | 2958 | 3048 | B-2-1c
CANT41 | SELL4D | 26.711 | 0 | OHL | 0.0416 | 0.5125 | 16.0297 | 3103 | 3048 | 2959 | 3048 | B-2-1c
CAPE4A | CONQ41 | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 3326 | 3160 | 2971 | 3160 | B-2-1c
CAPE4A | FROD41 | 18.404 | 0 | OHL | 0.0199 | 0.2926 | 13.3521 | 2889 | 2748 | 2418 | 2748 | B-2-1c
CAPE4B | CONQ41 | 11.543 | 0 | OHL | 0.0102 | 0.1983 | 7.7586 | 3326 | 3160 | 2971 | 3160 | B-2-1c
CAPE4B | FROD41 | 18.315 | 0 | OHL | 0.0198 | 0.2912 | 13.2878 | 2890 | 2749 | 2418 | 2749 | B-2-1c
CARE21 | COWT2A | 27.881 | 0 | OHL | 0.1533 | 1.4488 | 6.2406 | 682 | 629 | 538 | 629 | B-2-1c
CARE21 | USKM2B | 19.94 | 0 | OHL | 0.1096 | 1.0362 | 4.4651 | 682 | 629 | 538 | 629 | B-2-1c
CARR41 | KEAR41 | 13.154 | 0 | OHL | 0.0225 | 0.2574 | 7.7626 | 2212 | 2125 | 1979 | 2125 | B-2-1c
CARR41 | PEWO4A | 56.9 | 0 | OHL | 0.0988 | 1.1179 | 33.4404 | 2169 | 2084 | 1940 | 2084 | B-2-1c
CARR4B | DAIN41 | 2.036 | 0 | OHL | 0.0037 | 0.0405 | 1.1791 | 1553 | 1553 | 1553 | 1553 | B-2-1c
CELL41 | MACC41 | 31.617 | 0 | OHL | 0.0494 | 0.6067 | 18.9767 | 3102 | 3048 | 2958 | 3048 | B-2-1c
CHIC41 | MANN41 | 53.913 | 0 | OHL | 0.0585 | 0.9377 | 35.5401 | 3065 | 2829 | 2418 | 2829 | B-2-1c
CHIC4A | MANN41 | 54.066 | 0 | OHL | 0.0587 | 0.9404 | 35.6406 | 3065 | 2829 | 2418 | 2829 | B-2-1c
CHSI21 | WWEY21 | 15.318 | 0 | OHL | 0.0519 | 0.6229 | 4.351 | 1316 | 1213 | 1104 | 1213 | B-2-1c
CHSI21 | WWEY22 | 15.347 | 0 | OHL | 0.052 | 0.6241 | 4.3592 | 1316 | 1213 | 1104 | 1213 | B-2-1c
CHUE4A | WTHU4D | 2.419 | 0 | OHL | 0.0038 | 0.0488 | 1.378 | 3102 | 3048 | 2958 | 3048 | B-2-1c
CHUE4B | WTHU4C | 2.581 | 0 | OHL | 0.004 | 0.0519 | 1.4744 | 3102 | 3048 | 2958 | 3048 | B-2-1c
CILF2A | UPPB21 | 6.975 | 0 | OHL | 0.0319 | 0.2952 | 1.8923 | 955 | 882 | 762 | 882 | B-2-1c
CILF2B | UPPB22 | 6.975 | 0 | OHL | 0.0319 | 0.2952 | 1.8923 | 955 | 882 | 762 | 882 | B-2-1c
CILF41 | IMPP41 | 25.119 | 0 | OHL | 0.0273 | 0.4396 | 16.4758 | 2779 | 2568 | 2217 | 2568 | B-2-1c
CILF41 | RASS41 | 26.901 | 0 | OHL | 0.0292 | 0.4679 | 17.7332 | 2779 | 2568 | 2217 | 2568 | B-2-1c
CILF41 | RHIG41 | 25.011 | 0 | OHL | 0.0271 | 0.435 | 16.4876 | 2779 | 2568 | 2217 | 2568 | B-2-1c
CILF41 | SWAN41 | 61.595 | 0 | OHL | 0.0668 | 1.0713 | 40.6034 | 2779 | 2568 | 2217 | 2568 | B-2-1c
CILF41 | SWAN42 | 61.655 | 0 | OHL | 0.0669 | 1.0724 | 40.6428 | 3180 | 3000 | 2692 | 3000 | B-2-1c
CILF41 | WHSO4A | 35.208 | 0 | OHL | 0.0383 | 0.6151 | 23.1262 | 2779 | 2568 | 2217 | 2568 | B-2-1c
CLEH41 | KEMS4B | 13.5 | 0 | OHL | 0.021 | 0.259 | 8.1013 | 3102 | 3048 | 2853 | 3048 | B-2-1c
CONQ41 | DAIN41 | 60.331 | 0 | OHL | 0.094 | 1.1575 | 36.2038 | 3102 | 3048 | 2853 | 3048 | B-2-1c
CONQ41 | DAIN41 | 60.294 | 0 | OHL | 0.0938 | 1.1562 | 36.2009 | 3102 | 3048 | 2853 | 3048 | B-2-1c
CONQ41 | TREU4A | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2397 | 2302 | 2144 | 2302 | B-2-1c
CONQ41 | TREU4B | 14.323 | 0 | OHL | 0.0245 | 0.2802 | 8.4568 | 2212 | 2125 | 1979 | 2125 | B-2-1c
COSO41 | RAYL41 | 13.913 | 0 | OHL | 0.0217 | 0.2698 | 8.2601 | 2886 | 2835 | 2663 | 2835 | B-2-1c
COSO41 | TILB4B | 12.363 | 0 | OHL | 0.0193 | 0.24 | 7.3306 | 3075 | 2876 | 2663 | 2876 | B-2-1c
COTT41 | MARH4B | 100.853 | 0 | OHL | 0.1772 | 1.9852 | 59.1294 | 2009 | 1912 | 1746 | 1912 | B-2-1c
COTT41 | RYHA4A | 76.891 | 0 | OHL | 0.0682 | 1.3211 | 51.7563 | 3326 | 3326 | 3317 | 3326 | B-2-1c
COTT42 | RYHA4B | 76.816 | 0 | OHL | 0.0681 | 1.3196 | 51.7119 | 2807 | 2696 | 2511 | 2696 | B-2-1c
COTT42 | STAY41 | 27.698 | 0 | OHL | 0.0441 | 0.5297 | 16.7334 | 2212 | 2125 | 1979 | 2125 | B-2-1c
COVE21 | NECH21 | 30.715 | 0 | OHL | 0.0736 | 1.1961 | 9.1449 | 1204 | 1115 | 1018 | 1115 | B-2-1c
COWL41 | CULJ4A | 6.496 | 0 | OHL | 0.0085 | 0.1266 | 3.8528 | 2771 | 2568 | 2217 | 2568 | B-2-1c
COWL41 | DIDC41 | 11.503 | 0 | OHL | 0.0151 | 0.2242 | 6.8223 | 2779 | 2568 | 2217 | 2568 | B-2-1c
COWL41 | ECLA41 | 36.301 | 0 | OHL | 0.0322 | 0.6236 | 24.4394 | 3326 | 3326 | 3326 | 3326 | B-2-1c
COWL41 | LEIB4A | 52.495 | 0 | OHL | 0.0465 | 0.9017 | 35.3306 | 2779 | 2568 | 2217 | 2568 | B-2-1c
COWT2A | PYLE21 | 22.6 | 0 | OHL | 0.1334 | 0.9291 | 6.3441 | 932 | 879 | 790 | 879 | B-2-1c
CREB2A | HEDO21 | 20.347 | 0 | OHL | 0.0564 | 0.7587 | 6.312 | 1749 | 1664 | 1520 | 1664 | B-2-1c
CREB2B | SAEN21 | 20.347 | 0 | OHL | 0.0564 | 0.7587 | 6.312 | 1749 | 1664 | 1520 | 1664 | B-2-1c
CREB41 | GART4A | 32.081 | 0 | OHL | 0.0348 | 0.558 | 21.1475 | 3075 | 2876 | 2663 | 2876 | B-2-1c
CREB41 | GART4B | 32.109 | 0 | OHL | 0.0348 | 0.5585 | 21.1659 | 3326 | 3159 | 2971 | 3159 | B-2-1c
CULJ4A | DIDC41 | 4.898 | 0 | OHL | 0.0064 | 0.0955 | 2.905 | 2771 | 2568 | 2217 | 2568 | B-2-1c
DISS4A | YAXL41 | 0.05 | 0 | OHL | 0 | 0.0009 | 0.0336 | 3326 | 3326 | 3326 | 3326 | B-2-1c
DISS4B | NORM41 | 29.7 | 0 | OHL | 0.0263 | 0.5101 | 19.9633 | 3326 | 3326 | 3326 | 3326 | B-2-1c
DISS4B | YAXL41 | 0.05 | 0 | OHL | 0 | 0.0009 | 0.0336 | 3326 | 3326 | 3326 | 3326 | B-2-1c
DRAK41 | HAMH41 | 29.434 | 0 | OHL | 0.0534 | 0.5857 | 17.0575 | 2009 | 1911 | 1746 | 1911 | B-2-1c
DRAK41 | RATS41 | 32.907 | 0 | OHL | 0.0489 | 0.6238 | 20.201 | 2009 | 1911 | 1746 | 1911 | B-2-1c
DRAK41 | RUGE41 | 20.966 | 0 | OHL | 0.0379 | 0.4173 | 12.1495 | 2009 | 1911 | 1746 | 1911 | B-2-1c
DRAK41 | WILE41 | 16.937 | 0 | OHL | 0.0208 | 0.3015 | 11.0841 | 2009 | 1911 | 1746 | 1911 | B-2-1c
DRAX41 | FENW4A | 13.443 | 0 | OHL | 0.0146 | 0.2338 | 8.8618 | 3180 | 3000 | 2692 | 3000 | B-2-1c
DRAX41 | THTO43 | 22.579 | 0 | OHL | 0.0198 | 0.3877 | 15.2046 | 3075 | 2876 | 2663 | 2876 | B-2-1c
DRAX42 | EGGB41 | 11.188 | 0 | OHL | 0.0124 | 0.1983 | 7.2605 | 2973 | 2778 | 2447 | 2778 | B-2-1c
DRAX42 | THOM41 | 21.73 | 0 | OHL | 0.0311 | 0.3992 | 13.6444 | 2981 | 2867 | 2248 | 2505 | B-2-1c
DRAX42 | THTO41 | 22.579 | 0 | OHL | 0.0198 | 0.3877 | 15.2046 | 3075 | 2876 | 2663 | 2876 | B-2-1c
DUNG41 | NINF41 | 44.081 | 0 | OHL | 0.0391 | 0.7571 | 29.6278 | 3065 | 2829 | 2418 | 2829 | B-2-1c
DUNG41 | NINF41 | 44.056 | 0 | OHL | 0.0391 | 0.7567 | 29.6111 | 3066 | 2830 | 2418 | 2830 | B-2-1c
DUNG41 | SELL4E | 25.387 | 0 | OHL | 0.0395 | 0.4871 | 15.2346 | 3066 | 2830 | 2418 | 2830 | B-2-1c
DUNG41 | SELL4F | 25.403 | 0 | OHL | 0.0396 | 0.4874 | 15.2441 | 3066 | 2830 | 2418 | 2830 | B-2-1c
EASO4A | RYHA4B | 58.769 | 0 | OHL | 0.0521 | 1.0095 | 39.5649 | 2779 | 2569 | 2217 | 2569 | B-2-1c
EASO4B | RYHA4A | 58.95 | 0 | OHL | 0.0522 | 1.0126 | 39.6863 | 3326 | 3160 | 2971 | 3160 | B-2-1c
EASO4B | WYMO41 | 35.272 | 0 | OHL | 0.0313 | 0.6059 | 23.7466 | 2779 | 2568 | 2217 | 2568 | B-2-1c
ECLA41 | LEIB4B | 15.985 | 0 | OHL | 0.0141 | 0.2745 | 10.7511 | 2779 | 2568 | 2217 | 2568 | B-2-1c
ECLA41 | PAFB4A | 44.72 | 0 | OHL | 0.0814 | 0.8898 | 25.9172 | 2009 | 1911 | 1746 | 1911 | B-2-1c
ECLA41 | PAFB4B | 44.886 | 0 | OHL | 0.0817 | 0.8931 | 26.0131 | 2009 | 1911 | 1746 | 1911 | B-2-1c
EGGB42 | FERR4A | 11.864 | 0 | OHL | 0.0128 | 0.2063 | 7.8228 | 2779 | 2568 | 2217 | 2568 | B-2-1c
EGGB42 | STSB4B | 48.084 | 0 | OHL | 0.052 | 0.8361 | 31.7071 | 2779 | 2568 | 2217 | 2568 | B-2-1c
ELLA21 | FERR22 | 45.565 | 0 | OHL | 0.1573 | 1.8245 | 13.1474 | 1324 | 1260 | 1151 | 1260 | B-2-1c
ELLA21 | STAL21 | 39.6 | 0 | OHL | 0.1647 | 1.6624 | 10.8691 | 955 | 882 | 762 | 882 | B-2-1c
ENDE41 | PAFB4A | 41.13 | 0 | OHL | 0.0709 | 0.8051 | 24.2569 | 2009 | 1911 | 1746 | 1911 | B-2-1c
ENDE41 | PAFB4B | 41.13 | 0 | OHL | 0.0709 | 0.8051 | 24.2569 | 2009 | 1911 | 1746 | 1911 | B-2-1c
ENDE41 | RATS41 | 36.941 | 0 | OHL | 0.0399 | 0.5872 | 26.8034 | 2779 | 2568 | 2217 | 2568 | B-2-1c
ENDE41 | RATS41 | 36.873 | 0 | OHL | 0.0398 | 0.5862 | 26.7543 | 2779 | 2568 | 2217 | 2568 | B-2-1c
EXET41 | TAUN41 | 38.147 | 0 | OHL | 0.0694 | 0.759 | 22.1074 | 2009 | 1911 | 1746 | 1911 | B-2-1c
EXET41 | TAUN42 | 38.107 | 0 | OHL | 0.0693 | 0.7582 | 22.0842 | 2009 | 1911 | 1746 | 1911 | B-2-1c
FAWL41 | MANN41 | 61.115 | 0 | OHL | 0.066 | 1.0014 | 43.0253 | 2779 | 2568 | 2217 | 2568 | B-2-1c
FAWL41 | MAWO41 | 18.639 | 0 | OHL | 0.0214 | 0.3062 | 13.1667 | 2423 | 2327 | 2167 | 2327 | B-2-1c
FECK41 | HAMH41 | 43.314 | 0 | OHL | 0.078 | 0.8621 | 25.1018 | 2009 | 1911 | 1746 | 1911 | B-2-1c
FECK41 | IRON41 | 66.123 | 0 | OHL | 0.123 | 1.3148 | 38.3377 | 2009 | 1911 | 1746 | 1911 | B-2-1c
FENW4A | KEAD42 | 42.517 | 0 | OHL | 0.0198 | 0.2161 | 24.6399 | 3075 | 2876 | 2663 | 2876 | B-2-1c
FENW4A | THOM42 | 8.287 | 0 | OHL | 0.0165 | 0.1653 | 4.7826 | 2009 | 1911 | 1746 | 1911 | B-2-1c
FERR21 | MONF21 | 4.485 | 0 | OHL | 0.0103 | 0.1651 | 1.3966 | 1372 | 1307 | 1207 | 1307 | B-2-1c
FERR23 | FERR2A | 0.586 | 0 | OHL | 0.0013 | 0.0216 | 0.1825 | 1381 | 1307 | 1227 | 1307 | B-2-1c
FERR2A | MONF22 | 3.922 | 0 | OHL | 0.009 | 0.1444 | 1.2212 | 1204 | 1115 | 1018 | 1115 | B-2-1c
FFES21 | TRAW21 | 7.358 | 0 | OHL | 0.0772 | 0.3075 | 2.0153 | 551 | 512 | 442 | 512 | B-2-1c
FIDF21 | FROD21 | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1316 | 1213 | 1104 | 1213 | B-2-1c
FIDF21 | FROD22 | 9.145 | 0 | OHL | 0.021 | 0.3366 | 2.8484 | 1316 | 1213 | 1104 | 1213 | B-2-1c
FIDF21 | RAIN21 | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1316 | 1213 | 1104 | 1213 | B-2-1c
FIDF21 | RAIN21 | 7.963 | 0 | OHL | 0.0183 | 0.2678 | 2.7299 | 1316 | 1213 | 1104 | 1213 | B-2-1c
FLEE41 | LOVE41 | 41.095 | 0 | OHL | 0.064 | 0.7885 | 24.661 | 3140 | 3086 | 2999 | 3086 | B-2-1c
FLEE41 | LOVE41 | 41.095 | 0 | OHL | 0.064 | 0.7885 | 24.661 | 3140 | 3086 | 2999 | 3086 | B-2-1c
FOUR21 | HARK24 | 55.711 | 0 | OHL | 0.3289 | 2.3608 | 15.2112 | 854 | 795 | 700 | 795 | B-2-1c
FOUR21 | STEW21 | 27.731 | 0 | OHL | 0.1637 | 1.1751 | 7.5717 | 854 | 795 | 700 | 795 | B-2-1c
FRIS4A | SIZE41 | 7.61 | 0 | OHL | 0.0083 | 0.1324 | 5.0166 | 2779 | 2568 | 2217 | 2568 | B-2-1c
FRIS4B | SIZE41 | 7.61 | 0 | OHL | 0.0083 | 0.1324 | 5.0166 | 2779 | 2568 | 2217 | 2568 | B-2-1c
FRIS4C | LEIS4A | 6.8 | 0 | OHL | 0.0074 | 0.1183 | 4.4826 | 2779 | 2569 | 2217 | 2569 | B-2-1c
FRIS4D | SIZE41 | 7.61 | 0 | OHL | 0.0083 | 0.1324 | 5.0166 | 2779 | 2568 | 2217 | 2568 | B-2-1c
FROD41 | ROCK41 | 1.197 | 0 | OHL | 0.0022 | 0.0238 | 0.6917 | 1100 | 1100 | 1100 | 1100 | B-2-1c
GART4A | HUMR41 | 37.372 | 0 | OHL | 0.0413 | 0.7015 | 23.0779 | 3156 | 3032 | 2823 | 3032 | B-2-1c
GART4A | KEAD43 | 5.711 | 0 | OHL | 0.0062 | 0.0993 | 3.7642 | 3075 | 2876 | 2663 | 2876 | B-2-1c
GART4B | KILL41 | 34.462 | 0 | OHL | 0.038 | 0.6467 | 21.2883 | 3156 | 3032 | 2823 | 3032 | B-2-1c
GRAI41 | MEDW41 | 2.5 | 0 | OHL | 0.0054 | 0.0513 | 1.3945 | 1390 | 1390 | 1390 | 1390 | B-2-1c
GREN41 | MARH4A | 28.74 | 0 | OHL | 0.0522 | 0.5717 | 16.6594 | 2514 | 2439 | 2314 | 2439 | B-2-1c
GREN41 | MARH4B | 28.56 | 0 | OHL | 0.052 | 0.5682 | 16.5517 | 2009 | 1912 | 1746 | 1912 | B-2-1c
GRIW41 | KEAD41 | 49.379 | 0 | OHL | 0.047 | 0.873 | 32.3362 | 3075 | 2876 | 2663 | 2876 | B-2-1c
GRIW41 | SHBA41 | 12.673 | 0 | OHL | 0.0127 | 0.2284 | 8.1498 | 2860 | 2720 | 2484 | 2720 | B-2-1c
HAMB4A | HEYS41 | 25.85 | 0 | OHL | 0.0229 | 0.444 | 17.3733 | 3326 | 3299 | 3098 | 3299 | B-2-1c
HAMB4B | HEYS41 | 26.02 | 0 | OHL | 0.0231 | 0.4469 | 17.4871 | 3326 | 3326 | 3152 | 3326 | B-2-1c
HAMH2A | NECH21 | 10.439 | 0 | OHL | 0.0263 | 0.4067 | 3.0955 | 1362 | 1285 | 1202 | 1285 | B-2-1c
HARM21 | HATL21 | 13.983 | 0 | OHL | 0.0472 | 0.5702 | 3.9648 | 1093 | 1031 | 925 | 1031 | B-2-1c
HARM21 | HAWP21 | 17.287 | 0 | OHL | 0.0584 | 0.7033 | 4.9126 | 1204 | 1115 | 1018 | 1115 | B-2-1c
HATL21 | HAWP2A | 31.443 | 0 | OHL | 0.1066 | 1.2811 | 8.9228 | 1093 | 1031 | 926 | 1031 | B-2-1c
HATL21 | SALH21 | 7.794 | 0 | OHL | 0.0327 | 0.3353 | 2.0878 | 1381 | 1279 | 1157 | 1279 | B-2-1c
HATL21 | TODP21 | 18.433 | 0 | OHL | 0.0713 | 0.7756 | 5.0465 | 1381 | 1279 | 1157 | 1279 | B-2-1c
HAWP21 | OFFE21 | 9.514 | 0 | OHL | 0.0379 | 0.3948 | 2.6412 | 1093 | 1031 | 925 | 1031 | B-2-1c
HAWP2A | WBOL21 | 17.721 | 0 | OHL | 0.0705 | 0.7355 | 4.9196 | 1176 | 1119 | 1024 | 1119 | B-2-1c
HEDO21 | SAES21 | 0.605 | 0 | OHL | 0.0017 | 0.0226 | 0.1876 | 1749 | 1664 | 1520 | 1664 | B-2-1c
HEYS41 | MIDL41 | 0.9 | 0 | OHL | 0.0008 | 0.0155 | 0.6049 | 3326 | 3160 | 2971 | 3160 | B-2-1c
HEYS41 | QUER4B | 9.604 | 0 | OHL | 0.0085 | 0.165 | 6.4553 | 3326 | 3299 | 3098 | 3299 | B-2-1c
HINP41 | SHUR41 | 1.2 | 0 | OHL | 0.0019 | 0.0235 | 0.7057 | 3103 | 3048 | 2959 | 3048 | B-2-1c
HINP41 | SHUR41 | 1.213 | 0 | OHL | 0.002 | 0.024 | 0.707 | 3103 | 3048 | 2959 | 3048 | B-2-1c
HUMR41 | KILL41 | 2.879 | 0 | OHL | 0.0032 | 0.0543 | 1.7706 | 2771 | 2771 | 2771 | 2771 | B-2-1c
HUTT41 | QUER4A | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3102 | 3048 | 2958 | 3048 | B-2-1c
HUTT41 | QUER4B | 34.42 | 0 | OHL | 0.0536 | 0.6617 | 20.6138 | 3102 | 3048 | 2958 | 3048 | B-2-1c
INDQ41 | LAND41 | 49.565 | 0 | OHL | 0.107 | 0.9921 | 28.4764 | 2199 | 2092 | 1911 | 2092 | B-2-1c
INDQ41 | LAND42 | 49.565 | 0 | OHL | 0.107 | 0.9921 | 28.4764 | 1389 | 1284 | 1108 | 1284 | B-2-1c
IROA11 | OLDS12 | 1 | 0 | OHL | 0.298 | 2.366 | 3.453 | 452 | 423 | 365 | 372 | B-2-1c
IROA12 | OLDS12 | 1 | 0 | OHL | 0.297 | 2.361 | 2.693 | 457 | 424 | 366 | 372 | B-2-1c
IROA21 | WHSO2A | 34.621 | 0 | OHL | 0.2033 | 1.4667 | 9.4554 | 750 | 750 | 715 | 750 | B-2-1c
IROA21 | WHSO2B | 34.555 | 0 | OHL | 0.2034 | 1.4638 | 9.4375 | 750 | 750 | 715 | 750 | B-2-1c
IRON41 | LEGA4B | 62.073 | 0 | OHL | 0.0991 | 1.1937 | 37.3273 | 2002 | 2002 | 2002 | 2002 | B-2-1c
IRON41 | PENN4A | 27.761 | 0 | OHL | 0.0574 | 0.5549 | 15.9851 | 1389 | 1284 | 1108 | 1284 | B-2-1c
IRON41 | PENN4B | 24.617 | 0 | OHL | 0.0488 | 0.491 | 14.2132 | 1590 | 1500 | 1346 | 1500 | B-2-1c
IRON41 | RUGE41 | 58.681 | 0 | OHL | 0.1135 | 1.1701 | 33.9045 | 1389 | 1284 | 1108 | 1284 | B-2-1c
IRON41 | SHRE4A | 15.129 | 0 | OHL | 0.0242 | 0.2909 | 9.0977 | 2397 | 2302 | 2144 | 2302 | B-2-1c
KEAD42 | WBUR42 | 28.425 | 0 | OHL | 0.0252 | 0.4882 | 19.1053 | 3326 | 3249 | 3098 | 3249 | B-2-1c
KEAD43 | KILL41 | 41.067 | 0 | OHL | 0.0403 | 0.7345 | 26.6033 | 3060 | 2931 | 2715 | 2931 | B-2-1c
KEAD44 | WBUR41 | 28.266 | 0 | OHL | 0.0251 | 0.4855 | 18.9976 | 3326 | 3249 | 3098 | 3249 | B-2-1c
KEAR41 | PADI41 | 39.101 | 0 | OHL | 0.0567 | 0.7296 | 24.2055 | 2169 | 2084 | 1940 | 2084 | B-2-1c
KEMS41 | LOFI4A | 38.035 | 0 | OHL | 0.0623 | 0.726 | 23.0007 | 3102 | 2935 | 2765 | 2935 | B-2-1c
KEMS41 | LOFI4B | 37.572 | 0 | OHL | 0.0617 | 0.7176 | 22.7061 | 3102 | 2935 | 2765 | 2935 | B-2-1c
KIBY21 | RAIN21 | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1416 | 1339 | 1258 | 1339 | B-2-1c
KIBY21 | RAIN21 | 11.236 | 0 | OHL | 0.0258 | 0.3778 | 3.8519 | 1416 | 1339 | 1258 | 1339 | B-2-1c
KIBY21 | WASF2A | 10.945 | 0 | OHL | 0.0414 | 0.4478 | 3.0891 | 1521 | 1461 | 1360 | 1461 | B-2-1c
KIBY21 | WASF2B | 10.978 | 0 | OHL | 0.0415 | 0.4491 | 3.0984 | 1521 | 1461 | 1360 | 1461 | B-2-1c
KILL41 | SHBA41 | 17.05 | 0 | OHL | 0.0179 | 0.3134 | 10.7556 | 2860 | 2720 | 2484 | 2720 | B-2-1c
KINO41 | NFLE41 | 23.626 | 0 | OHL | 0.0284 | 0.4216 | 15.2234 | 3102 | 2935 | 2692 | 2935 | B-2-1c
KINO41 | SING41 | 17.685 | 0 | OHL | 0.0192 | 0.3076 | 11.6582 | 2889 | 2748 | 2510 | 2748 | B-2-1c
LACK21 | TODP21 | 5.965 | 0 | OHL | 0.0212 | 0.2477 | 1.654 | 1408 | 1332 | 1251 | 1332 | B-2-1c
LAGA41 | LAND41 | 21.224 | 0 | OHL | 0.0339 | 0.4081 | 12.7621 | 2423 | 2327 | 2168 | 2327 | B-2-1c
LAGA41 | LAND42 | 21.355 | 0 | OHL | 0.0341 | 0.4108 | 12.8369 | 2423 | 2327 | 2168 | 2327 | B-2-1c
LALE21 | WWEY2A | 8.395 | 0 | OHL | 0.0317 | 0.3434 | 2.3695 | 1316 | 1213 | 1104 | 1213 | B-2-1c
LEGA41 | TREU4A | 12.119 | 0 | OHL | 0.0135 | 0.2316 | 7.3388 | 2860 | 2720 | 2484 | 2720 | B-2-1c
LEGA41 | TREU4B | 12.119 | 0 | OHL | 0.0135 | 0.2316 | 7.3388 | 2860 | 2720 | 2484 | 2720 | B-2-1c
LEGA4A | SHRE4A | 46.944 | 0 | OHL | 0.075 | 0.9028 | 28.2295 | 2002 | 2002 | 2002 | 2002 | B-2-1c
LEIB4A | SUND42 | 13.455 | 0 | OHL | 0.0119 | 0.2311 | 9.0472 | 2779 | 2568 | 2217 | 2568 | B-2-1c
LEIB4B | SUND41 | 13.455 | 0 | OHL | 0.0119 | 0.2311 | 9.0472 | 2779 | 2568 | 2217 | 2568 | B-2-1c
LEIS4A | SIZE41 | 0.81 | 0 | OHL | 0.0009 | 0.0141 | 0.534 | 2779 | 2569 | 2217 | 2569 | B-2-1c
LITT41 | LOFI4A | 8.152 | 0 | OHL | 0.0127 | 0.157 | 4.8712 | 3103 | 3048 | 2959 | 3048 | B-2-1c
LITT41 | LOFI4B | 8.152 | 0 | OHL | 0.0127 | 0.157 | 4.8712 | 3103 | 3048 | 2959 | 3048 | B-2-1c
LOFI4A | ROWD41 | 26.714 | 0 | OHL | 0.0576 | 0.5347 | 15.3479 | 1590 | 1500 | 1346 | 1500 | B-2-1c
LOFI4B | ROWD42 | 26.714 | 0 | OHL | 0.0576 | 0.5347 | 15.3479 | 1590 | 1500 | 1346 | 1500 | B-2-1c
LOVE41 | NURS41 | 36.477 | 0 | OHL | 0.0396 | 0.6344 | 24.0461 | 2771 | 2568 | 2217 | 2568 | B-2-1c
LOVE41 | NURS4A | 36.477 | 0 | OHL | 0.0396 | 0.6344 | 24.0461 | 2779 | 2568 | 2217 | 2568 | B-2-1c
MACC41 | STAL4B | 31.196 | 0 | OHL | 0.062 | 0.617 | 18.1761 | 1710 | 1627 | 1488 | 1627 | B-2-1c
MAGA21 | PYLE21 | 6.238 | 0 | OHL | 0.0211 | 0.2537 | 1.7667 | 1204 | 1115 | 1018 | 1115 | B-2-1c
MANN41 | NURS4A | 39.823 | 0 | OHL | 0.043 | 0.6631 | 27.5672 | 2779 | 2568 | 2217 | 2568 | B-2-1c
MARH4A | STAY41 | 73.027 | 0 | OHL | 0.1328 | 1.4529 | 42.3252 | 2514 | 2439 | 2314 | 2439 | B-2-1c
MARV41 | MARV4A | 0.145 | 0 | OHL | 0.0003 | 0.0029 | 0.0839 | 2009 | 2009 | 2009 | 2009 | B-2-1c
MARV41 | MARV4B | 0.077 | 0 | OHL | 0.0001 | 0.0015 | 0.0446 | 2009 | 2009 | 2009 | 2009 | B-2-1c
MAWO41 | NURS41 | 7.441 | 0 | OHL | 0.0093 | 0.1281 | 5.0417 | 2423 | 2327 | 2167 | 2327 | B-2-1c
MEDB4A | STEW41 | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3326 | 3326 | 3326 | 3326 | B-2-1c
MEDB4A | STWB4R | 87.852 | 0 | OHL | 0.0779 | 1.5089 | 59.0491 | 3326 | 3326 | 3326 | 3326 | B-2-1c
MEDB4B | STEW41 | 7 | 0 | OHL | 0.0062 | 0.1202 | 4.705 | 3326 | 3326 | 3326 | 3326 | B-2-1c
MEDB4B | STWB4Q | 87.852 | 0 | OHL | 0.0779 | 1.5089 | 59.0491 | 3326 | 3326 | 3326 | 3326 | B-2-1c
MELK41 | MITY41 | 28.101 | 0 | OHL | 0.0511 | 0.5591 | 16.2853 | 2105 | 2016 | 1867 | 2016 | B-2-1c
MELK41 | MITY41 | 28.052 | 0 | OHL | 0.051 | 0.5581 | 16.257 | 2105 | 2016 | 1867 | 2016 | B-2-1c
MELK41 | SEAB41 | 53.558 | 0 | OHL | 0.0598 | 0.9451 | 34.8897 | 2545 | 2421 | 2211 | 2421 | B-2-1c
MIDL41 | QUER4A | 9.704 | 0 | OHL | 0.0086 | 0.1667 | 6.5225 | 3326 | 3159 | 2971 | 3159 | B-2-1c
MONF41 | PADI41 | 87.848 | 0 | OHL | 0.1064 | 1.6286 | 54.7416 | 2518 | 2395 | 2188 | 2395 | B-2-1c
NEEP4A | STSB4B | 12.801 | 0 | OHL | 0.0276 | 0.2627 | 7.1402 | 2779 | 2568 | 2217 | 2568 | B-2-1c
NFLE41 | SING41 | 5.941 | 0 | OHL | 0.0093 | 0.114 | 3.5652 | 2889 | 2748 | 2510 | 2748 | B-2-1c
NFLE41 | WTHU4A | 7.511 | 0 | OHL | 0.0137 | 0.1494 | 4.3529 | 2004 | 1907 | 1746 | 1907 | B-2-1c
NFLE41 | WTHU4B | 7.511 | 0 | OHL | 0.0137 | 0.1494 | 4.3529 | 2004 | 1907 | 1746 | 1907 | B-2-1c
NORT21 | SALH21 | 12.178 | 0 | OHL | 0.0464 | 0.526 | 3.2482 | 1381 | 1293 | 1197 | 1293 | B-2-1c
NORT41 | SALH42 | 12.206 | 0 | OHL | 0.022 | 0.2492 | 6.888 | 1831 | 1739 | 1588 | 1739 | B-2-1c
OCKH21 | OLDB2A | 5.46 | 0 | OHL | 0.0208 | 0.2294 | 1.4988 | 772 | 772 | 619 | 619 | B-2-1c
OCKH2A | WIEN2B | 4.67 | 0 | OHL | 0.0213 | 0.1977 | 1.2665 | 760 | 760 | 760 | 760 | B-2-1c
OFFE21 | WBOL21 | 8.207 | 0 | OHL | 0.0327 | 0.3406 | 2.2784 | 1176 | 1115 | 1018 | 1115 | B-2-1c
PADI41 | PEWO4B | 37.608 | 0 | OHL | 0.0556 | 0.7049 | 23.1779 | 2169 | 2084 | 1940 | 2084 | B-2-1c
PEMB41 | SWAN42 | 84.57 | 0 | OHL | 0.0918 | 1.4709 | 55.7496 | 2779 | 2568 | 2217 | 2568 | B-2-1c
PENT41 | WYLF41 | 35.24 | 0 | OHL | 0.0382 | 0.6129 | 23.2307 | 2779 | 2568 | 2217 | 2568 | B-2-1c
PEWO2C | WASF2A | 23.481 | 0 | OHL | 0.0887 | 0.9606 | 6.6274 | 1521 | 1461 | 1360 | 1461 | B-2-1c
PEWO2D | WASF2B | 23.521 | 0 | OHL | 0.0889 | 0.9623 | 6.6386 | 1521 | 1461 | 1360 | 1461 | B-2-1c
PEWO41 | QUER4A | 31.939 | 0 | OHL | 0.0498 | 0.6128 | 19.1665 | 3102 | 3048 | 2853 | 3048 | B-2-1c
PEWO41 | QUER4B | 32.087 | 0 | OHL | 0.05 | 0.6156 | 19.2551 | 3102 | 3048 | 2853 | 3048 | B-2-1c
RATS41 | WILE41 | 21.684 | 0 | OHL | 0.0394 | 0.4314 | 12.5666 | 2009 | 1911 | 1746 | 1911 | B-2-1c
RAYL41 | TILB4A | 20.499 | 0 | OHL | 0.0319 | 0.3933 | 12.3014 | 3102 | 2935 | 2765 | 2935 | B-2-1c
RHIG41 | SWAN41 | 34.34 | 0 | OHL | 0.0373 | 0.5973 | 22.6374 | 2779 | 2568 | 2217 | 2568 | B-2-1c
ROCH21 | STAL21 | 31.256 | 0 | OHL | 0.1235 | 1.3183 | 8.54 | 1324 | 1260 | 1151 | 1260 | B-2-1c
RYEH4A | RYEH43 | 0.264 | 0 | OHL | 0.0004 | 0.0051 | 0.1585 | 2779 | 2569 | 2217 | 2569 | B-2-1c
RYEH4B | RYEH42 | 0.215 | 0 | OHL | 0.0003 | 0.0041 | 0.1291 | 2779 | 2569 | 2217 | 2569 | B-2-1c
SAEN21 | SAES21 | 0.484 | 0 | OHL | 0.0013 | 0.018 | 0.1501 | 1749 | 1664 | 1520 | 1664 | B-2-1c
SAFO41 | SEAB41 | 31.28 | 0 | OHL | 0.0345 | 0.5479 | 20.4859 | 3190 | 3060 | 2850 | 3060 | B-2-1c
SELL4B | SELL4C | 0.257 | 0 | OHL | 0.0004 | 0.0049 | 0.1542 | 3326 | 3159 | 2971 | 3159 | B-2-1c
SELL4B | SELL4D | 0.257 | 0 | OHL | 0.0004 | 0.0049 | 0.1542 | 3326 | 3326 | 3326 | 3326 | B-2-1c
SELL4B | SELL4E | 0.39 | 0 | OHL | 0.0006 | 0.0075 | 0.234 | 3326 | 3159 | 2971 | 3159 | B-2-1c
SELL4B | SELL4F | 0.39 | 0 | OHL | 0.0006 | 0.0075 | 0.234 | 3326 | 3159 | 2971 | 3159 | B-2-1c
SHRE4A | SHRE4B | 0.054 | 0 | OHL | 0.0001 | 0.001 | 0.0324 | 240 | 240 | 240 | 240 | B-2-1c
SHUR41 | TAUN41 | 27 | 0 | OHL | 0.0487 | 0.5369 | 15.6574 | 2213 | 2126 | 1980 | 2126 | B-2-1c
SHUR41 | TAUN42 | 27 | 0 | OHL | 0.0487 | 0.5369 | 15.6574 | 2213 | 2126 | 1980 | 2126 | B-2-1c
SPLN41 | WALP41 | 29.234 | 0 | OHL | 0.0272 | 0.5117 | 19.3195 | 3189 | 3063 | 2853 | 3063 | B-2-1c
SSHI22 | TYNE2A | 7.028 | 0 | OHL | 0.031 | 0.2985 | 1.9072 | 1247 | 1180 | 1065 | 1180 | B-2-1c
SSHI22 | WBOL21 | 4.366 | 0 | OHL | 0.02 | 0.1848 | 1.1845 | 1176 | 1119 | 1024 | 1119 | B-2-1c
STEN11 | STES11 | 1 | 0 | OHL | 0.0266 | 0.1193 | 0.1077 | 198 | 198 | 181 | 181 | B-2-1c
SWAN41 | SWAN4B | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 3048 | 3048 | 2971 | 3048 | B-2-1c
SWAN42 | SWAN4A | 0.64 | 0 | OHL | 0.0014 | 0.0128 | 0.3677 | 1389 | 1284 | 1108 | 1284 | B-2-1c
THUR21 | THUR2A | 4.653 | 0 | OHL | 0.0488 | 0.1944 | 1.2745 | 551 | 512 | 442 | 512 | B-2-1c
THUR2A | WMEL21 | 16.348 | 0 | OHL | 0.0746 | 0.7099 | 4.3235 | 955 | 882 | 762 | 882 | B-2-1c
TILB21 | WARL21 | 13.065 | 0 | OHL | 0.0597 | 0.553 | 3.5441 | 1175 | 1119 | 1023 | 1119 | B-2-1c
TILB21 | WARL21 | 12.897 | 0 | OHL | 0.059 | 0.5459 | 3.4987 | 1175 | 1119 | 1023 | 1119 | B-2-1c
TILB41 | TILB4A | 0.058 | 0 | OHL | 0.0001 | 0.0012 | 0.033 | 3102 | 3048 | 2958 | 3048 | B-2-1c
TILB41 | TILB4B | 0.059 | 0 | OHL | 0.0001 | 0.0011 | 0.0353 | 3102 | 3048 | 2853 | 3048 | B-2-1c
TREM21 | USKM2A | 15.048 | 0 | OHL | 0.0854 | 0.7095 | 3.7487 | 695 | 641 | 548 | 641 | B-2-1c
TYNE21 | WBOL21 | 11.399 | 0 | OHL | 0.051 | 0.4835 | 3.093 | 1131 | 1052 | 912 | 1052 | B-2-1c
USKM21 | USKM2A | 0.692 | 0 | OHL | 0.0038 | 0.036 | 0.1546 | 695 | 642 | 548 | 642 | B-2-1c
USKM21 | USKM2B | 0.391 | 0 | OHL | 0.0039 | 0.0167 | 0.1052 | 682 | 629 | 538 | 629 | B-2-1c
USKM21 | WHSO21 | 5.841 | 0 | OHL | 0.0345 | 0.2401 | 1.6394 | 1005 | 956 | 874 | 956 | B-2-1c
USKM21 | WHSO22 | 5.849 | 0 | OHL | 0.0345 | 0.2405 | 1.6417 | 1005 | 956 | 873 | 956 | B-2-1c
USKM2A | WHSO21 | 5.562 | 0 | OHL | 0.0306 | 0.289 | 1.2455 | 695 | 641 | 548 | 641 | B-2-1c
USKM2B | WHSO22 | 5.851 | 0 | OHL | 0.0322 | 0.304 | 1.3103 | 682 | 629 | 538 | 629 | B-2-1c
WHSO41 | WHSO4A | 0.077 | 0 | OHL | 0.0001 | 0.0013 | 0.0506 | 992 | 916 | 783 | 916 | B-2-1c
CHAR1S | GLAG1S | 1.4 | 0 | OHL | 0.1274 | 0.3262 | 0.07 | 126 | 117 | 101 | 117 | B-2-2a | 2025 | Addition
CHAR1T | GLAG1T | 1.4 | 0 | OHL | 0.1274 | 0.3262 | 0.07 | 126 | 117 | 101 | 117 | B-2-2a | 2025 | Addition
GREM1L | GREM1P | 2.3 | 0 | OHL | 0.115 | 0.4761 | 0.129 | 241 | 230 | 210 | 230 | B-2-2a | 2025 | Addition
GREM1M | KERG1M | 0 | 11.1 | OHL | 0.555 | 2.2977 | 0.622 | 203 | 193 | 176 | 193 | B-2-2a | 2025 | Addition
GREM1Q | KERG1L | 0 | 7.94 | OHL | 0.397 | 1.6436 | 0.445 | 241 | 230 | 210 | 230 | B-2-2a | 2025 | Addition
INRU1Q | PEHE1- | 6.7 | 0 | OHL | 0.3417 | 1.5008 | 0.348 | 241 | 230 | 210 | 230 | B-2-2a | 2025 | Change
INRU1R | PEHE1- | 6.7 | 0 | OHL | 0.3417 | 1.5008 | 0.348 | 241 | 230 | 210 | 230 | B-2-2a | 2025 | Change
LIMK1- | LIMK1A | 4.9 | 0 | OHL | 0.245 | 1.014 | 0.652 | 203 | 193 | 176 | 193 | B-2-2a | 2025 | Addition
ABED1- | DUNM1T | 5 | 0 | OHL | 0.25 | 1.035 | 0.28 | 163 | 152 | 131 | 152 | B-2-2a | 2027 | Addition
ACHE1- | SHIN1- | 17.5 | 0 | OHL | 0.875 | 3.6225 | 0.98 | 203 | 193 | 176 | 193 | B-2-2a | 2027 | Addition
AIGN1A | KION1A | 2.92 | 0 | OHL | 0.264 | 0.594 | 0.66 | 111 | 103 | 89 | 103 | B-2-2a | 2027 | Addition
ALYT4J | FETT4R | 67.06 | 0 | OHL | 0.1341 | 1.2799 | 41.079 | 2000 | 1920 | 1790 | 1920 | B-2-2a | 2027 | Addition
ALYT4J | KINB4J | 69.22 | 0 | OHL | 0.1384 | 1.311 | 42.688 | 2000 | 1920 | 1790 | 1920 | B-2-2a | 2027 | Addition
ALYT4K | FETT4Q | 67.06 | 0 | OHL | 0.1341 | 1.2799 | 41.079 | 2000 | 1920 | 1790 | 1920 | B-2-2a | 2027 | Addition
ALYT4K | KINB4K | 69.22 | 0 | OHL | 0.1384 | 1.311 | 42.688 | 2000 | 1920 | 1790 | 1920 | B-2-2a | 2027 | Addition
BAGP2- | BAGP2J | 0.25 | 0 | OHL | 0.01 | 0.0138 | 0.053 | 965 | 925 | 865 | 925 | B-2-2a | 2027 | Addition
BAGP2- | BAGP2K | 0.25 | 0 | OHL | 0.01 | 0.0138 | 0.053 | 965 | 925 | 865 | 925 | B-2-2a | 2027 | Addition
BEAU1J | KION1B | 1.5 | 0 | OHL | 0.0295 | 0.0433 | 1.175 | 251 | 252 | 252 | 252 | B-2-2a | 2027 | Addition
BEAU1K | KION1A | 1.5 | 0 | OHL | 0.0295 | 0.0433 | 1.175 | 251 | 252 | 252 | 252 | B-2-2a | 2027 | Addition
BEAU2J | FYRI2J | 30.5 | 0 | OHL | 0.183 | 1.6772 | 6.465 | 702 | 665 | 599 | 665 | B-2-2a | 2027 | Change
BEAU2K | FYRI2K | 30.5 | 0 | OHL | 0.183 | 1.6772 | 6.465 | 702 | 665 | 599 | 665 | B-2-2a | 2027 | Change
BERB2Q | CAID2- | 7.99 | 0 | OHL | 0.0452 | 0.3288 | 2.178 | 935 | 880 | 790 | 880 | B-2-2a | 2027 | Addition
BLEX1A | BLEX1B | 14.4 | 0 | OHL | 0.7191 | 3.2528 | 0.79 | 203 | 193 | 176 | 193 | B-2-2a | 2027 | Addition
BLHI1J | ELCH1- | 24 | 0 | OHL | 1.209 | 4.97 | 1.344 | 203 | 193 | 176 | 193 | B-2-2a | 2027 | Addition
CAID2- | KNOC2J | 0 | 38.99 | OHL | 0.2208 | 1.6052 | 10.631 | 935 | 880 | 790 | 880 | B-2-2a | 2027 | Addition
CLGO2- | KNOC2K | 0 | 47.45 | OHL | 0.2687 | 1.9535 | 12.938 | 935 | 880 | 790 | 880 | B-2-2a | 2027 | Addition
CONN2J | DOUN2- | 10.34 | 0 | OHL | 0.0621 | 0.5689 | 2.193 | 780 | 750 | 700 | 750 | B-2-2a | 2027 | Change
CONN2K | DOUN2- | 10.34 | 0 | OHL | 0.0621 | 0.5689 | 2.193 | 780 | 750 | 700 | 750 | B-2-2a | 2027 | Change
CONN2K | GORW2- | 47.76 | 0 | OHL | 0.2866 | 2.6272 | 10.127 | 780 | 750 | 700 | 750 | B-2-2a | 2027 | Change
CULL1Q | DEAW1A | 9 | 0 | OHL | 0.93 | 2.12 | 0.45 | 111 | 103 | 89 | 103 | B-2-2a | 2027 | Addition
CULL1Q | KION1B | 12.6 | 0 | OHL | 1.287 | 2.952 | 0.621 | 111 | 103 | 89 | 103 | B-2-2a | 2027 | Addition
DELL1A | DELL1B | 7.2 | 0 | OHL | 0.2304 | 1.5696 | 0.382 | 280 | 270 | 245 | 270 | B-2-2a | 2027 | Addition
DLCH1B | LAIS1A | 3.7 | 0 | OHL | 0.0869 | 0.8073 | 0.195 | 464 | 446 | 414 | 446 | B-2-2a | 2027 | Addition
DOUN2- | BAGP2J | 5 | 0 | OHL | 0.025 | 0.275 | 1.065 | 965 | 925 | 865 | 925 | B-2-2a | 2027 | Addition
DUNO1Q | WHTB1S | 18.1 | 0 | OHL | 0.9231 | 4.1087 | 0.923 | 241 | 230 | 210 | 230 | B-2-2a | 2027 | Change
DUNO1R | WHTB1T | 18.1 | 0 | OHL | 0.9231 | 4.1087 | 0.923 | 241 | 230 | 210 | 230 | B-2-2a | 2027 | Change
FYRI2J | LOCB2K | 35.93 | 0 | OHL | 0.2156 | 1.9762 | 7.617 | 780 | 750 | 700 | 750 | B-2-2a | 2027 | Change
FYRI2K | LOCB2J | 35.93 | 0 | OHL | 0.2156 | 1.9762 | 7.617 | 780 | 750 | 700 | 750 | B-2-2a | 2027 | Change
GILB1L | THUS1L | 13.1 | 0 | OHL | 0.303 | 2.776 | 0.72 | 463 | 444 | 415 | 444 | B-2-2a | 2027 | Addition
GILB1M | THUS1M | 13.1 | 0 | OHL | 0.303 | 2.776 | 0.72 | 463 | 444 | 415 | 444 | B-2-2a | 2027 | Addition
GORW2- | STRB2- | 10.3 | 0 | OHL | 0.0618 | 0.5665 | 2.184 | 780 | 750 | 700 | 750 | B-2-2a | 2027 | Change
KINT4J | FETT4Q | 32.19 | 0 | OHL | 0.0644 | 0.6052 | 19.977 | 2000 | 1920 | 1790 | 1920 | B-2-2a | 2027 | Addition
KINT4K | FETT4R | 32.19 | 0 | OHL | 0.0644 | 0.6052 | 19.977 | 2000 | 1920 | 1790 | 1920 | B-2-2a | 2027 | Addition
LAIS1A | LAIS1B | 1.6 | 0 | OHL | 0.1456 | 0.3456 | 0.0864 | 111 | 103 | 89 | 103 | B-2-2a | 2027 | Addition
LAIS1A | LOCB1M | 13.3 | 0 | OHL | 0.3123 | 2.9012 | 0.703 | 464 | 446 | 414 | 446 | B-2-2a | 2027 | Addition
LOCB2K | STRB2- | 18.9 | 0 | OHL | 0.1134 | 1.0395 | 4.007 | 780 | 750 | 700 | 750 | B-2-2a | 2027 | Change
THUS2J | BAGP2K | 10.4 | 0 | OHL | 0.052 | 0.572 | 2.215 | 965 | 925 | 865 | 925 | B-2-2a | 2027 | Addition
ANSN2- | CRDH2J | 20.25 | 0 | OHL | 0.081 | 0.8303 | 5.711 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
ANSN2- | CRMU2J | 24.95 | 0 | OHL | 0.0998 | 1.023 | 7.036 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
ARMA1- | STCS1B | 15 | 0 | OHL | 0.49 | 2.0286 | 0.549 | 203 | 193 | 176 | 193 | B-2-2a | 2029 | Addition
ARMO1J | DUGR1Q | 14 | 0 | OHL | 0.7 | 2.898 | 0.784 | 203 | 193 | 176 | 193 | B-2-2a | 2029 | Change
BEAU4- | BING4- | 25.3 | 0 | OHL | 0.0328 | 0.4847 | 15.298 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2029 | Addition
BING4- | FAUG4K | 25.4 | 0 | OHL | 0.0329 | 0.4866 | 15.358 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2029 | Addition
BLHI2A | CLGO2A | 45.8 | 0 | OHL | 0.2593 | 1.8854 | 12.487 | 935 | 880 | 790 | 880 | B-2-2a | 2029 | Addition
BLHI2B | DAAS2- | 33.02 | 0 | OHL | 0.187 | 1.3593 | 9.003 | 935 | 880 | 790 | 880 | B-2-2a | 2029 | Addition
BONB4A | CMBS4B | 10.1 | 0 | OHL | 0.0131 | 0.1935 | 6.107 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2029 | Addition
BROA1A | QUOI1Q | 63 | 0 | OHL | 1.4888 | 13.3653 | 3.474 | 465 | 445 | 415 | 445 | B-2-2a | 2029 | Addition
BROA1B | FAUG1S | 82 | 0 | OHL | 1.9378 | 17.3962 | 4.522 | 465 | 445 | 415 | 445 | B-2-2a | 2029 | Addition
BROA1C | BROA1J | 7.75 | 0 | OHL | 0.1831 | 1.6441 | 0.427 | 465 | 445 | 415 | 445 | B-2-2a | 2029 | Addition
BROA1D | BROA1K | 7.75 | 0 | OHL | 0.1831 | 1.6441 | 0.427 | 465 | 445 | 415 | 445 | B-2-2a | 2029 | Addition
CAAD1Q | TNGF1- | 1 | 0 | OHL | 0.0236 | 0.2121 | 0.055 | 448 | 430 | 398 | 430 | B-2-2a | 2029 | Addition
CHLS1- | DLCH1A | 10.5 | 0 | OHL | 0.525 | 2.1735 | 0.588 | 203 | 193 | 176 | 193 | B-2-2a | 2029 | Addition
CLUN1S | ERRO1K | 15.4 | 0 | OHL | 0.7801 | 3.4546 | 0.795 | 241 | 230 | 210 | 230 | B-2-2a | 2029 | Change
CLUN1T | ERRO1J | 15.4 | 0 | OHL | 0.7801 | 3.4546 | 0.795 | 241 | 230 | 210 | 230 | B-2-2a | 2029 | Change
CMBS4A | KINA4B | 59.8 | 0 | OHL | 0.0775 | 1.1456 | 36.158 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2029 | Addition
COGL4J | LOCL4J | 3.5 | 0 | OHL | 0.0045 | 0.067 | 2.116 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2029 | Addition
COGL4K | LOCL4K | 3.5 | 0 | OHL | 0.0045 | 0.067 | 2.116 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2029 | Addition
CONN1J | STCS1A | 11 | 0 | OHL | 0.2159 | 1.9817 | 0.689 | 335 | 320 | 290 | 320 | B-2-2a | 2029 | Addition
CONN1K | KRKN1- | 2 | 0 | OHL | 0.1 | 0.414 | 0.112 | 203 | 193 | 176 | 193 | B-2-2a | 2029 | Addition
CONN1K | STCS1B | 11 | 0 | OHL | 0.2159 | 1.9817 | 0.689 | 335 | 320 | 290 | 320 | B-2-2a | 2029 | Addition
CRAS2- | CRDH2K | 31.48 | 0 | OHL | 0.1259 | 1.2907 | 8.877 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
CRAS2- | CRMU2K | 13.72 | 0 | OHL | 0.0549 | 0.5625 | 3.869 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
CRDH1J | KILC1Q | 4.98 | 0 | OHL | 0.7095 | 1.1715 | 0.244 | 99 | 92 | 79 | 92 | B-2-2a | 2029 | Addition
CRDH1K | FERO1S | 5.02 | 0 | OHL | 0.7118 | 1.1784 | 0.246 | 99 | 92 | 79 | 92 | B-2-2a | 2029 | Addition
CRDH2J | DALB2A | 14 | 0 | OHL | 0.0516 | 0.5615 | 3.962 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
CRDH2K | DALB2B | 14 | 0 | OHL | 0.0516 | 0.5615 | 3.962 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
CRMU2J | ANSN2- | 24.95 | 0 | OHL | 0.0998 | 1.023 | 7.036 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
CRMU2J | CRSN2Q | 44.7 | 0 | OHL | 0.1788 | 1.8327 | 12.605 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
CRMU2K | EARR21 | 28.34 | 0 | OHL | 0.1134 | 1.1621 | 7.993 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
CRSN2R | EARR2A | 16.36 | 0 | OHL | 0.0654 | 0.6706 | 4.612 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
CRSS1J | TNGF1- | 12.08 | 0 | OHL | 0.2855 | 2.5628 | 0.666 | 448 | 430 | 398 | 430 | B-2-2a | 2029 | Addition
DUGR1Q | EDIN1J | 9.5 | 0 | OHL | 0.475 | 1.9665 | 0.532 | 203 | 193 | 176 | 193 | B-2-2a | 2029 | Addition
EARR21 | EARR2B | 5.6 | 0 | OHL | 0.0224 | 0.2296 | 1.579 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
EARR2A | EARR2B | 5.6 | 0 | OHL | 0.0224 | 0.2296 | 1.579 | 1540 | 1480 | 1380 | 1480 | B-2-2a | 2029 | Addition
EDIN1A | EDIN1C | 20.25 | 0 | OHL | 0.4785 | 4.296 | 1.117 | 465 | 445 | 415 | 445 | B-2-2a | 2029 | Addition
EDIN1B | EDIN1D | 20.25 | 0 | OHL | 0.4785 | 4.296 | 1.117 | 465 | 445 | 415 | 445 | B-2-2a | 2029 | Addition
EDIN1K | GLNU1- | 0.5 | 0 | OHL | 0.0118 | 0.1061 | 0.028 | 448 | 430 | 398 | 430 | B-2-2a | 2029 | Addition
ELIB1- | ELIB1A | 7.5 | 0 | OHL | 0.375 | 1.5525 | 0.42 | 241 | 230 | 210 | 230 | B-2-2a | 2029 | Addition
ENEI1N | SYEL1N | 18 | 0 | OHL | 0.9 | 3.726 | 1.008 | 203 | 193 | 176 | 193 | B-2-2a | 2029 | Addition
FASQ1- | FASQ1J | 10 | 0 | OHL | 1 | 4.14 | 1.12 | 203 | 193 | 176 | 193 | B-2-2a | 2029 | Addition
FAUG1R | QUOI1Q | 19 | 0 | OHL | 0.449 | 4.0308 | 1.048 | 465 | 445 | 415 | 445 | B-2-2a | 2029 | Addition
FAUG4J | LOCL4K | 8.5 | 0 | OHL | 0.0109 | 0.1627 | 5.139 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2029 | Addition
FAUG4K | KINA4A | 80.2 | 0 | OHL | 0.104 | 1.5363 | 48.493 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2029 | Addition
FAUG4K | LOCL4J | 8.5 | 0 | OHL | 0.0109 | 0.1627 | 5.139 | 2780 | 2670 | 2480 | 2670 | B-2-2a | 2029 | Addition
FETT1- | GLDY1- | 19 | 0 | OHL | 0.9488 | 4.2918 | 1.068 | 203 | 193 | 176 | 193 | B-2-2a | 2029 | Addition
FWIL1Q | LOCL1K | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247 | B-2-2a | 2029 | Addition
FWIL1R | LOCL1K | 34.9 | 0 | OHL | 3.9786 | 7.9223 | 1.745 | 255 | 247 | 237 | 247 | B-2-2a | 2029 | Addition
GILB1J | SLCK1- | 7.5 | 0 | OHL | 0.375 | 1.5525 | 0.42 | 203 | 193 | 176 | 193 | B-2-2a | 2029 | Addition
INGA1Q | LOCL1K | 2.4 | 0 | OHL | 0.2184 | 0.5592 | 0.12 | 111 | 103 | 89 | 103 | B-2-2a | 2029 | Addition
INRU1Q | SALM1A | 3.05 | 0 | OHL | 0.1555 | 0.6832 | 0.158 | 241 | 230 | 210 | 230 | B-2-2a | 2029 | Addition
INRU1R | SALM1B | 3.05 | 0 | OHL | 0.1555 | 0.6832 | 0.158 | 241 | 230 | 210 | 230 | B-2-2a | 2029 | Addition
KILC1Q | CRDH1J | 4.98 | 0 | OHL | 0.7095 | 1.1715 | 0.244 | 99 | 92 | 79 | 92 | B-2-2a | 2029 | Addition
KINM2A | PEHE2- | 23.8 | 0 | OHL | 0.12 | 1.04 | 6.26 | 1090 | 1030 | 920 | 1030 | B-2-2a | 2029 | Addition
KINM2B | PERS2Q | 23.8 | 0 | OHL | 0.12 | 1.04 | 6.26 | 1090 | 1030 | 920 | 1030 | B-2-2a | 2029 | Addition
SALM1A | SFER1L | 3.05 | 0 | OHL | 0.1555 | 0.6832 | 0.158 | 241 | 230 | 210 | 230 | B-2-2a | 2029 | Addition
SALM1B | SFER1M | 3.05 | 0 | OHL | 0.1555 | 0.6832 | 0.158 | 241 | 230 | 210 | 230 | B-2-2a | 2029 | Addition
TNGF1- | TNGF1A | 21.5 | 0 | OHL | 1.075 | 4.4505 | 1.204 | 203 | 193 | 176 | 193 | B-2-2a | 2029 | Addition
AREX1A | CHMO1T | 4.7 | 0 | OHL | 0.35711 | 1.0182 | 0.24839 | 284 | 272 | 249 | 278 | B-2-2b | 2025 | Addition
BENB1- | BENB1T | 2.5 | 0 | OHL | 0.1875 | 0.5505 | 0.1315 | 167 | 160 | 148 | 160 | B-2-2b | 2025 | Addition
BENB1T | NECU1B | 4 | 0 | OHL | 0.1038 | 0.7722 | 0.2394 | 482 | 460 | 420 | 460 | B-2-2b | 2025 | Addition
CHAP1- | HAKB1- | 14.72 | 0 | OHL | 0.78187 | 3.1313 | 0.80314 | 242 | 225 | 194 | 225 | B-2-2b | 2025 | Change
CHMO1- | CHMO1T | 0.3 | 0 | OHL | 0.0225 | 0.066 | 0.0158 | 167 | 160 | 148 | 160 | B-2-2b | 2025 | Addition
CHMO1T | STOC1- | 5.9 | 0 | OHL | 0.4426 | 1.2993 | 0.3103 | 167 | 160 | 148 | 160 | B-2-2b | 2025 | Addition
DEVM1- | ERSK1Q | 16.5 | 0 | OHL | 1.0026 | 3.563 | 0.8861 | 213 | 202 | 185 | 202 | B-2-2b | 2025 | Change
DEVM1- | SPAV1Q | 7.63 | 0 | OHL | 0.5726 | 1.7268 | 0.3878 | 107 | 107 | 101 | 107 | B-2-2b | 2025 | Change
DEVM1- | SPAV1R | 7.51 | 0 | OHL | 0.5636 | 1.699 | 0.3818 | 107 | 107 | 101 | 107 | B-2-2b | 2025 | Change
FASI1- | FASI1A | 5 | 0 | OHL | 0.3756 | 1.1002 | 0.2633 | 199 | 191 | 178 | 191 | B-2-2b | 2025 | Addition
FASI1- | FASI1B | 5 | 0 | OHL | 0.3756 | 1.1002 | 0.2633 | 199 | 191 | 178 | 191 | B-2-2b | 2025 | Addition
FASI1A | HAWI1- | 19.11 | 0 | OHL | 1.7391 | 4.468 | 0.9407 | 133 | 124 | 107 | 124 | B-2-2b | 2025 | Addition
FASI1A | JUNV1- | 31.5 | 0 | OHL | 2.3859 | 7.5314 | 1.5385 | 199 | 191 | 178 | 191 | B-2-2b | 2025 | Addition
FASI1B | HAWI1- | 19.11 | 0 | OHL | 1.7391 | 4.468 | 0.9407 | 133 | 124 | 107 | 124 | B-2-2b | 2025 | Addition
FASI1B | JUNV1A | 31.5 | 0 | OHL | 2.3859 | 7.5314 | 1.5385 | 199 | 191 | 178 | 191 | B-2-2b | 2025 | Addition
GRNA1- | JUNV1- | 4.74 | 0 | OHL | 0.359 | 1.1333 | 0.2315 | 199 | 191 | 178 | 191 | B-2-2b | 2025 | Change
GRNA1- | JUNV1A | 4.74 | 0 | OHL | 0.359 | 1.1333 | 0.2315 | 199 | 191 | 178 | 191 | B-2-2b | 2025 | Addition
HOLM1- | SHRG1T | 8 | 0 | OHL | 0.6078 | 1.7331 | 0.4228 | 365 | 360 | 350 | 360 | B-2-2b | 2025 | Addition
HOLM1T | NECU1B | 16.35 | 0 | OHL | 0.4243 | 3.1565 | 0.9785 | 482 | 460 | 420 | 460 | B-2-2b | 2025 | Addition
HUNE4- | KILS4- | 59.125 | 0 | OHL | 0.0853 | 1.1104 | 36.755 | 2030 | 1930 | 1770 | 1930 | B-2-2b | 2025 | Addition
HUNE4- | KILS4T | 59.125 | 0 | OHL | 0.0853 | 1.1104 | 36.755 | 2030 | 1930 | 1770 | 1930 | B-2-2b | 2025 | Addition
JUNB1A | JUNV1A | 1 | 0 | OHL | 0 | 0.0001 | 0 | 2286 | 2286 | 2286 | 2286 | B-2-2b | 2025 | Addition
HARK13 | JUNV1- | 1 | 0 | OHL | 1.194 | 2.729 | 0.743 | 199 | 191 | 178 | 191 | B-2-2b | 2025 | Change
BENB1T | KEOO1Q | 20.25 | 0 | OHL | 0.5256 | 3.9095 | 1.2119 | 482 | 460 | 420 | 460 | B-2-2b | 2027 | Addition
BLCW1- | GNSH1- | 1.8 | 0 | OHL | 0.1352 | 0.3961 | 0.0948 | 167 | 160 | 148 | 160 | B-2-2b | 2027 | Addition
CAFA1Q | KEOO1- | 2.58 | 0 | OHL | 0.198 | 0.5682 | 0.1357 | 135 | 126 | 110 | 126 | B-2-2b | 2027 | Change
COAL4- | REDS4- | 11 | 0 | OHL | 0.0192 | 0.2085 | 6.5859 | 2210 | 2130 | 1980 | 2130 | B-2-2b | 2027 | Addition
COAN4- | REDS4- | 11 | 0 | OHL | 0.0192 | 0.2085 | 6.5859 | 2210 | 2130 | 1980 | 2130 | B-2-2b | 2027 | Addition
COAN4- | STHA4A | 21.79 | 0 | OHL | 0.0381 | 0.413 | 13.045 | 2210 | 2130 | 1980 | 2130 | B-2-2b | 2027 | Addition
COYL2- | CRCK2- | 25 | 0 | OHL | 0.1824 | 1.4207 | 5.0907 | 1110 | 1090 | 1060 | 1090 | B-2-2b | 2027 | Addition
CRCK2- | MAHI2- | 25 | 0 | OHL | 0.1824 | 1.4207 | 5.0907 | 1110 | 1090 | 1060 | 1090 | B-2-2b | 2027 | Addition
DUMF1- | OFOA1T | 2.08 | 0 | OHL | 0.0822 | 0.4694 | 0.1069 | 229 | 212 | 183 | 212 | B-2-2b | 2027 | Addition
ELVA4- | REDS4- | 15.77 | 0 | OHL | 0.0276 | 0.2989 | 9.4418 | 2210 | 2130 | 1980 | 2130 | B-2-2b | 2027 | Addition
ELVA4- | REDS4- | 15.77 | 0 | OHL | 0.0276 | 0.2989 | 9.4418 | 2210 | 2130 | 1980 | 2130 | B-2-2b | 2027 | Addition
ENHI3- | MONQ3- | 7 | 0 | OHL | 8.424 | 21.315 | 0.0269 | 34 | 32 | 28 | 32 | B-2-2b | 2027 | Addition
EWEH1Q | HORI1- | 6 | 0 | OHL | 0.4507 | 1.3202 | 0.316 | 199 | 191 | 178 | 191 | B-2-2b | 2027 | Addition
FASI1A | HAWI1D | 19.11 | 0 | OHL | 1.7391 | 4.468 | 0.9407 | 133 | 124 | 107 | 124 | B-2-2b | 2027 | Addition
FASI1B | HAWI1C | 19.11 | 0 | OHL | 1.7391 | 4.468 | 0.9407 | 133 | 124 | 107 | 124 | B-2-2b | 2027 | Addition
FELL1- | WNUK1- | 5 | 0 | OHL | 0.3751 | 1.1011 | 0.263 | 167 | 160 | 148 | 160 | B-2-2b | 2027 | Addition
GALA1- | HAWI1- | 23.55 | 0 | OHL | 1.7838 | 5.6307 | 1.1502 | 167 | 160 | 148 | 160 | B-2-2b | 2027 | Addition
GALA1- | HAWI1- | 23.55 | 0 | OHL | 1.7838 | 5.6307 | 1.1502 | 167 | 160 | 148 | 160 | B-2-2b | 2027 | Addition
GHPS1- | GLGL1- | 10 | 0 | OHL | 0.2554 | 1.7761 | 0.6376 | 12 | 12 | 11 | 12 | B-2-2b | 2027 | Addition
GHPS1- | GLGL1- | 10 | 0 | OHL | 0.2554 | 1.7761 | 0.6376 | 12 | 12 | 11 | 12 | B-2-2b | 2027 | Addition
GLLE1- | HOLM1T | 18.58 | 0 | OHL | 0.479 | 3.4684 | 1.142 | 482 | 460 | 420 | 460 | B-2-2b | 2027 | Addition
GLLE1- | KEOO1- | 7.68 | 0 | OHL | 0.1961 | 1.3641 | 0.4896 | 482 | 445 | 385 | 445 | B-2-2b | 2027 | Addition
GLLE1- | NETS1- | 30.04 | 0 | OHL | 2.3011 | 7.0802 | 1.472 | 284 | 278 | 270 | 278 | B-2-2b | 2027 | Change
GLLE1- | NETS1- | 30.04 | 0 | OHL | 2.3011 | 7.0802 | 1.472 | 284 | 278 | 270 | 278 | B-2-2b | 2027 | Change
GLLE1- | TONG1- | 33.1 | 0 | OHL | 2.0116 | 7.2879 | 1.729 | 198 | 186 | 168 | 186 | B-2-2b | 2027 | Addition
GLLE1- | TONG1- | 33.1 | 0 | OHL | 2.0116 | 7.2879 | 1.729 | 197.7656 | 186.1054 | 168.0436 | 186.1054 | B-2-2b | 2027 | Change
GNSH1- | TRSN1- | 5 | 0 | OHL | 0.3751 | 1.1011 | 0.263 | 167 | 160 | 148 | 160 | B-2-2b | 2027 | Addition
GRNA4- | HAKB4B | 1.97 | 0 | OHL | 0.0035 | 0.0381 | 1.1674 | 2370 | 2270 | 2270 | 2270 | B-2-2b | 2027 | Change
HAKB4- | MOFF4C | 43.79 | 0 | OHL | 0.0772 | 0.8467 | 25.9494 | 2370 | 2270 | 2270 | 2270 | B-2-2b | 2027 | Change
KEOO1- | KEOO1Q | 3 | 0 | OHL | 0.0779 | 0.5792 | 0.1795 | 482 | 460 | 420 | 460 | B-2-2b | 2027 | Addition
KINB4J | KINN4- | 8.8 | 0 | OHL | 0.0181 | 0.1864 | 4.8531 | 2000 | 1920 | 1790 | 1920 | B-2-2b | 2027 | Addition
KINB4K | KINN4- | 8.8 | 0 | OHL | 0.0181 | 0.1864 | 4.8531 | 2000 | 1920 | 1790 | 1920 | B-2-2b | 2027 | Addition
OFOA1- | OFOA1T | 20 | 0 | OHL | 1.5025 | 4.4007 | 1.0533 | 167 | 160 | 148 | 160 | B-2-2b | 2027 | Addition
DENN2T | KINC2- | 17.75 | 0 | OHL | 0.0442 | 0.6378 | 5.5815 | 1500 | 1500 | 1500 | 1500 | B-2-2b | 2028 | Addition
AYR-2Q | COYW2S | 9.37 | 0 | OHL | 0.0396 | 0.3827 | 2.6056 | 955 | 885 | 760 | 885 | B-2-2b | 2029 | Change
AYR-2R | COYW2T | 9.37 | 0 | OHL | 0.0396 | 0.3827 | 2.6056 | 955 | 885 | 760 | 885 | B-2-2b | 2029 | Change
BAGA1Q | BONN1- | 18.3 | 0 | OHL | 0.6862 | 3.8983 | 0.9904 | 238 | 220 | 191 | 220 | B-2-2b | 2029 | Change
BAGA1R | BONN1- | 18.4 | 0 | OHL | 0.69 | 3.9202 | 0.9957 | 238 | 220 | 191 | 220 | B-2-2b | 2029 | Change
BONB4- | DENN4- | 19.894 | 0 | OHL | 0.0255 | 0.3658 | 12.2977 | 2570 | 2570 | 2508 | 2570 | B-2-2b | 2029 | Change
BONB4A | DENN4- | 19.894 | 0 | OHL | 0.0255 | 0.3658 | 12.2977 | 2570 | 2570 | 2508 | 2570 | B-2-2b | 2029 | Addition
BREE1- | CLAW1- | 6.5 | 0 | OHL | 0.4883 | 1.4302 | 0.3423 | 199 | 191 | 178 | 191 | B-2-2b | 2029 | Addition
BRNX4- | ECCL4B | 34.2 | 0 | OHL | 0.0442 | 0.6403 | 20.975 | 2470 | 2350 | 2150 | 2350 | B-2-2b | 2029 | Addition
BRNX4- | SMEA4Q | 54.32 | 0 | OHL | 0.0716 | 1.0582 | 32.3337 | 2473 | 2349 | 2148 | 2349 | B-2-2b | 2029 | Addition
BRNX4Q | CRYR4- | 9.36 | 0 | OHL | 0.012 | 0.1717 | 5.799 | 2522 | 2397 | 2189 | 2397 | B-2-2b | 2029 | Addition
BRNX4R | ECCL4A | 34.2 | 0 | OHL | 0.0442 | 0.6403 | 20.975 | 2470 | 2350 | 2150 | 2350 | B-2-2b | 2029 | Addition
BROT1- | LINM1Q | 5.774 | 0 | OHL | 0.1373 | 1.3023 | 0.2972 | 134 | 123 | 123 | 123 | B-2-2b | 2029 | Change
CLYM4- | KINN4- | 49.48 | 0 | OHL | 0.0528 | 0.8203 | 33.5272 | 2780 | 2570 | 2220 | 2570 | B-2-2b | 2029 | Addition
COCK4Q | GALN4- | 35.5 | 0 | OHL | 0.0727 | 0.7644 | 19.1125 | 1120 | 1060 | 990 | 1060 | B-2-2b | 2029 | Addition
COCK4R | GALN4- | 35.5 | 0 | OHL | 0.0727 | 0.7644 | 19.1125 | 1120 | 1060 | 990 | 1060 | B-2-2b | 2029 | Addition
COYL2- | NECU2- | 14.3 | 0 | OHL | 0.0529 | 0.5733 | 4.0467 | 1540 | 1480 | 1380 | 1480 | B-2-2b | 2029 | Change
COYL2- | NECU2- | 14.3 | 0 | OHL | 0.0529 | 0.5733 | 4.0467 | 1540 | 1480 | 1380 | 1480 | B-2-2b | 2029 | Change
CRYR4- | FALL4- | 13.86 | 0 | OHL | 0.0182 | 0.2732 | 8.1821 | 2473 | 2349 | 2148 | 2349 | B-2-2b | 2029 | Change
DALB2A | DALL2- | 5.7 | 0 | OHL | 0.0241 | 0.2328 | 1.5851 | 1380 | 1320 | 1230 | 1320 | B-2-2b | 2029 | Addition
DALB2B | WIYH2- | 72.45 | 0 | OHL | 0.3064 | 2.9592 | 20.1469 | 1380 | 1320 | 1230 | 1320 | B-2-2b | 2029 | Addition
DALL2- | INVR2- | 22.55 | 0 | OHL | 0.0954 | 0.921 | 6.2707 | 570 | 570 | 570 | 570 | B-2-2b | 2029 | Addition
DENN2- | DENN2T | 1 | 0 | OHL | 0 | 0 | 0 | 4763 | 4763 | 4763 | 4763 | B-2-2b | 2029 | Addition
DENN2- | LAMB2- | 31.991 | 0 | OHL | 0.1391 | 1.4345 | 8.3553 | 1380 | 1320 | 1230 | 1320 | B-2-2b | 2029 | Change
DENN2T | EERH2- | 24.88 | 0 | OHL | 0.0561 | 0.8727 | 7.9683 | 1500 | 1500 | 1500 | 1500 | B-2-2b | 2029 | Addition
DENN4- | KINN4- | 16.1 | 0 | OHL | 0.0178 | 0.273 | 10.7108 | 2550 | 2420 | 2210 | 2420 | B-2-2b | 2029 | Addition
DENN4- | KINN4- | 16.1 | 0 | OHL | 0.0178 | 0.273 | 10.7108 | 2550 | 2420 | 2210 | 2420 | B-2-2b | 2029 | Addition
DENN4- | LAMB4T | 32.18 | 0 | OHL | 0.0661 | 0.6818 | 17.786 | 2000 | 1920 | 1790 | 1920 | B-2-2b | 2029 | Addition
DEVM4- | WIYH4Q | 28.908 | 0 | OHL | 0.0586 | 0.5888 | 16.3967 | 1390 | 1280 | 1110 | 1280 | B-2-2b | 2029 | Change
DUNE1- | GALN1Q | 12.64 | 0 | OHL | 0.3239 | 2.287 | 0.7972 | 482 | 460 | 420 | 460 | B-2-2b | 2029 | Addition
DUNE1- | GALN1R | 12.64 | 0 | OHL | 0.3239 | 2.287 | 0.7972 | 482 | 460 | 420 | 460 | B-2-2b | 2029 | Addition
ECCL1- | GALA1- | 30.58 | 0 | OHL | 1.6249 | 6.7325 | 1.5989 | 242 | 232 | 214 | 232 | B-2-2b | 2029 | Addition
ECCL1- | GALN1Q | 41.14 | 0 | OHL | 1.8834 | 8.6227 | 2.2702 | 242 | 232 | 214 | 232 | B-2-2b | 2029 | Addition
ECCL4A | GALN4- | 30.4 | 0 | OHL | 0.0623 | 0.6546 | 16.3668 | 2000 | 1920 | 1790 | 1920 | B-2-2b | 2029 | Addition
ECCL4B | GALN4- | 30.4 | 0 | OHL | 0.0623 | 0.6546 | 16.3668 | 2000 | 1920 | 1790 | 1920 | B-2-2b | 2029 | Addition
EKIS2- | STHA2B | 5.8 | 0 | OHL | 0.0245 | 0.2366 | 1.614 | 1372 | 1324 | 1228 | 1324 | B-2-2b | 2029 | Change
ELVA1- | NLEI1- | 14 | 0 | OHL | 0.7436 | 2.9782 | 0.7639 | 226 | 216 | 200 | 216 | B-2-2b | 2029 | Addition
EUCH1- | LORG1- | 3.5 | 0 | OHL | 0.2629 | 0.7701 | 0.1843 | 167 | 160 | 148 | 160 | B-2-2b | 2029 | Addition
FALL4- | SMEA4R | 31.1 | 0 | OHL | 0.0414 | 0.6133 | 18.3526 | 2473 | 2349 | 2148 | 2349 | B-2-2b | 2029 | Change
GALA1- | GALN1R | 11 | 0 | OHL | 0.2819 | 1.9903 | 0.6938 | 482 | 460 | 420 | 460 | B-2-2b | 2029 | Addition
GHPS4- | REDS4- | 25 | 0 | OHL | 0.0514 | 0.5412 | 13.4707 | 1995 | 1926 | 1787 | 1926 | B-2-2b | 2029 | Addition
GHPS4- | REDS4- | 25 | 0 | OHL | 0.0514 | 0.5412 | 13.4707 | 1995 | 1926 | 1787 | 1926 | B-2-2b | 2029 | Addition
GLLU1R | NETS1- | 22 | 0 | OHL | 2.0091 | 5.2246 | 1.0696 | 49 | 49 | 49 | 49 | B-2-2b | 2029 | Change
GLNI1- | REDH1- | 10.547 | 0 | OHL | 0.9555 | 2.3056 | 0.552 | 161 | 156 | 145 | 156 | B-2-2b | 2029 | Change
HOLM1T | QUAN1- | 6 | 0 | OHL | 0.4559 | 1.2998 | 0.3171 | 284 | 278 | 270 | 278 | B-2-2b | 2029 | Addition
JUNB1- | JUNV1- | 1 | 0 | OHL | 0 | 0.0001 | 0 | 2286 | 2286 | 2286 | 2286 | B-2-2b | 2029 | Change
KAIM2- | SMEA2- | 8.78 | 0 | OHL | 0.0374 | 0.3629 | 2.4323 | 1090 | 1030 | 925 | 1030 | B-2-2b | 2029 | Change
KINC2- | KINN2A | 1.9 | 0 | OHL | 0.0043 | 0.0666 | 0.6085 | 1390 | 1280 | 1110 | 1280 | B-2-2b | 2029 | Change
KINC2- | MOSM2- | 35.776 | 0 | OHL | 0.1612 | 1.5146 | 9.6208 | 1090 | 1030 | 925 | 1030 | B-2-2b | 2029 | Addition
KINC2- | WFIE2- | 33.449 | 0 | OHL | 0.1501 | 1.3961 | 9.079 | 1090 | 1030 | 925 | 1030 | B-2-2b | 2029 | Addition
LAMB2- | WIYH2- | 17.88 | 0 | OHL | 0.0756 | 0.7303 | 4.9716 | 1380 | 1320 | 1230 | 1320 | B-2-2b | 2029 | Change
LAMB4T | WIYH4Q | 17.88 | 0 | OHL | 0.0357 | 0.3452 | 10.5184 | 2000 | 1920 | 1790 | 1920 | B-2-2b | 2029 | Addition
LORG1- | SHRG1T | 10 | 0 | OHL | 0.7598 | 2.1663 | 0.5285 | 284 | 278 | 270 | 278 | B-2-2b | 2029 | Change
NEIL2- | WIYH2R | 25.453 | 0 | OHL | 0.1093 | 1.0873 | 6.9047 | 1372 | 1324 | 1228 | 1324 | B-2-2b | 2029 | Change
REDS1A | SPRB1- | 18 | 0 | OHL | 1.3662 | 4.0108 | 0.9183 | 284 | 278 | 270 | 278 | B-2-2b | 2029 | Addition
REDS1A | SPRB1- | 18 | 0 | OHL | 1.3662 | 4.0108 | 0.9183 | 284 | 278 | 270 | 278 | B-2-2b | 2029 | Addition
SMEA4Q | WISH4- | 61.77 | 0 | OHL | 0.1313 | 1.2264 | 35.999 | 2778 | 2736 | 2667 | 2736 | B-2-2b | 2029 | Change
SMEA4R | WISH4- | 61.77 | 0 | OHL | 0.1313 | 1.2264 | 35.999 | 2778 | 2736 | 2667 | 2736 | B-2-2b | 2029 | Change
STHA4A | WISH4- | 11.6 | 0 | OHL | 0.0243 | 0.2192 | 7.0076 | 2778 | 2736 | 2667 | 2736 | B-2-2b | 2029 | Change
STHA4B | WISH4- | 11.6 | 0 | OHL | 0.0243 | 0.2192 | 7.0076 | 2778 | 2736 | 2667 | 2736 | B-2-2b | 2029 | Change
BOLN41 | LHOR4A | 28.1 | 0 | OHL | 0.0305 | 0.4887 | 18.5239 | 3102 | 2935 | 2765 | 2935 | B-2-2c | 2025 | Addition
BOLN41 | NINF41 | 51.404 | 0 | OHL | 0.0558 | 0.8941 | 33.8859 | 3102 | 2935 | 2765 | 2935 | B-2-2c | 2025 | Change
CARR41 | DAIN41 | 2.545 | 0 | OHL | 0.004 | 0.0488 | 1.5263 | 3100 | 3100 | 3100 | 3100 | B-2-2c | 2025 | Change
CARR41 | DAIN41 | 3.352 | 0 | OHL | 0.0059 | 0.0653 | 1.9782 | 3102 | 3048 | 2958 | 3048 | B-2-2c | 2025 | Change
CARR4A | DAIN41 | 2.063 | 0 | OHL | 0.0032 | 0.0397 | 1.2352 | 1500 | 1500 | 1500 | 1500 | B-2-2c | 2025 | Change
COTT41 | KEAD4C | 34.628 | 0 | OHL | 0.054 | 0.673 | 20.467 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2025 | Change
COTT41 | KEAD4D | 34.479 | 0 | OHL | 0.0538 | 0.6702 | 20.3774 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2025 | Change
GART4B | KEAD41 | 5.689 | 0 | OHL | 0.0062 | 0.0989 | 3.7497 | 3420 | 3260 | 2980 | 3260 | B-2-2c | 2025 | Change
HARG41 | HUTT42 | 81.544 | 0 | OHL | 0.127 | 1.5659 | 48.8916 | 2771 | 2771 | 2663 | 2771 | B-2-2c | 2025 | Addition
KLYN41 | NECT41 | 30.347 | 0 | OHL | 0.0269 | 0.5209 | 20.404 | 2520 | 2520 | 2520 | 2520 | B-2-2c | 2025 | Addition
KLYN41 | WALP41 | 16.672 | 0 | OHL | 0.0148 | 0.286 | 11.2124 | 2520 | 2520 | 2520 | 2520 | B-2-2c | 2025 | Addition
LHOR4B | NINF41 | 23.2 | 0 | OHL | 0.0252 | 0.4035 | 15.2937 | 3102 | 2935 | 2765 | 2935 | B-2-2c | 2025 | Addition
NECT41 | NORM41 | 37.492 | 0 | OHL | 0.0332 | 0.644 | 25.1993 | 3326 | 3326 | 3317 | 3326 | B-2-2c | 2025 | Addition
NECT41 | NORM41 | 37.492 | 0 | OHL | 0.0332 | 0.644 | 25.1993 | 3326 | 3258 | 3060 | 3258 | B-2-2c | 2025 | Addition
NECT41 | WALP41 | 41.619 | 0 | OHL | 0.0369 | 0.7148 | 27.9739 | 3326 | 3160 | 2971 | 3160 | B-2-2c | 2025 | Addition
ALVE4A | INDQ41 | 97.176 | 0 | OHL | 0.2121 | 1.9367 | 56.1415 | 1389 | 1284 | 1108 | 1284 | B-2-2c | 2027 | Addition
ALVE4A | INDQ41 | 97.294 | 0 | OHL | 0.2123 | 1.9391 | 56.2092 | 1389 | 1284 | 1108 | 1284 | B-2-2c | 2027 | Addition
ALVE4A | TAUN41 | 73.293 | 0 | OHL | 0.117 | 1.477 | 42.0344 | 1389 | 1284 | 1108 | 1284 | B-2-2c | 2027 | Addition
ALVE4A | TAUN42 | 73.437 | 0 | OHL | 0.1172 | 1.4799 | 42.117 | 1389 | 1284 | 1108 | 1284 | B-2-2c | 2027 | Addition
BRIM2A | WALX2A | 5.865 | 0 | OHL | 0.0193 | 0.2381 | 1.6636 | 2310 | 2100 | 2030 | 2100 | B-2-2c | 2027 | Addition
BRIM2B | WALX2A | 5.997 | 0 | OHL | 0.0198 | 0.2434 | 1.701 | 2310 | 2100 | 2030 | 2100 | B-2-2c | 2027 | Addition
BRIM4C | WALX41 | 5.97 | 0 | OHL | 0.0093 | 0.1145 | 3.5827 | 3100 | 3100 | 3100 | 3100 | B-2-2c | 2027 | Addition
BRIM4D | WALX41 | 5.97 | 0 | OHL | 0.0093 | 0.1145 | 3.5827 | 3100 | 3100 | 3100 | 3100 | B-2-2c | 2027 | Addition
BRLE41 | FLEE41 | 17.555 | 0 | OHL | 0.0156 | 0.3015 | 11.7995 | 3320 | 3320 | 3130 | 3320 | B-2-2c | 2027 | Change
BRLE41 | FLEE41 | 17.555 | 0 | OHL | 0.0156 | 0.3015 | 11.7995 | 3330 | 3160 | 2970 | 3160 | B-2-2c | 2027 | Change
CELL42 | DRAK41 | 45.012 | 0 | OHL | 0.0719 | 0.8656 | 27.0675 | 2397 | 2302 | 2144 | 2302 | B-2-2c | 2027 | Addition
CELL43 | DRAK41 | 45.712 | 0 | OHL | 0.073 | 0.8791 | 27.4871 | 2397 | 2302 | 2144 | 2302 | B-2-2c | 2027 | Addition
COTT43 | WBUR42 | 6.76 | 0 | OHL | 0.0105 | 0.1321 | 3.9942 | 3326 | 3160 | 2144 | 3160 | B-2-2c | 2027 | Addition
CREB41 | CREB42 | 14.835 | 0 | OHL | 0.0131 | 0.2548 | 9.9719 | 3075 | 3075 | 3075 | 3075 | B-2-2c | 2027 | Addition
CREB41 | CREB42 | 14.904 | 0 | OHL | 0.0132 | 0.256 | 10.0181 | 3075 | 3075 | 3075 | 3075 | B-2-2c | 2027 | Addition
CREB42 | THTO41 | 14.835 | 0 | OHL | 0.0131 | 0.2548 | 9.9719 | 3075 | 3075 | 3075 | 3075 | B-2-2c | 2027 | Addition
CREB42 | THTO42 | 14.904 | 0 | OHL | 0.0132 | 0.256 | 10.0181 | 3075 | 3075 | 3075 | 3075 | B-2-2c | 2027 | Addition
DISS4A | NORM41 | 29.7 | 0 | OHL | 0.0263 | 0.5101 | 19.9633 | 3326 | 3326 | 3320 | 3326 | B-2-2c | 2027 | Change
EGGB41 | MFSN41 | 10.37 | 0 | OHL | 0.0091 | 0.1781 | 6.9831 | 3070 | 2830 | 2420 | 2830 | B-2-2c | 2027 | Addition
EGGB42 | MFSN41 | 10.37 | 0 | OHL | 0.0091 | 0.1781 | 6.9831 | 3070 | 2830 | 2420 | 2830 | B-2-2c | 2027 | Addition
GWYD41 | TRAW41 | 39.445 | 0 | OHL | 0.0615 | 0.7568 | 23.67 | 3102 | 3048 | 2958 | 3048 | B-2-2c | 2027 | Addition
GWYD41 | TREU4A | 25.573 | 0 | OHL | 0.0398 | 0.4907 | 15.3454 | 3102 | 3048 | 2958 | 3048 | B-2-2c | 2027 | Addition
HAMB4A | STAH4A | 3.926 | 0 | OHL | 0.007 | 0.078 | 2.2826 | 1970 | 1870 | 1710 | 1870 | B-2-2c | 2027 | Change
HAMB4B | STAH4B | 3.926 | 0 | OHL | 0.007 | 0.078 | 2.2826 | 1970 | 1970 | 1970 | 1970 | B-2-2c | 2027 | Change
HARG41 | HUTT43 | 81.544 | 0 | OHL | 0.127 | 1.5659 | 48.8916 | 2771 | 2771 | 2771 | 2771 | B-2-2c | 2027 | Addition
KNAR21 | TADT2A | 25 | 0 | OHL | 0.1224 | 1.0976 | 6.5267 | 1500 | 1500 | 1300 | 1300 | B-2-2c | 2027 | Addition
KNAR21 | TADT2B | 25 | 0 | OHL | 0.1224 | 1.0976 | 6.5267 | 1500 | 1500 | 1300 | 1500 | B-2-2c | 2027 | Addition
MFSN21 | TADT2A | 14.18 | 0 | OHL | 0.0694 | 0.6225 | 3.7019 | 1500 | 1500 | 1300 | 1500 | B-2-2c | 2027 | Addition
OBST4A | YORK4A | 2.8 | 0 | OHL | 0.0051 | 0.0575 | 1.5702 | 1500 | 1500 | 1750 | 1300 | B-2-2c | 2027 | Addition
OBST4B | YORK4B | 2.8 | 0 | OHL | 0.0051 | 0.0575 | 1.5702 | 1500 | 1500 | 1750 | 1300 | B-2-2c | 2027 | Addition
OSBA41 | THTO43 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 3326 | 3160 | 2980 | 3160 | B-2-2c | 2027 | Change
OSBA42 | THTO42 | 16.79 | 0 | OHL | 0.0182 | 0.292 | 11.0682 | 3326 | 3160 | 2980 | 3160 | B-2-2c | 2027 | Addition
OVER21 | POPP21 | 4.729 | 0 | OHL | 0.0257 | 0.2475 | 1.0505 | 680 | 540 | 540 | 680 | B-2-2c | 2027 | Addition
OVER21 | POPP21 | 4.634 | 0 | OHL | 0.0254 | 0.2439 | 1.0211 | 550 | 440 | 440 | 550 | B-2-2c | 2027 | Addition
OVER21 | TADT2A | 20.176 | 0 | OHL | 0.0988 | 0.8858 | 5.2674 | 1500 | 1500 | 1300 | 1500 | B-2-2c | 2027 | Addition
OVER21 | TADT2B | 20.176 | 0 | OHL | 0.0988 | 0.8858 | 5.2673 | 1500 | 1500 | 1300 | 1500 | B-2-2c | 2027 | Addition
PELH4A | RYEH4A | 23.015 | 0 | OHL | 0.0202 | 0.3952 | 15.4966 | 3326 | 3326 | 3320 | 3326 | B-2-2c | 2027 | Addition
PELH4A | RYEH4B | 23.439 | 0 | OHL | 0.0206 | 0.4024 | 15.7811 | 3326 | 3326 | 3320 | 3326 | B-2-2c | 2027 | Addition
PEMB41 | POAB41 | 74.6 | 0 | OHL | 0.081 | 1.2975 | 49.1773 | 2779 | 2568 | 2217 | 2568 | B-2-2c | 2027 | Addition
PEMB41 | SWAN41 | 83.854 | 0 | OHL | 0.091 | 1.4585 | 55.2774 | 2779 | 2568 | 2217 | 2568 | B-2-2c | 2027 | Change
PENT41 | WYLS41 | 27.13 | 0 | OHL | 0.0294 | 0.4719 | 17.8844 | 2779 | 2568 | 2217 | 2568 | B-2-2c | 2027 | Addition
POAB41 | SWAN41 | 9.35 | 0 | OHL | 0.0101 | 0.1626 | 6.1636 | 2779 | 2568 | 2217 | 2568 | B-2-2c | 2027 | Addition
RYEH41 | RYEH4B | 0.137 | 0 | OHL | 0.0001 | 0.0024 | 0.0923 | 3326 | 3326 | 3320 | 3326 | B-2-2c | 2027 | Change
RYEH41 | WALX41 | 5.324 | 0 | OHL | 0.0047 | 0.0914 | 3.5851 | 3326 | 3326 | 3326 | 3326 | B-2-2c | 2027 | Addition
RYEH4A | WALX41 | 5.461 | 0 | OHL | 0.0048 | 0.0938 | 3.6774 | 3326 | 3326 | 3326 | 3326 | B-2-2c | 2027 | Addition
SPEN42 | STEW41 | 37.795 | 0 | OHL | 0.0497 | 0.7368 | 22.4165 | 2780 | 2780 | 2480 | 2670 | B-2-2c | 2027 | Change
TRAW41 | TREU4B | 64.278 | 0 | OHL | 0.1002 | 1.2333 | 38.5726 | 3102 | 3048 | 2958 | 3048 | B-2-2c | 2027 | Change
WYLF41 | WYLS41 | 8.11 | 0 | OHL | 0.0088 | 0.1411 | 5.3462 | 2779 | 2568 | 2217 | 2568 | B-2-2c | 2027 | Addition
AMEM4A | UXBR41 | 19.256 | 0 | OHL | 0.0368 | 0.3831 | 11.1597 | 2009 | 1911 | 1746 | 1911 | B-2-2c | 2029 | Addition
AMEM4B | UXBR41 | 19.256 | 0 | OHL | 0.0368 | 0.3831 | 11.1597 | 2032 | 1933 | 1766 | 1933 | B-2-2c | 2029 | Addition
BARK41 | WHAM41 | 9.662 | 0 | OHL | 0.0151 | 0.191 | 5.623 | 3100 | 3100 | 3100 | 3100 | B-2-2c | 2029 | Change
BRFO41 | TWIN4A | 28.419 | 0 | OHL | 0.0252 | 0.4881 | 19.1016 | 3820 | 3630 | 3320 | 3630 | B-2-2c | 2029 | Addition
BRFO41 | TWIN4B | 28.419 | 0 | OHL | 0.0252 | 0.4881 | 19.1016 | 3820 | 3630 | 3320 | 3630 | B-2-2c | 2029 | Addition
BRIN41 | CHTE41 | 22.375 | 0 | OHL | 0.0243 | 0.3892 | 14.7493 | 2810 | 2700 | 2510 | 2700 | B-2-2c | 2029 | Addition
COTT42 | WBUR42 | 6.76 | 0 | OHL | 0.0096 | 0.1298 | 4.0616 | 3326 | 3160 | 2971 | 3160 | B-2-2c | 2029 | Change
ELST4B | SUND41 | 34.834 | 0 | OHL | 0.0549 | 0.6691 | 20.9253 | 2400 | 2300 | 2140 | 2300 | B-2-2c | 2029 | Addition
ELST4B | SUND42 | 34.706 | 0 | OHL | 0.0547 | 0.6666 | 20.848 | 3100 | 1732 | 1732 | 1732 | B-2-2c | 2029 | Change
FOUX41 | PENI4A | 23.025 | 0 | OHL | 0.0303 | 0.4488 | 13.6563 | 2780 | 2700 | 2510 | 2700 | B-2-2c | 2029 | Addition
GRAI41 | WALE41 | 1.68 | 0 | OHL | 0.0015 | 0.0288 | 1.1313 | 3326 | 3160 | 2633 | 2813 | B-2-2c | 2029 | Change
GREN41 | MARV4A | 26 | 0 | OHL | 0.0406 | 0.5007 | 15.5357 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Change
GREN41 | MARV4B | 26 | 0 | OHL | 0.0406 | 0.5007 | 15.5357 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Change
HAKB4- | HARG41 | 10.107 | 0 | OHL | 0.0175 | 0.1997 | 5.8779 | 3180 | 3130 | 3050 | 3130 | B-2-2c | 2029 | Change
HAKB4B | HARG41 | 10.107 | 0 | OHL | 0.0175 | 0.1997 | 5.8779 | 3180 | 3130 | 3050 | 3130 | B-2-2c | 2029 | Change
HAWP41 | NORT41 | 30.157 | 0 | OHL | 0.047 | 0.5786 | 18.0971 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Addition
HAWP4A | NORT41 | 30.157 | 0 | OHL | 0.047 | 0.5786 | 18.0971 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Change
HIMB21 | THUR2A | 46.867 | 0 | OHL | 0.492 | 1.9585 | 12.7959 | 626 | 591 | 535 | 591 | B-2-2c | 2029 | Addition
HIMB41 | STAY41 | 20.939 | 0 | OHL | 0.0329 | 0.4037 | 12.4972 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Addition
HIMB41 | STOB41 | 39.671 | 0 | OHL | 0.0642 | 0.7694 | 23.5463 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Addition
IVER4A | UXBR41 | 1 | 0 | OHL | 0.0368 | 0.019895 | 0.57954 | 2009 | 1911 | 1746 | 1911 | B-2-2c | 2029 | Addition
IVER4B | UXBR41 | 1 | 0 | OHL | 0.0368 | 0.019895 | 0.57954 | 2032 | 1933 | 1766 | 1933 | B-2-2c | 2029 | Addition
MARV4A | SUND41 | 13.75 | 0 | OHL | 0.0215 | 0.2648 | 8.216 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Change
NORT41 | OBST4A | 70.35 | 0 | OHL | 0.0624 | 1.2083 | 47.2853 | 3326 | 3326 | 3320 | 3326 | B-2-2c | 2029 | Change
NORT41 | OBST4B | 70.35 | 0 | OHL | 0.0624 | 1.2083 | 47.2853 | 3326 | 3326 | 3320 | 3326 | B-2-2c | 2029 | Change
OBST4A | OSBA41 | 13.35 | 0 | OHL | 0.0118 | 0.2293 | 8.9731 | 3326 | 3326 | 3320 | 3326 | B-2-2c | 2029 | Change
OBST4B | OSBA42 | 13.35 | 0 | OHL | 0.0118 | 0.2293 | 8.9731 | 3326 | 3326 | 3320 | 3326 | B-2-2c | 2029 | Change
PELH41 | TWIN4A | 40.882 | 0 | OHL | 0.0362 | 0.7022 | 27.4783 | 3100 | 3100 | 3100 | 3100 | B-2-2c | 2029 | Addition
PELH41 | TWIN4B | 40.823 | 0 | OHL | 0.0362 | 0.7012 | 27.4387 | 3820 | 3630 | 3320 | 3630 | B-2-2c | 2029 | Addition
PELH41 | WYMO41 | 26.856 | 0 | OHL | 0.0291 | 0.4667 | 17.7225 | 2771 | 2771 | 2692 | 2771 | B-2-2c | 2029 | Change
PELH41 | WYMO41 | 26.891 | 0 | OHL | 0.0292 | 0.4677 | 17.7269 | 3180 | 3180 | 3180 | 3180 | B-2-2c | 2029 | Addition
PEMB41 | POAB41 | 74.6 | 0 | OHL | 0.081 | 1.2975 | 49.1773 | 2779 | 2568 | 2217 | 2568 | B-2-2c | 2029 | Addition
PENI4A | PENT41 | 4.545 | 0 | OHL | 0.0049 | 0.0722 | 3.2978 | 2780 | 2570 | 2220 | 2570 | B-2-2c | 2029 | Addition
POAB41 | SWAN41 | 9.454 | 0 | OHL | 0.0103 | 0.1644 | 6.232 | 2779 | 2779 | 2779 | 2779 | B-2-2c | 2029 | Addition
RATS41 | STAY4A | 43.614 | 0 | OHL | 0.0738 | 0.8539 | 25.6652 | 2147 | 2057 | 1905 | 2057 | B-2-2c | 2029 | Change
SUND41 | WYMO41 | 18.156 | 0 | OHL | 0.0197 | 0.3152 | 11.9934 | 3180 | 3180 | 3180 | 3180 | B-2-2c | 2029 | Change
SUND42 | WYMO41 | 17.986 | 0 | OHL | 0.0195 | 0.3128 | 11.8566 | 3180 | 3180 | 3180 | 3180 | B-2-2c | 2029 | Addition

## Composite
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Sheet_Name | Year | Status
ABNE1R | AMUL1G | 28.099 | 0.001 | Composite | 2.8706 | 6.5818 | 1.397 | 132 | 123 | 106 | 123 | B-2-1a
GARB1T | SLOY1K | 14.185 | 0.715 | Composite | 1.44 | 3.3 | 0.7 | 132 | 123 | 106 | 123 | B-2-1a
SFEM1Q | SFER1L | 1.9 | 1.1 | Composite | 0.382 | 0.557 | 1.871 | 132 | 122 | 106 | 122 | B-2-1a
SFEM1R | SFER1M | 1.9 | 1.1 | Composite | 0.382 | 0.557 | 1.871 | 132 | 122 | 106 | 122 | B-2-1a
AREC1- | MAHI1- | 7.615 | 1.613 | Composite | 0.4363 | 1.668 | 2.5345 | 214 | 195 | 195 | 195 | B-2-1b
AREC3- | GLAP3- | 10.79 | 5.931 | Composite | 10.6428 | 36.9228 | 0.6748 | 40 | 38 | 38 | 38 | B-2-1b
BAGA1Q | DRCR1Q | 4.71 | 3.39 | Composite | 0.5756 | 1.4393 | 2.8779 | 146 | 146 | 146 | 146 | B-2-1b
BAGA1R | DRCR1R | 4.71 | 3.38 | Composite | 0.5752 | 1.4382 | 2.8701 | 146 | 146 | 146 | 146 | B-2-1b
BAIN1Q | BONN1- | 7.02 | 0.08 | Composite | 0.2761 | 1.4801 | 0.4755 | 114 | 114 | 114 | 114 | B-2-1b
BAIN1R | BONN1- | 7.02 | 0.28 | Composite | 0.2797 | 1.4992 | 0.7089 | 114 | 114 | 114 | 114 | B-2-1b
BERW1Q | ECCL1- | 21.54 | 0.31 | Composite | 1.622 | 4.903 | 1.5274 | 132 | 123 | 106 | 123 | B-2-1b
BERW1R | ECCL1- | 21.54 | 0.27 | Composite | 1.6213 | 4.8991 | 1.4716 | 132 | 123 | 106 | 123 | B-2-1b
BLKL1- | WISH1- | 5.33 | 6.13 | Composite | 0.6542 | 1.8052 | 6.2962 | 161 | 154 | 140 | 154 | B-2-1b
BLLX1- | LINM1Q | 12.85 | 5.24 | Composite | 1.1339 | 3.1699 | 7.5599 | 132 | 123 | 106 | 123 | B-2-1b
BONN1- | DENN1- | 4.04 | 0.3 | Composite | 0.1878 | 0.4755 | 1.1901 | 240 | 234 | 202 | 234 | B-2-1b
BONN1- | STIR1S | 3.3 | 13.05 | Composite | 0.2591 | 1.8255 | 22.5303 | 238 | 219 | 191 | 219 | B-2-1b
BONN1- | STIR1T | 3.3 | 13.05 | Composite | 0.2591 | 1.8255 | 22.5303 | 238 | 219 | 191 | 219 | B-2-1b
BONN2A | DENN2- | 3.812 | 0.55 | Composite | 0.0183 | 0.1734 | 4.382 | 722 | 647 | 593 | 647 | B-2-1b
BONN2B | DENN2- | 3.812 | 0.46 | Composite | 0.0181 | 0.1709 | 3.8346 | 722 | 647 | 593 | 647 | B-2-1b
BRAP1- | PAIS1R | 4.52 | 2.19 | Composite | 0.1309 | 0.9964 | 3.6706 | 274 | 274 | 274 | 274 | B-2-1b
CHAP1- | DUMF1- | 26.9 | 0.125 | Composite | 1.065 | 6.0817 | 1.5576 | 171 | 155 | 155 | 155 | B-2-1b
CHAP1- | ECCF1J | 6.569 | 0.23 | Composite | 0.6009 | 1.515 | 0.651 | 18 | 18 | 18 | 18 | B-2-1b
CHAP1- | ECCF1K | 6.569 | 0.185 | Composite | 0.6 | 1.5109 | 0.5882 | 21 | 21 | 21 | 21 | B-2-1b
CLYM2- | DALM2R | 4.21 | 0.093 | Composite | 0.0193 | 0.1737 | 1.8402 | 695 | 560 | 500 | 560 | B-2-1b
COAL1A | LINM1R | 5.774 | 3.14 | Composite | 0.2748 | 1.6606 | 2.8754 | 134 | 123 | 123 | 123 | B-2-1b
COAT2Q | NEAR2Q | 3.4 | 4.9 | Composite | 0.045 | 0.2476 | 17.1398 | 176 | 156 | 156 | 156 | B-2-1b
COAT2R | NEAR2R | 3.4 | 4.9 | Composite | 0.045 | 0.2476 | 17.1398 | 176 | 156 | 156 | 156 | B-2-1b
COYL1- | COYT1T | 4.37 | 0.27 | Composite | 0.4027 | 1.0118 | 0.5089 | 132 | 123 | 106 | 123 | B-2-1b
COYL1- | MAYT1T | 9.14 | 0.57 | Composite | 0.8423 | 2.157 | 1.0619 | 132 | 123 | 106 | 123 | B-2-1b
COYL2- | COYW2S | 1.29 | 0.08 | Composite | 0.0057 | 0.0515 | 0.4645 | 1500 | 1500 | 1500 | 1500 | B-2-1b
COYT1T | KILS1- | 15.215 | 4.815 | Composite | 1.4768 | 3.99 | 7.6706 | 132 | 123 | 106 | 123 | B-2-1b
COYT1T | MAYB1- | 17.666 | 0.28 | Composite | 1.6159 | 4.1178 | 1.1779 | 132 | 123 | 106 | 123 | B-2-1b
CRUA2Q | DALL2- | 8.16 | 0.4 | Composite | 0.0346 | 0.3435 | 4.3204 | 283 | 283 | 283 | 283 | B-2-1b
CRUA2R | DALL2- | 8.16 | 0.4 | Composite | 0.0346 | 0.3435 | 4.3204 | 283 | 283 | 283 | 283 | B-2-1b
CURR1A | GORG1Q | 1.49 | 5.8 | Composite | 0.261 | 0.9656 | 5.1127 | 111 | 100 | 92 | 100 | B-2-1b
CURR1A | LING1Q | 8.323 | 5.205 | Composite | 0.7926 | 2.2632 | 6.4813 | 132 | 123 | 106 | 123 | B-2-1b
CURR1B | GORG1R | 1.49 | 5.78 | Composite | 0.2603 | 0.9634 | 5.0953 | 111 | 100 | 92 | 100 | B-2-1b
CURR1B | LING1R | 8.323 | 5.335 | Composite | 0.7972 | 2.2773 | 6.5941 | 132 | 123 | 106 | 123 | B-2-1b
DESA1Q | NECU1- | 6.4 | 4.3 | Composite | 0.5652 | 1.7993 | 6.3388 | 167 | 160 | 147 | 160 | B-2-1b
DRUM2Q | WIYH2- | 2.46 | 0.29 | Composite | 0.0113 | 0.1081 | 3.8932 | 120 | 120 | 120 | 120 | B-2-1b
EKIL2R | EKIL2T | 5.17 | 0.108 | Composite | 0.0141 | 0.186 | 2.1213 | 480 | 405 | 405 | 405 | B-2-1b
GARE1S | WIYH1- | 35.082 | 0.33 | Composite | 3.1938 | 7.8537 | 2.4208 | 109 | 105 | 101 | 105 | B-2-1b
GARE1T | WIYH1- | 34.74 | 0.162 | Composite | 3.1552 | 7.7595 | 2.0813 | 109 | 105 | 101 | 105 | B-2-1b
GOVA1Q | PAIS1Q | 4.52 | 4.03 | Composite | 0.2635 | 1.0894 | 8.2673 | 125 | 113 | 110 | 113 | B-2-1b
HELE1R | WIYH1- | 24.799 | 0.182 | Composite | 2.2553 | 5.5463 | 1.6125 | 109 | 105 | 101 | 105 | B-2-1b
HUNF1Q | KILW1R | 12.85 | 3.06 | Composite | 0.6044 | 3.1854 | 6.863 | 146 | 146 | 145 | 146 | B-2-1b
HUNF1R | SACO1R | 8.572 | 3.04 | Composite | 0.4215 | 2.2374 | 6.6019 | 146 | 146 | 145 | 146 | B-2-1b
KIER1Q | WIYH1- | 2.089 | 4.183 | Composite | 0.3881 | 0.9293 | 7.6166 | 100 | 80 | 60 | 80 | B-2-1b
KIER1R | WIYH1- | 2.089 | 4.095 | Composite | 0.3833 | 0.9197 | 7.4586 | 100 | 80 | 60 | 80 | B-2-1b
LAMB2- | PORD2R | 3.94 | 0.177 | Composite | 0.0192 | 0.1721 | 2.1551 | 300 | 300 | 300 | 300 | B-2-1b
MAYB1- | MAYT1T | 12.59 | 0.31 | Composite | 1.1567 | 3.0101 | 0.9444 | 132 | 123 | 106 | 123 | B-2-1b
NEIL1- | PAIS1Q | 8.29 | 0.29 | Composite | 0.1643 | 1.4877 | 1.704 | 268 | 268 | 268 | 268 | B-2-1b
NEIL1- | PAIS1R | 8.31 | 0.31 | Composite | 0.1648 | 1.493 | 1.7861 | 268 | 268 | 268 | 268 | B-2-1b
POOB2Q | SMEA2- | 7.79 | 0.19 | Composite | 0.0335 | 0.3227 | 2.9788 | 360 | 300 | 240 | 300 | B-2-1b
POOB2R | SMEA2- | 7.79 | 0.19 | Composite | 0.0335 | 0.3227 | 2.9788 | 360 | 300 | 240 | 300 | B-2-1b
STIR1S | WFIE1A | 37.6 | 5.816 | Composite | 3.218 | 9.4053 | 8.7867 | 162 | 154 | 141 | 154 | B-2-1b
STLE1R | WIYH1- | 12.892 | 0.291 | Composite | 1.1813 | 2.9041 | 1.2141 | 109 | 105 | 101 | 105 | B-2-1b
ABTH21 | UPPB22 | 27.035 | 0.547 | Composite | 0.1245 | 1.1595 | 13.2801 | 772 | 772 | 595 | 595 | B-2-1c
AXMI41 | CHIC4A | 30.7 | 8.8 | Composite | 0.0379 | 0.6609 | 130.8219 | 2779 | 2568 | 2217 | 2568 | B-2-1c
BAGB21 | MAGA21 | 12.629 | 1.389 | Composite | 0.0435 | 0.5216 | 17.0509 | 1204 | 1115 | 1018 | 1115 | B-2-1c
BAGB21 | SWAN21 | 18.21 | 1.439 | Composite | 0.0625 | 0.7488 | 19.1165 | 1548 | 1548 | 1431 | 1431 | B-2-1c
BEDD21 | CHSI21 | 17.836 | 0.286 | Composite | 0.068 | 0.7365 | 7.9729 | 944 | 882 | 762 | 835 | B-2-1c
BEDD21 | WIMB21 | 8.5 | 0.968 | Composite | 0.0409 | 0.3915 | 11.7005 | 859 | 827 | 623 | 694 | B-2-1c
BEDD22 | CHSI21 | 17.836 | 0.137 | Composite | 0.0677 | 0.7328 | 6.4221 | 762 | 762 | 662 | 662 | B-2-1c
BEDD23 | WIMB21 | 8.5 | 0.582 | Composite | 0.0398 | 0.3821 | 8.4754 | 995 | 930 | 728 | 806 | B-2-1c
BESW21 | OCKH21 | 56.939 | 0.731 | Composite | 0.2318 | 2.4208 | 22.7971 | 819 | 819 | 638 | 638 | B-2-1c
BRAW21 | ELLA21 | 16.802 | 0.081 | Composite | 0.0769 | 0.7134 | 5.4384 | 762 | 762 | 619 | 619 | B-2-1c
BRAW21 | KIRK21 | 17.279 | 4.547 | Composite | 0.0844 | 0.855 | 54.1379 | 762 | 762 | 619 | 619 | B-2-1c
BRED21 | SMAN21 | 10.004 | 5.629 | Composite | 0.0513 | 0.4604 | 46.762 | 865 | 865 | 749 | 749 | B-2-1c
BRFO41 | DISS4A | 31.4 | 0.1 | Composite | 0.0279 | 0.5404 | 23.1059 | 3326 | 3326 | 3326 | 3326 | B-2-1c
BRFO41 | DISS4B | 31.4 | 0.1 | Composite | 0.0279 | 0.5404 | 23.1059 | 3326 | 3326 | 3326 | 3326 | B-2-1c
BRIN21 | JORD21 | 13.257 | 1.489 | Composite | 0.0647 | 0.5918 | 16.0432 | 557 | 557 | 499 | 499 | B-2-1c
BRIN21 | NORL2A | 13.257 | 2.845 | Composite | 0.0708 | 0.6085 | 24.8202 | 419 | 419 | 381 | 381 | B-2-1c
BRLE41 | DIDC41 | 37.691 | 5.7 | Composite | 0.0419 | 0.6724 | 87.0663 | 2779 | 2568 | 2217 | 2245 | B-2-1c
BRLE41 | DIDC41 | 37.691 | 5.7 | Composite | 0.0419 | 0.6719 | 134.3668 | 2277 | 2277 | 2037 | 2037 | B-2-1c
BRWA42 | BRWA4B | 4 | 0.462 | Composite | 0.0076 | 0.085 | 7.3611 | 2030 | 1930 | 1770 | 1930 | B-2-1c
BUSH21 | WIEN2B | 5.197 | 4.318 | Composite | 0.0311 | 0.3404 | 48.3427 | 762 | 762 | 681 | 681 | B-2-1c
BUST21 | NECH21 | 2.648 | 7.619 | Composite | 0.026 | 0.3163 | 76.3606 | 725 | 713 | 599 | 635 | B-2-1c
BUST21 | NECH21 | 2.648 | 7.648 | Composite | 0.026 | 0.3169 | 76.528 | 725 | 713 | 599 | 635 | B-2-1c
CARR21 | SMAN21 | 9.294 | 0.133 | Composite | 0.0414 | 0.4101 | 3.8882 | 835 | 835 | 665 | 665 | B-2-1c
CARR21 | SMAN21 | 10.747 | 0.23 | Composite | 0.0475 | 0.476 | 5.3274 | 835 | 835 | 665 | 665 | B-2-1c
CELL41 | DAIN41 | 53.412 | 2.31 | Composite | 0.0842 | 1.0314 | 76.8805 | 2508 | 2508 | 2300 | 2300 | B-2-1c
CHIC41 | EXET41 | 67.12 | 8.8 | Composite | 0.0786 | 1.3565 | 152.8884 | 2779 | 2568 | 2217 | 2568 | B-2-1c
CHIL41 | LOVE41 | 22.379 | 0.315 | Composite | 0.0201 | 0.389 | 20.2483 | 1109 | 1109 | 901 | 901 | B-2-1c
CHUE4A | TILB41 | 13.045 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2827 | 2827 | 2591 | 2591 | B-2-1c
CHUE4B | TILB41 | 13.045 | 0.48 | Composite | 0.0207 | 0.2569 | 13.0341 | 2924 | 2924 | 2591 | 2591 | B-2-1c
COVE21 | RATS2A | 64.863 | 0.5 | Composite | 0.1812 | 2.5694 | 23.9446 | 1000 | 1000 | 1000 | 1000 | B-2-1c
DAIN41 | MACC41 | 33.593 | 2.4 | Composite | 0.0535 | 0.6515 | 66.7385 | 2397 | 2302 | 2144 | 2300 | B-2-1c
DRAK41 | OLDB4A | 48.818 | 0.5 | Composite | 0.0921 | 0.9799 | 36.5074 | 1169 | 1169 | 1068 | 1068 | B-2-1c
EGGB41 | ROCH4A | 84.875 | 0.7 | Composite | 0.1416 | 1.6214 | 64.456 | 1239 | 1239 | 1122 | 1122 | B-2-1c
EGGB41 | THOM41 | 28.07 | 0.197 | Composite | 0.0293 | 0.4897 | 21.8489 | 2217 | 2217 | 1801 | 1801 | B-2-1c
ELLA21 | KIRK21 | 33.995 | 5.044 | Composite | 0.1618 | 1.5765 | 64.0738 | 762 | 762 | 619 | 619 | B-2-1c
ELST21 | MILH2A | 6.375 | 6.338 | Composite | 0.0548 | 0.3963 | 55.677 | 524 | 524 | 430 | 430 | B-2-1c
ELST21 | MILH2B | 6.375 | 6.282 | Composite | 0.0546 | 0.3952 | 55.2004 | 524 | 524 | 430 | 430 | B-2-1c
ELST21 | WARL21 | 59.208 | 0.261 | Composite | 0.2449 | 2.4665 | 19.2619 | 762 | 762 | 619 | 619 | B-2-1c
ELST21 | WATS21 | 5.398 | 0.399 | Composite | 0.0254 | 0.2396 | 5.8016 | 762 | 762 | 619 | 619 | B-2-1c
ELST22 | WARL21 | 59.244 | 0.59 | Composite | 0.2456 | 2.4772 | 22.8481 | 762 | 762 | 619 | 619 | B-2-1c
ELST22 | WATS22 | 5.398 | 0.222 | Composite | 0.0251 | 0.2347 | 3.8776 | 762 | 762 | 619 | 619 | B-2-1c
FERR21 | SKLG21 | 20.033 | 0.685 | Composite | 0.0991 | 0.9874 | 9.8077 | 865 | 823 | 752 | 823 | B-2-1c
FERR22 | FERR2B | 0.554 | 0.16 | Composite | 0.002 | 0.0234 | 1.3262 | 1031 | 1031 | 981 | 981 | B-2-1c
FERR2B | SKLG21 | 19.545 | 0.56 | Composite | 0.0975 | 0.9671 | 8.7544 | 865 | 823 | 752 | 823 | B-2-1c
FFES21 | TRAW21 | 7.291 | 0.133 | Composite | 0.0771 | 0.3081 | 2.8868 | 551 | 512 | 442 | 512 | B-2-1c
GRAI41 | KEMS41 | 7.992 | 1.93 | Composite | 0.0106 | 0.1512 | 34.7588 | 2643 | 2570 | 2397 | 2570 | B-2-1c
GRAI41 | KEMS41 | 7.992 | 1.93 | Composite | 0.0106 | 0.1512 | 34.7588 | 2643 | 2570 | 2397 | 2570 | B-2-1c
GRST2A | LACK2A | 1.016 | 0.15 | Composite | 0.0049 | 0.0466 | 1.8737 | 1175 | 1119 | 1023 | 1119 | B-2-1c
GRST2A | LACK2B | 1.016 | 0.15 | Composite | 0.0049 | 0.0466 | 1.8737 | 1129 | 1119 | 1000 | 1000 | B-2-1c
GRST2B | LACK2B | 0.63 | 0.15 | Composite | 0.0031 | 0.0298 | 1.7716 | 1129 | 1119 | 1000 | 1000 | B-2-1c
GRST2B | LACK2A | 0.63 | 0.15 | Composite | 0.0031 | 0.0298 | 1.7716 | 1129 | 1119 | 1000 | 1000 | B-2-1c
HAMB4A | PEWO41 | 19.698 | 0.752 | Composite | 0.0308 | 0.3917 | 24.9792 | 2473 | 2473 | 2189 | 2189 | B-2-1c
HAMB4B | PEWO41 | 19.698 | 0.592 | Composite | 0.0308 | 0.3911 | 20.9006 | 2473 | 2473 | 2189 | 2189 | B-2-1c
HAMH41 | WILE41 | 84.14 | 0.7 | Composite | 0.1001 | 1.549 | 78.4627 | 2009 | 1912 | 1746 | 1912 | B-2-1c
HARK23 | STEW21 | 83.682 | 0.117 | Composite | 0.4944 | 3.549 | 23.7211 | 774 | 774 | 676 | 676 | B-2-1c
HINP41 | SAFO41 | 26.58 | 8.94 | Composite | 0.0421 | 0.5573 | 218.3267 | 2009 | 1911 | 1746 | 1911 | B-2-1c
HINP41 | SEAB41 | 57.813 | 8.99 | Composite | 0.0765 | 1.1045 | 239.9146 | 2009 | 1911 | 1746 | 1911 | B-2-1c
HURS21 | LITT2A | 5.164 | 2.938 | Composite | 0.0279 | 0.3019 | 12.6277 | 864 | 864 | 824 | 861 | B-2-1c
HURS21 | LITT2B | 5.14 | 2.863 | Composite | 0.0277 | 0.2987 | 12.3347 | 864 | 864 | 824 | 861 | B-2-1c
IMPP41 | MELK41 | 78.775 | 3.913 | Composite | 0.0882 | 1.4129 | 130.2038 | 1424 | 1424 | 1424 | 1424 | B-2-1c
IROA21 | MELK2A | 33.683 | 0.38 | Composite | 0.1862 | 1.7591 | 10.7703 | 581 | 581 | 524 | 524 | B-2-1c
IROA21 | MELK2B | 33.683 | 0.951 | Composite | 0.1877 | 1.7704 | 15.6295 | 581 | 581 | 524 | 524 | B-2-1c
IVER21 | WWEY22 | 25.652 | 0.342 | Composite | 0.0975 | 1.059 | 10.9579 | 960 | 960 | 839 | 839 | B-2-1c
IVER22 | WATS21 | 13.881 | 0.483 | Composite | 0.0643 | 0.601 | 9.0158 | 776 | 776 | 631 | 631 | B-2-1c
IVER22 | WATS22 | 13.881 | 0.436 | Composite | 0.0642 | 0.5997 | 8.5049 | 776 | 776 | 631 | 631 | B-2-1c
IVER2A | LALE21 | 17.186 | 0.402 | Composite | 0.0656 | 0.7143 | 9.2206 | 841 | 841 | 665 | 665 | B-2-1c
KEAR21 | WHGA21 | 14.509 | 0.241 | Composite | 0.0667 | 0.6208 | 6.5558 | 835 | 835 | 665 | 665 | B-2-1c
KEAR21 | WHGA21 | 14.509 | 0.129 | Composite | 0.0665 | 0.6177 | 5.3384 | 213 | 213 | 289 | 289 | B-2-1c
KITW21 | OLDB21 | 7.704 | 0.597 | Composite | 0.0301 | 0.3318 | 8.6639 | 667 | 667 | 619 | 619 | B-2-1c
KITW21 | OLDB2A | 8.278 | 0.222 | Composite | 0.0317 | 0.3449 | 4.7492 | 772 | 772 | 619 | 619 | B-2-1c
LACK41 | SALH41 | 10.237 | 0.25 | Composite | 0.0184 | 0.2024 | 10.54 | 1831 | 1739 | 1588 | 1739 | B-2-1c
LACK41 | THTO41 | 92.075 | 5.7 | Composite | 0.1057 | 1.6537 | 264.9969 | 2418 | 2418 | 2030 | 2030 | B-2-1c
LACK41 | THTO42 | 92.075 | 5.7 | Composite | 0.1057 | 1.6537 | 264.9969 | 2418 | 2418 | 2030 | 2030 | B-2-1c
LITT41 | WTHU4E | 1.847 | 1.853 | Composite | 0.0041 | 0.0575 | 21.3295 | 1936 | 1883 | 1666 | 1815 | B-2-1c
LITT41 | WTHU4F | 1.847 | 1.853 | Composite | 0.0041 | 0.0575 | 21.3295 | 1936 | 1883 | 1666 | 1815 | B-2-1c
NEEP21 | PITS21 | 0.851 | 3.975 | Composite | 0.0214 | 0.1378 | 26.8236 | 419 | 419 | 381 | 381 | B-2-1c
NEEP21 | SHEC21 | 0.851 | 4.428 | Composite | 0.0234 | 0.1494 | 29.8542 | 419 | 419 | 381 | 381 | B-2-1c
OCKH21 | WIEN2A | 4.623 | 0.283 | Composite | 0.0216 | 0.202 | 4.2819 | 672 | 672 | 599 | 599 | B-2-1c
RASS41 | WALH41 | 72.788 | 5.269 | Composite | 0.0799 | 1.2847 | 109.6583 | 2779 | 2568 | 2217 | 2568 | B-2-1c
RATS41 | WILE41 | 21.748 | 0.216 | Composite | 0.0397 | 0.435 | 16.174 | 1309 | 1309 | 1067 | 1067 | B-2-1c
REBR21 | TOTT23 | 3.305 | 9.678 | Composite | 0.0166 | 0.2027 | 106.1327 | 1205 | 1127 | 1044 | 1127 | B-2-1c
REBR22 | TOTT24 | 3.305 | 11.448 | Composite | 0.0174 | 0.2151 | 125.3726 | 1205 | 1127 | 1044 | 1127 | B-2-1c
ROCH21 | WHGA21 | 11.489 | 0.257 | Composite | 0.053 | 0.4934 | 5.9105 | 841 | 841 | 665 | 665 | B-2-1c
ROCH21 | WHGA21 | 11.489 | 0.238 | Composite | 0.0529 | 0.4929 | 5.7039 | 419 | 419 | 404 | 404 | B-2-1c
SEAB41 | WHSO4A | 30.426 | 3.89 | Composite | 0.0374 | 0.5858 | 97.4265 | 1424 | 1424 | 1424 | 1424 | B-2-1c
STAL4A | THOM41 | 69.271 | 6.952 | Composite | 0.0793 | 1.2727 | 151.2452 | 1442 | 1442 | 1314 | 1314 | B-2-1c
STAL4B | STSB4A | 26.581 | 7.031 | Composite | 0.0345 | 0.532 | 124.2199 | 1436 | 1436 | 1308 | 1308 | B-2-1c
THOM21 | WMEL21 | 23.791 | 0.947 | Composite | 0.1105 | 1.0548 | 15.8849 | 764 | 764 | 698 | 698 | B-2-1c
THOM2A | WMEL21 | 24.413 | 0.8 | Composite | 0.1126 | 1.0793 | 10.588 | 955 | 882 | 762 | 882 | B-2-1c
GARB1Q | SLOY1K | 14.229 | 0.671 | Composite | 0.7599 | 3.3376 | 0.775 | 241 | 230 | 210 | 230 | B-2-2a | 2025 | Change
GARB1R | SLOY1J | 14.185 | 0.715 | Composite | 0.7599 | 3.3376 | 0.775 | 241 | 230 | 210 | 230 | B-2-2a | 2025 | Change
GARB1S | SLOY1J | 14.229 | 0.671 | Composite | 0.7599 | 3.3376 | 0.775 | 241 | 230 | 210 | 230 | B-2-2a | 2025 | Change
GARB1T | SLOY1K | 14.185 | 0.715 | Composite | 0.7599 | 3.3376 | 0.775 | 241 | 230 | 210 | 230 | B-2-2a | 2025 | Change
CONN2J | LOCB2J | 76.071 | 0.269 | Composite | 0.458 | 4.1987 | 16.184 | 780 | 750 | 700 | 750 | B-2-2a | 2027 | Change
AREX1A | MAHI1B | 7.5 | 0.5 | Composite | 0.5731 | 1.6545 | 1.2722 | 365 | 360 | 350 | 360 | B-2-2b | 2025 | Addition
CLYS3A | WHBR3A | 13.1 | 2.5 | Composite | 16.4566 | 43.5395 | 0.3436 | 42 | 40 | 36 | 40 | B-2-2b | 2025 | Addition
CLYS3B | WHBR3B | 13.1 | 2.5 | Composite | 17.1837 | 42.3511 | 0.2892 | 42 | 40 | 36 | 40 | B-2-2b | 2025 | Addition
CROO1Q | NEIL1- | 12.56 | 0.22 | Composite | 0.4737 | 2.7011 | 0.9855 | 229 | 211 | 183 | 211 | B-2-2b | 2025 | Change
CROO1R | NEIL1- | 12.56 | 0.23 | Composite | 0.4738 | 2.702 | 0.9994 | 229 | 211 | 183 | 211 | B-2-2b | 2025 | Change
MOFF1- | SCOP1- | 2.5 | 0.3 | Composite | 0.1924 | 0.5661 | 0.6908 | 293 | 293 | 293 | 293 | B-2-2b | 2025 | Addition
MOFF1A | SCOP1A | 2.5 | 0.3 | Composite | 0.1924 | 0.5661 | 0.6908 | 293 | 293 | 293 | 293 | B-2-2b | 2025 | Addition
MOFF1A | SCOP1A | 2.5 | 0.3 | Composite | 0.1924 | 0.5661 | 0.6908 | 293 | 293 | 293 | 293 | B-2-2b | 2025 | Addition
CHAP1- | OFOA1T | 24.82 | 0.18 | Composite | 0.984 | 5.6173 | 1.5274 | 171 | 155 | 155 | 155 | B-2-2b | 2027 | Addition
CLAW1- | DESA1Q | 6.4 | 2.3 | Composite | 0.5256 | 1.6179 | 3.5471 | 167 | 160 | 147 | 160 | B-2-2b | 2027 | Addition
DUNF1Q | INKE1Q | 7.58 | 0.09 | Composite | 0.5757 | 1.7891 | 0.5513 | 132 | 122 | 106 | 122 | B-2-2b | 2027 | Change
DUNF1R | INKE1R | 7.58 | 0.09 | Composite | 0.5757 | 1.7891 | 0.5513 | 132 | 122 | 106 | 122 | B-2-2b | 2027 | Change
EAST1Q | GLLE1- | 1.5 | 0.3 | Composite | 0.1236 | 0.3498 | 0.4484 | 133 | 124 | 107 | 124 | B-2-2b | 2027 | Addition
GLLE1- | WNUK1- | 17 | 0.5 | Composite | 1.2996 | 3.7201 | 1.6799 | 200 | 200 | 200 | 200 | B-2-2b | 2027 | Addition
GNSH1- | KEOO1Q | 10.1 | 0.9 | Composite | 0.7816 | 2.2655 | 2.0167 | 272 | 231 | 231 | 231 | B-2-2b | 2027 | Addition
KILS2- | KILT2Q | 3.56 | 0.29 | Composite | 0.0165 | 0.1465 | 2.1425 | 204 | 177 | 177 | 177 | B-2-2b | 2027 | Change
KILS2- | KILT2R | 3.56 | 0.33 | Composite | 0.0168 | 0.1474 | 2.2967 | 204 | 177 | 177 | 177 | B-2-2b | 2027 | Change
BLAH1- | GLGL1Q | 13.6 | 0.375 | Composite | 0.5207 | 2.9382 | 1.1932 | 181 | 164 | 164 | 164 | B-2-2b | 2029 | Change
BLAH1- | GLGL1R | 13.6 | 0.375 | Composite | 0.5207 | 2.9382 | 1.1932 | 181 | 164 | 164 | 164 | B-2-2b | 2029 | Change
BRAP1- | ERSK1Q | 3.17 | 5.4 | Composite | 0.3985 | 1.1026 | 12.4454 | 121 | 110 | 106 | 110 | B-2-2b | 2029 | Change
BRAP1- | ERSK1R | 3.45 | 6.23 | Composite | 0.4418 | 1.1771 | 12.9647 | 102 | 79 | 79 | 79 | B-2-2b | 2029 | Change
CHAP1- | GRNA1- | 12.83 | 0.35 | Composite | 0.7983 | 3.0495 | 1.0029 | 144 | 144 | 144 | 144 | B-2-2b | 2029 | Change
CHAP1- | GRNA1- | 12.83 | 0.3 | Composite | 0.797 | 3.0442 | 0.9509 | 144 | 144 | 144 | 144 | B-2-2b | 2029 | Change
CLFO1- | CURR1A | 27 | 1.6 | Composite | 2.1169 | 6.0497 | 3.3907 | 133 | 124 | 107 | 124 | B-2-2b | 2029 | Addition
COAL1A | KENN1- | 16 | 3.4 | Composite | 1.2963 | 3.7441 | 5.0291 | 167 | 160 | 148 | 160 | B-2-2b | 2029 | Change
CRDY3A | EWEH3- | 4.736 | 0.35 | Composite | 3.8899 | 14.1591 | 0.06 | 38 | 38 | 38 | 38 | B-2-2b | 2029 | Change
CRDY3B | EWEH3- | 4.775 | 0.35 | Composite | 3.9211 | 14.2732 | 0.0602 | 38 | 38 | 38 | 38 | B-2-2b | 2029 | Change
CURR2- | SIGH2Q | 1.54 | 1.7 | Composite | 0.0169 | 0.1036 | 6.0402 | 120 | 120 | 120 | 120 | B-2-2b | 2029 | Change
CURR2- | SIGH2R | 1.54 | 1.67 | Composite | 0.0168 | 0.103 | 5.941 | 120 | 120 | 120 | 120 | B-2-2b | 2029 | Change
DAER1- | MOFF1A | 6.1 | 6.8 | Composite | 0.6601 | 1.7847 | 8.6959 | 133 | 124 | 107 | 124 | B-2-2b | 2029 | Addition
DEVO1- | STIR1T | 5.8 | 5.816 | Composite | 0.3236 | 1.8724 | 7.2413 | 162 | 154 | 141 | 154 | B-2-2b | 2029 | Change
DUNB1Q | INWI1Q | 7.8 | 3.7 | Composite | 0.8335 | 1.9723 | 8.1951 | 102 | 91 | 91 | 91 | B-2-2b | 2029 | Change
DUNB1R | INWI1R | 7.8 | 3.7 | Composite | 0.8335 | 1.9723 | 8.1951 | 102 | 91 | 91 | 91 | B-2-2b | 2029 | Change
ELDE1Q | NEIL1- | 3.82 | 0.18 | Composite | 0.1455 | 0.8324 | 0.4574 | 229 | 211 | 183 | 211 | B-2-2b | 2029 | Change
ELDE1R | NEIL1- | 3.82 | 0.23 | Composite | 0.1461 | 0.8373 | 0.5271 | 229 | 211 | 183 | 211 | B-2-2b | 2029 | Change
EWEH1Q | GRNA1- | 15.9 | 0.36 | Composite | 1.2138 | 3.4754 | 1.4335 | 241 | 241 | 241 | 241 | B-2-2b | 2029 | Change
GLNI1- | MOSM1A | 1.41 | 0.09 | Composite | 0.0651 | 0.2344 | 0.3797 | 229 | 229 | 229 | 229 | B-2-2b | 2029 | Change
GLNI1- | MOSM1B | 1.41 | 0.11 | Composite | 0.0654 | 0.2362 | 0.4421 | 171 | 171 | 171 | 171 | B-2-2b | 2029 | Change
HLND1- | WISH1- | 17 | 1.01 | Composite | 1.3056 | 3.8061 | 2.1392 | 167 | 160 | 148 | 160 | B-2-2b | 2029 | Addition
KNOK1- | MAHI1C | 2.5 | 0.5 | Composite | 0.1407 | 0.5692 | 0.9179 | 241 | 230 | 210 | 230 | B-2-2b | 2029 | Addition
MAHI3- | TRLO3- | 8.722 | 5.5 | Composite | 12.1114 | 32.1139 | 0.6017 | 25 | 25 | 25 | 25 | B-2-2b | 2029 | Change
BODE41 | CONQ41 | 30.717 | 0.21 | Composite | 0.0335 | 0.5367 | 22.5401 | 2665 | 2561 | 2217 | 2561 | B-2-2c | 2027 | Addition
BODE41 | CONQ41 | 30.717 | 0.21 | Composite | 0.0335 | 0.5367 | 22.5401 | 2665 | 2561 | 2217 | 2561 | B-2-2c | 2027 | Addition
BODE41 | PENT41 | 49.211 | 0.8 | Composite | 0.0653 | 0.9665 | 36.8939 | 2779 | 2568 | 2217 | 2568 | B-2-2c | 2027 | Addition
BODE41 | PENT41 | 49.211 | 0.8 | Composite | 0.0653 | 0.9665 | 36.8939 | 2779 | 2568 | 2217 | 2568 | B-2-2c | 2027 | Addition
BRIM2A | TOTT21 | 7.437 | 0.311 | Composite | 0.025 | 0.3106 | 5.4901 | 2310 | 2100 | 2030 | 2100 | B-2-2c | 2027 | Addition
BRIM2B | TOTT22 | 7.305 | 0.393 | Composite | 0.0247 | 0.3075 | 6.344 | 2310 | 2100 | 2030 | 2100 | B-2-2c | 2027 | Change
BRIM4C | HACK41 | 13.209 | 0.527 | Composite | 0.0209 | 0.2597 | 13.6792 | 3100 | 3100 | 3100 | 3100 | B-2-2c | 2027 | Addition
BRIM4D | HACK41 | 13.209 | 0.676 | Composite | 0.021 | 0.2614 | 15.3056 | 3100 | 3100 | 3100 | 3100 | B-2-2c | 2027 | Addition
KINO41 | WALE41 | 9.467 | 0.8 | Composite | 0.0104 | 0.1673 | 17.2184 | 3326 | 3160 | 2633 | 2813 | B-2-2c | 2027 | Addition
MFSN21 | TADT2B | 14.18 | 0.6 | Composite | 0.0705 | 0.6359 | 10.1219 | 1500 | 1500 | 1300 | 1500 | B-2-2c | 2027 | Addition
NORT41 | SPEN41 | 21.134 | 2 | Composite | 0.0276 | 0.4062 | 12.7287 | 2810 | 2700 | 2510 | 2700 | B-2-2c | 2027 | Change
NORT41 | SPEN42 | 21.134 | 2 | Composite | 0.0276 | 0.4062 | 12.7287 | 2810 | 2700 | 2510 | 2700 | B-2-2c | 2027 | Change
SPEN41 | STEW41 | 37.795 | 0.126 | Composite | 0.0498 | 0.7386 | 24.4993 | 2780 | 2670 | 2480 | 2670 | B-2-2c | 2027 | Change
SWAN41 | WALH41 | 133.752 | 5.468 | Composite | 0.146 | 2.3458 | 152.0578 | 2779 | 2568 | 2217 | 2568 | B-2-2c | 2027 | Addition
BARK41 | WHAM41 | 9.662 | 0.124 | Composite | 0.0151 | 0.1915 | 10.4342 | 3100 | 3100 | 3100 | 3100 | B-2-2c | 2029 | Change
BRAI4A | BRFO41 | 41 | 8 | Composite | 0.0441 | 0.8075 | 127.9671 | 3326 | 3326 | 3320 | 3326 | B-2-2c | 2029 | Addition
BRAI4B | BRFO41 | 41 | 8 | Composite | 0.0442 | 0.8076 | 127.9635 | 3326 | 3326 | 3320 | 3326 | B-2-2c | 2029 | Addition
BRIN41 | CHTE41 | 22.464 | 0.22 | Composite | 0.0245 | 0.3933 | 17.2091 | 2810 | 2700 | 2510 | 2700 | B-2-2c | 2029 | Addition
BRLE41 | MELK41 | 77.5 | 4.4 | Composite | 0.1014 | 1.4577 | 154.835 | 2830 | 2770 | 2680 | 2770 | B-2-2c | 2029 | Change
BRLE41 | MELK41 | 77.5 | 4.4 | Composite | 0.1029 | 1.4603 | 101.331 | 2830 | 2770 | 2680 | 2770 | B-2-2c | 2029 | Change
COTT41 | HIMB41 | 7.099 | 0.25 | Composite | 0.0113 | 0.1388 | 9.876 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Addition
COWL41 | MITY41 | 100.105 | 2.092 | Composite | 0.1293 | 1.8315 | 98.6831 | 1180 | 1132 | 877 | 979 | B-2-2c | 2029 | Change
COWL41 | WALH41 | 89.553 | 2.092 | Composite | 0.1112 | 1.627 | 92.3926 | 1180 | 1132 | 877 | 979 | B-2-2c | 2029 | Change
FECK41 | MITY41 | 65.268 | 7.5 | Composite | 0.0997 | 1.2484 | 222.0437 | 2830 | 2770 | 2680 | 2770 | B-2-2c | 2029 | Change
FECK41 | WALH41 | 55.11 | 7.5 | Composite | 0.082 | 1.0511 | 215.9994 | 2830 | 2770 | 2680 | 2770 | B-2-2c | 2029 | Change
FOUX41 | TRAW41 | 14.128 | 9.54 | Composite | 0.0248 | 0.3917 | 231.479 | 1830 | 1830 | 1830 | 1830 | B-2-2c | 2029 | Addition
GRAI41 | TILB41 | 26.642 | 2.049 | Composite | 0.0267 | 0.4794 | 61.4717 | 2950 | 2950 | 2950 | 2950 | B-2-2c | 2029 | Change
HIMB41 | WBUR41 | 14.852 | 0.229 | Composite | 0.0224 | 0.2868 | 17.1381 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Addition
KINO41 | TILB41 | 15.478 | 1.835 | Composite | 0.0149 | 0.2859 | 47.1231 | 2950 | 2950 | 2950 | 2950 | B-2-2c | 2029 | Change
MARV4B | SUND42 | 13.955 | 1 | Composite | 0.0218 | 0.2688 | 8.3345 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Change
PENT41 | TRAW41 | 41.698 | 9.71 | Composite | 0.0611 | 0.9304 | 251.71 | 1830 | 1830 | 1830 | 1830 | B-2-2c | 2029 | Change
RATS41 | STOB41 | 26.72 | 0.179 | Composite | 0.0451 | 0.5238 | 21.6497 | 3100 | 3050 | 2960 | 3050 | B-2-2c | 2029 | Change
DRAX41 | EGGB42 | 11.188 | 0.64 | Composite | 0.0129 | 0.1991 | 15.0423 | 2973 | 2778 | 2447 | 2778 | B-2-2c | 2030 | Change

## Series Capacitor
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Sheet_Name | Year | Status
ECCL4A | ECCL4C | 0 | 0 | Series Capacitor | 0 | 0.575 | 0 | 2771 | 2771 | 2771 | 2771 | B-2-1b
ECCL4B | ECCL4D | 0 | 0 | Series Capacitor | 0 | 0.575 | 0 | 2771 | 2771 | 2771 | 2771 | B-2-1b
GRNA4- | GRNA4C | 0 | 0 | Series Capacitor | 0 | 0.729 | 0 | 2771 | 2771 | 2771 | 2771 | B-2-1b
MOFF4- | MOFF4C | 0 | 0 | Series Capacitor | 0 | 0.729 | 0 | 2771 | 2771 | 2771 | 2771 | B-2-1b
HUTT41 | HUTT42 | 0 | 0 | Series Capacitor | 0 | 0.5114 | 0 | 2771 | 2771 | 2771 | 2771 | B-2-1c
HUTT41 | HUTT43 | 0 | 0 | Series Capacitor | 0 | 0.5114 | 0 | 2771 | 2771 | 2771 | 2771 | B-2-1c

## Series Reactor
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Sheet_Name | Year | Status
EKIL3A | EKIL3B | 0 | 0 | Series Reactor | 0.5744 | 108.498 | 0 | 30 | 30 | 30 | 30 | B-2-1b
KAIM3- | KAIM3A | 0 | 0 | Series Reactor | 0.0625 | 13.5546 | 0 | 120 | 120 | 120 | 120 | B-2-1b
KAIM3- | KAIM3B | 0 | 0 | Series Reactor | 0.0624 | 13.55 | 0 | 120 | 120 | 120 | 120 | B-2-1b
WIYH2- | WIYH2R | 0 | 0 | Series Reactor | 0.005 | 1.5 | 0 | 1000 | 1000 | 1000 | 1000 | B-2-1b
DIDC41 | DIDC41 | 0 | 0 | Series Reactor | 0.0063 | 0.5 | 0 | 2640 | 2640 | 2640 | 2640 | B-2-1c
DRAX41 | DRAX42 | 0 | 0 | Series Reactor | 0.006 | 2 | 0 | 1320 | 1320 | 1320 | 1320 | B-2-1c
FIDF21 | FIDF21 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 750 | 750 | 750 | B-2-1c
FIDF21 | FIDF21 | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 750 | 750 | 750 | 750 | B-2-1c
GRAI41 | GRAI41 | 0 | 0 | Series Reactor | 0.0027 | 2.3091 | 0 | 2002 | 2002 | 2002 | 2002 | B-2-1c
LISD21 | LISD2A | 0 | 0 | Series Reactor | 0.0173 | 1.387 | 0 | 750 | 750 | 740 | 740 | B-2-1c
SELL4A | SELL4A | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 1860 | 1860 | 1860 | 1860 | B-2-1c
SHUR41 | SHUR41 | 0 | 0 | Series Reactor | 0 | 2 | 0 | 2400 | 2400 | 2400 | 2400 | B-2-1c
WBUR41 | WBUR42 | 0 | 0 | Series Reactor | 0.0026 | 2.3169 | 0 | 1500 | 1500 | 1500 | 1500 | B-2-1c
WTHU4C | WTHU4E | 0 | 0 | Series Reactor | 0 | 1 | 0 | 2400 | 2400 | 2400 | 2400 | B-2-1c
WTHU4D | WTHU4F | 0 | 0 | Series Reactor | 0 | 1 | 0 | 2400 | 2400 | 2400 | 2400 | B-2-1c
ELST41 | ELST4B | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 2000 | 2000 | 2000 | 2000 | B-2-2c | 2029 | Addition
ELST41 | ELST4B | 0 | 0 | Series Reactor | 0.0125 | 1 | 0 | 2000 | 2000 | 2000 | 2000 | B-2-2c | 2029 | Addition

## SSSC
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Sheet_Name | Year | Status
BLYT21 | BLYT22 | 0 | 0 | SSSC | 0 | 1.5868 | 0 | 1360 | 1307 | 1217 | 1307 | B-2-1c
BLYT21 | BLYT23 | 0 | 0 | SSSC | 0 | 1.5868 | 0 | 1360 | 1307 | 1217 | 1307 | B-2-1c
KEAD43 | KEAD44 | 0 | 0 | SSSC | 0 | 0.25 | 0 | 3326 | 3159 | 2971 | 3159 | B-2-1c
PEWO2A | PEWO2C | 0 | 0 | SSSC | 0 | 0.476 | 0 | 1521 | 1461 | 1360 | 1461 | B-2-1c
PEWO2B | PEWO2D | 0 | 0 | SSSC | 0 | 0.476 | 0 | 1521 | 1461 | 1360 | 1461 | B-2-1c
SALH41 | SALH42 | 0 | 0 | SSSC | 0 | 0.125 | 0 | 1831 | 1739 | 1588 | 1739 | B-2-2c | 2025 | Addition

## Zero Length
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Sheet_Name | Year | Status
EASO41 | EASO4A | 0 | 0 | Zero Length | 0 | 0 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1c
EASO41 | EASO4B | 0 | 0 | Zero Length | 0 | 0 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1c
GRAI41 | GRAI41 | 0 | 0 | Zero Length | 0 | 0 | 0 | 3326 | 3159 | 2971 | 3159 | B-2-1c
GRAI41 | GRAI41 | 0 | 0 | Zero Length | 0 | 0 | 0 | 3326 | 3159 | 2971 | 3159 | B-2-1c
GRAI41 | GRAI41 | 0 | 0 | Zero Length | 0 | 0 | 0 | 3326 | 3159 | 2971 | 3159 | B-2-1c
HAWP21 | HAWP2A | 0 | 0 | Zero Length | 0 | 0 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-1c
MANN41 | MANN41 | 0 | 0 | Zero Length | 0 | 0 | 0 | 3326 | 3159 | 2971 | 3159 | B-2-1c
MANN41 | MANN41 | 0 | 0 | Zero Length | 0 | 0 | 0 | 3326 | 3159 | 2971 | 3159 | B-2-1c
MARH41 | MARH4A | 0 | 0 | Zero Length | 0 | 0 | 0 | 2860 | 2860 | 2860 | 2860 | B-2-1c
MARH42 | MARH4B | 0 | 0 | Zero Length | 0 | 0 | 0 | 2860 | 2860 | 2860 | 2860 | B-2-1c
TOTT2A | TOTT22 | 0 | 0 | Zero Length | 0 | 0 | 0 | 904 | 904 | 904 | 904 | B-2-1c
TOTT2A | TOTT24 | 0 | 0 | Zero Length | 0 | 0 | 0 | 950 | 950 | 830 | 830 | B-2-1c
TOTT2B | TOTT21 | 0 | 0 | Zero Length | 0 | 0 | 0 | 904 | 904 | 904 | 904 | B-2-1c
TOTT2B | TOTT23 | 0 | 0 | Zero Length | 0 | 0 | 0 | 950 | 950 | 830 | 830 | B-2-1c
ALVE41 | ALVE4A | 0 | 0 | Zero Length | 0 | 0 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2c | 2027 | Addition
ALVE41 | ALVE4A | 0 | 0 | Zero Length | 0 | 0 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2c | 2027 | Addition
HARG21 | HARK23 | 0 | 0 | Zero Length | 0 | 0 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2c | 2027 | Addition
HARG2A | HARK24 | 0 | 0 | Zero Length | 0 | 0 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2c | 2027 | Addition
HIGM41 | HIMB41 | 0 | 0 | Zero Length | 0 | 0 | 0 | 9999 | 9999 | 9999 | 9999 | B-2-2c | 2029 | Addition

## Series Compensation
Node 1 | Node 2 | OHL Length (km) | Cable Length (km) | Circuit Type | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Sheet_Name | Year | Status
CELL41 | CELL42 | 0 | 0 | Series Compensation | 0 | 0.375 | 0 | 2420 | 2330 | 2170 | 2330 | B-2-2c | 2027 | Addition
CELL41 | CELL43 | 0 | 0 | Series Compensation | 0 | 0.125 | 0 | 2420 | 2330 | 2170 | 2330 | B-2-2c | 2027 | Addition
COTT42 | COTT43 | 0 | 0 | Series Compensation | 0 | 0.3125 | 0 | 3326 | 3160 | 2971 | 3160 | B-2-2c | 2027 | Addition

## Transformer
Node 1 | Node 2 | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Sheet_Name | Year | Status | Transformer Type
ABNE1Q | ABNE3- | 1.05 | 27.98 | 0 | 60 | B-3-1a |  |  | Transformer
ABNE1R | ABNE3- | 1.05 | 28.5 | 0 | 60 | B-3-1a |  |  | Transformer
ALNE1Q | ALNE3J | 0.365 | 26 | 0 | 120 | B-3-1a |  |  | Transformer
ALNE1R | ALNE3J | 0.365 | 26 | 0 | 120 | B-3-1a |  |  | Transformer
ARDK1- | ARDK3K | 0.807 | 24.876 | 0 | 45 | B-3-1a |  |  | Transformer
ARMO1J | ARMO3- | 0.615 | 17.82 | -0.026 | 60 | B-3-1a |  |  | Transformer
BEAU1J | BEAU2J | 0.6786 | 12.1644 | -0.0009 | 120 | B-3-1a |  |  | Transformer
BEAU1J | BEAU3- | 1.04 | 27.73 | 0 | 45 | B-3-1a |  |  | Transformer
BEAU1K | BEAU3- | 1.04 | 27.73 | 0 | 45 | B-3-1a |  |  | Transformer
BEAU2J | BEAU1J | 0.1486 | 5.3035 | -0.002 | 360 | B-3-1a |  |  | Transformer
BEAU2J | BEAU1J | 0.6786 | 12.1644 | 0 | 120 | B-3-1a |  |  | Transformer
BEAU2K | BEAU1K | 0.1486 | 5.3035 | -0.002 | 360 | B-3-1a |  |  | Transformer
BEAU2K | BEAU1K | 0.1486 | 5.3035 | -0.002 | 360 | B-3-1a |  |  | Transformer
BEAU2K | BEAU4- | 0.0374 | 1.5937 | -0.0004 | 1200 | B-3-1a |  |  | Transformer
BEAU4- | BEAU2J | 0.0376 | 1.5954 | -0.001 | 1200 | B-3-1a |  |  | Transformer
BEAU4- | BEAU2K | 0.0374 | 1.5937 | -0.001 | 1200 | B-3-1a |  |  | Transformer
BEIN11 | BEIN31 | 0.36 | 18 | 0 | 120 | B-3-1a |  |  | Transformer
BERB2Q | BERB3- | 0.42 | 20 | 0 | 120 | B-3-1a |  |  | Transformer
BHLA11 | BHLA31 | 0.36 | 18 | 0 | 120 | B-3-1a |  |  | Transformer
BLHI1J | BLHI2J | 0.1486 | 5.3035 | -0.0006 | 360 | B-3-1a |  |  | Transformer
BLHI1K | BLHI2K | 0.1506 | 5.3034 | -0.0006 | 360 | B-3-1a |  |  | Transformer
BLHI4- | BLHI2J | 0.0264 | 1.5331 | -0.001 | 1200 | B-3-1a |  |  | Transformer
BLHI4- | BLHI2K | 0.0262 | 1.5331 | -0.001 | 1200 | B-3-1a |  |  | Transformer
BOAG1Q | BOAG3- | 0.611 | 24.993 | 0 | 60 | B-3-1a |  |  | Transformer
BOAG1R | BOAG3- | 0.605 | 24.826 | 0 | 60 | B-3-1a |  |  | Transformer
BRID1Q | BRID3- | 0.633 | 28.76 | 0 | 60 | B-3-1a |  |  | Transformer
BRID1R | BRID3- | 0.637 | 28.943 | 0 | 60 | B-3-1a |  |  | Transformer
BROR1- | BROR3- | 0.763 | 25.144 | 0 | 45 | B-3-1a |  |  | Transformer
BUMU1Q | BUMU3- | 0.366 | 25.37 | -0.034 | 90 | B-3-1a |  |  | Transformer
BUMU1R | BUMU3- | 0.376 | 25.42 | -0.035 | 90 | B-3-1a |  |  | Transformer
CAAD1Q | CAAD3- | 0.3042 | 24.7991 | -0.0083 | 120 | B-3-1a |  |  | Transformer
CAAD1Q | CAAD3J | 0.2621 | 24.6736 | -0.0222 | 120 | B-3-1a |  |  | Transformer
CAAD1R | CAAD3- | 0.3042 | 24.7991 | -0.0083 | 120 | B-3-1a |  |  | Transformer
CAAD1R | CAAD3J | 0.2621 | 24.6736 | -0.0222 | 120 | B-3-1a |  |  | Transformer
CAIN2- | CAIN3J | 0.36 | 18 | 0 | 120 | B-3-1a |  |  | Transformer
CASS1Q | CASS3- | 1.518 | 39.871 | 0 | 30 | B-3-1a |  |  | Transformer
CEAN1Q | CEAN5- | 1.182 | 36.714 | 0 | 30 | B-3-1a |  |  | Transformer
CHAR1- | CHAR3- | 0.407 | 26.975 | 0 | 90 | B-3-1a |  |  | Transformer
CHAR1R | CHAR3- | 0.407 | 26.975 | 0 | 90 | B-3-1a |  |  | Transformer
CLAC1Q | CLAC5J | 0.75 | 25 | 0 | 60 | B-3-1a |  |  | Transformer
CLAY1Q | CLAY3- | 0.87 | 24.92 | 0 | 60 | B-3-1a |  |  | Transformer
CLAY1R | CLAY3- | 0.87 | 24.92 | 0 | 60 | B-3-1a |  |  | Transformer
CLUN1Q | CLUN5J | 0.71 | 19.53 | 0 | 60 | B-3-1a |  |  | Transformer
CLUN1R | CLUN5K | 0.71 | 19.55 | 0 | 60 | B-3-1a |  |  | Transformer
COGA1- | COGA3- | 0.324 | 17.9 | 0 | 90 | B-3-1a |  |  | Transformer
CORI1J | CORI3- | 0.5 | 25 | 0 | 90 | B-3-1a |  |  | Transformer
CORI1J | CORI3J | 1 | 20 | 0 | 90 | B-3-1a |  |  | Transformer
COUA1Q | COUA3- | 0.2143 | 25.0741 | -0.0067 | 120 | B-3-1a |  |  | Transformer
COUA1R | COUA3- | 0.2151 | 25.1241 | -0.0092 | 120 | B-3-1a |  |  | Transformer
CRAI1- | CRAI3- | 1.78 | 29.9 | 0 | 30 | B-3-1a |  |  | Transformer
CRAI1Q | CRAI3- | 1.75 | 30.27 | 0 | 30 | B-3-1a |  |  | Transformer
CREA1- | CREA3- | 0.36 | 18 | 0 | 120 | B-3-1a |  |  | Transformer
CRSS1J | CRSS3- | 0.3629 | 18.0297 | -0.0123 | 90 | B-3-1a |  |  | Transformer
DAAS2- | DAAS3- | 0.417 | 20 | 0 | 120 | B-3-1a |  |  | Transformer
DORE11 | DORE31 | 0.21 | 9.89 | 0 | 120 | B-3-1a |  |  | Transformer
DORE12 | DORE32 | 0.21 | 9.89 | 0 | 120 | B-3-1a |  |  | Transformer
DOUN1- | DOUN2- | 0.2112 | 7.7054 | -0.0005 | 240 | B-3-1a |  |  | Transformer
DOUN1- | DOUN2- | 0.2237 | 7.9135 | -0.0006 | 240 | B-3-1a |  |  | Transformer
DUBE1Q | DUBE3- | 1.52 | 39.4 | 0 | 30 | B-3-1a |  |  | Transformer
DUGR1Q | DUGR3- | 0.617 | 17.65 | -0.029 | 60 | B-3-1a |  |  | Transformer
DUNM1- | DUNM3- | 0.172 | 17.9 | 0 | 120 | B-3-1a |  |  | Transformer
DYCE1Q | DYCE3- | 0.4015 | 24.819 | -0.0194 | 90 | B-3-1a |  |  | Transformer
DYCE1R | DYCE3- | 0.3974 | 24.7301 | -0.0007 | 90 | B-3-1a |  |  | Transformer
ELGI1Q | ELGI3- | 0.63 | 27.98 | 0 | 90 | B-3-1a |  |  | Transformer
ELGI1R | ELGI3- | 0.63 | 27.78 | 0 | 90 | B-3-1a |  |  | Transformer
ERRO1J | ERRO5L | 0.72 | 26.6 | 0 | 60 | B-3-1a |  |  | Transformer
ERRO1K | ERRO5J | 0.72 | 26.6 | 0 | 60 | B-3-1a |  |  | Transformer
FAAR1Q | FAAR3J | 0.9 | 28.34 | 0 | 90 | B-3-1a |  |  | Transformer
FAAR1R | FAAR3K | 0.9 | 28.34 | 0 | 90 | B-3-1a |  |  | Transformer
FAUG1- | FAUG4J | 0.2149 | 8.0138 | -0.013 | 240 | B-3-1a |  |  | Transformer
FAUG1- | FAUG4J | 0.3185 | 8.4523 | -0.013 | 240 | B-3-1a |  |  | Transformer
FAUG1J | FAUG4J | 0.108 | 3.957 | -0.0007 | 480 | B-3-1a |  |  | Transformer
FAUG1K | FAUG4K | 0.108 | 3.957 | -0.0007 | 480 | B-3-1a |  |  | Transformer
FAUG1Q | FAUG3- | 0.5 | 25 | 0 | 90 | B-3-1a |  |  | Transformer
FERO1- | FERO3- | 0.3697 | 10.5 | 0 | 90 | B-3-1a |  |  | Transformer
FETT1- | FETT3S | 0.6 | 20 | 0 | 120 | B-3-1a |  |  | Transformer
FIDD1Q | FIDD3- | 0.4567 | 26.23 | 0 | 90 | B-3-1a |  |  | Transformer
FIDD1R | FIDD3- | 0.4562 | 26.084 | 0 | 90 | B-3-1a |  |  | Transformer
FINL1Q | FINL5- | 0.96 | 27.11 | 0 | 45 | B-3-1a |  |  | Transformer
FRAS1Q | FRAS3- | 0.642 | 26.904 | 0 | 45 | B-3-1a |  |  | Transformer
FRAS1R | FRAS3- | 0.642 | 26.904 | 0 | 45 | B-3-1a |  |  | Transformer
FWIL1Q | FWIL3- | 0.499 | 24.995 | 0 | 120 | B-3-1a |  |  | Transformer
FWIL1R | FWIL3- | 0.499 | 24.995 | 0 | 120 | B-3-1a |  |  | Transformer
FYRI1J | FYRI2J | 0.0967 | 3.8863 | -0.0006 | 480 | B-3-1a |  |  | Transformer
FYRI1K | FYRI2K | 0.0971 | 3.8738 | -0.0006 | 480 | B-3-1a |  |  | Transformer
GLDO1G | GLDO8- | 0.206 | 10.681 | 0 | 120 | B-3-1a |  |  | Transformer
GLEN1Q | GLEN5- | 0.55 | 21.94 | 0 | 70 | B-3-1a |  |  | Transformer
GLFA1- | GLFA3- | 1.111 | 28 | 0 | 90 | B-3-1a |  |  | Transformer
GORW2- | GORW3- | 0.258 | 20.06 | 0 | 120 | B-3-1a |  |  | Transformer
GRIF1S | GRIF36 | 0.248 | 16.298 | 0 | 120 | B-3-1a |  |  | Transformer
GRIF1T | GRIF38 | 0.247 | 16.248 | 0 | 120 | B-3-1a |  |  | Transformer
GRUB1Q | GRUB3- | 0.499 | 24.995 | 0 | 90 | B-3-1a |  |  | Transformer
GRUB1R | GRUB3- | 0.499 | 24.995 | 0 | 90 | B-3-1a |  |  | Transformer
INGA1Q | INGA5- | 1.287 | 25 | 0 | 30 | B-3-1a |  |  | Transformer
INNE1J | INNE3- | 0.89 | 27.87 | 0 | 60 | B-3-1a |  |  | Transformer
INNE1K | INNE3- | 0.9 | 28 | 0 | 60 | B-3-1a |  |  | Transformer
INNE1L | INNE3- | 0.427 | 26.774 | 0 | 90 | B-3-1a |  |  | Transformer
INVB2A | INVR1- | 0.2217 | 4.3026 | -0.0071 | 240 | B-3-1a |  |  | Transformer
INVB2B | INVR1- | 0.2164 | 4.257 | -0.0066 | 240 | B-3-1a |  |  | Transformer
KEIT1- | KEIT2Q | 0.2735 | 8.6123 | -0.0007 | 240 | B-3-1a |  |  | Transformer
KEIT1- | KEIT2R | 0.3328 | 8.9105 | -0.0389 | 240 | B-3-1a |  |  | Transformer
KEIT1- | KEIT3- | 0.54 | 27.778 | 0 | 90 | B-3-1a |  |  | Transformer
KEIT1- | KEIT3- | 0.54 | 27.778 | 0 | 90 | B-3-1a |  |  | Transformer
KEIT1- | KEIT3A | 0.4281 | 25.8965 | 0 | 90 | B-3-1a |  |  | Transformer
KEIT1- | KEIT3A | 0.499 | 24.995 | 0 | 90 | B-3-1a |  |  | Transformer
KIIN1- | KIIN3- | 0.772 | 24.877 | 0 | 45 | B-3-1a |  |  | Transformer
KIIN1- | KIIN3- | 0.769 | 24.521 | 0 | 45 | B-3-1a |  |  | Transformer
KILO1- | KILO3- | 0.88 | 27.78 | 0 | 45 | B-3-1a |  |  | Transformer
KINT1- | KINT2J | 0.3771 | 10.1929 | -0.018 | 240 | B-3-1a |  |  | Transformer
KINT1- | KINT2K | 0.6786 | 12.1477 | -0.0009 | 120 | B-3-1a |  |  | Transformer
KINT1- | KINT3- | 0.456 | 26.107 | 0 | 90 | B-3-1a |  |  | Transformer
KINT2J | KINT4K | 0.0253 | 1.2081 | -0.0005 | 1200 | B-3-1a |  |  | Transformer
KINT2K | KINT4J | 0.0252 | 1.1997 | -0.0005 | 1200 | B-3-1a |  |  | Transformer
KNOC1J | KNOC2J | 0.2216 | 4.311 | -0.0076 | 240 | B-3-1a |  |  | Transformer
KNOC1J | KNOC2K | 0.2205 | 4.3319 | -0.0006 | 240 | B-3-1a |  |  | Transformer
LAIR1- | LAIR3- | 0.425 | 24.674 | 0 | 90 | B-3-1a |  |  | Transformer
LOCB1J | LOCB2J | 0.2181 | 8.1262 | -0.0007 | 240 | B-3-1a |  |  | Transformer
LOCB1K | LOCB2K | 0.22 | 8.197 | -0.0007 | 240 | B-3-1a |  |  | Transformer
LOCH1- | LOCH5J | 1.968 | 79.976 | -0.0008 | 36 | B-3-1a |  |  | Transformer
LOCH1- | LOCH5K | 1.968 | 79.976 | -0.0008 | 36 | B-3-1a |  |  | Transformer
LUIC1Q | LUIC5J | 0.763 | 37.548 | 0 | 45 | B-3-1a |  |  | Transformer
LUIC1R | LUIC5K | 0.7668 | 37.548 | 0 | 45 | B-3-1a |  |  | Transformer
LYND1Q | LYND3- | 0.78 | 24.3 | 0 | 60 | B-3-1a |  |  | Transformer
LYND1R | LYND3- | 0.78 | 24.73 | 0 | 60 | B-3-1a |  |  | Transformer
MACD1Q | MACD3- | 0.83 | 18.89 | 0 | 90 | B-3-1a |  |  | Transformer
MACD1R | MACD3- | 0.83 | 18.89 | 0 | 90 | B-3-1a |  |  | Transformer
MELG1J | MELG4J | 0.108 | 3.957 | -0.0007 | 480 | B-3-1a |  |  | Transformer
MELG1K | MELG4K | 0.106 | 3.957 | -0.0007 | 480 | B-3-1a |  |  | Transformer
MELG4J | MELG8J | 0.25 | 12 | 0 | 100 | B-3-1a |  |  | Transformer
MELG4J | MELG8K | 0.25 | 12 | 0 | 100 | B-3-1a |  |  | Transformer
MILC1R | MILC3- | 0.78 | 24.83 | 0 | 60 | B-3-1a |  |  | Transformer
MILC1S | MILC3- | 0.88 | 28.13 | 0 | 60 | B-3-1a |  |  | Transformer
MILW1Q | MILW3- | 0.439 | 24.896 | 0 | 90 | B-3-1a |  |  | Transformer
MOSS1Q | MOSS5- | 1.192 | 36.847 | 0 | 30 | B-3-1a |  |  | Transformer
MOSS1R | MOSS5- | 1.2267 | 36.913 | 0 | 30 | B-3-1a |  |  | Transformer
MYBS1S | MYBS3J | 0.5 | 25 | 0 | 120 | B-3-1a |  |  | Transformer
MYBS1S | MYBS3K | 0.3837 | 24.98 | 0 | 120 | B-3-1a |  |  | Transformer
MYBS1S | MYBS3M | 0.2645 | 24.6069 | -0.024 | 120 | B-3-1a |  |  | Transformer
MYBS1T | MYBS3J | 0.5 | 25 | 0 | 120 | B-3-1a |  |  | Transformer
MYBS1T | MYBS3K | 0.3837 | 24.98 | 0 | 120 | B-3-1a |  |  | Transformer
MYBS1T | MYBS3N | 0.2578 | 24.757 | -0.024 | 120 | B-3-1a |  |  | Transformer
NAIR1Q | NAIR3- | 1.06 | 28.6 | 0 | 60 | B-3-1a |  |  | Transformer
NAIR1R | NAIR3- | 1.05 | 28.6 | 0 | 60 | B-3-1a |  |  | Transformer
NANT1Q | NANT5- | 1.47 | 56.67 | 0 | 30 | B-3-1a |  |  | Transformer
ORRI1Q | ORRI3- | 0.564 | 16.824 | 0 | 60 | B-3-1a |  |  | Transformer
ORRI1R | ORRI5- | 2.17 | 48.75 | 0 | 20 | B-3-1a |  |  | Transformer
PEHE1- | PEHE2- | 0.4842 | 9.9549 | -0.0178 | 240 | B-3-1a |  |  | Transformer
PEHE1- | PEHE2- | 0.3423 | 8.8892 | -0.0364 | 240 | B-3-1a |  |  | Transformer
PEHE1- | PEHS5- | 2.58 | 42.33 | 0 | 15 | B-3-1a |  |  | Transformer
PEHE2- | PEHE4J | 0.026 | 1.533 | -0.0005 | 1200 | B-3-1a |  |  | Transformer
PEHE2- | PEHE4K | 0.026 | 1.533 | -0.0005 | 1200 | B-3-1a |  |  | Transformer
PEHE2- | PEHE1- | 0.3423 | 8.8892 | -0.0364 | 240 | B-3-1a |  |  | Transformer
PEHG1Q | PEHG3- | 1.05 | 28.53 | 0 | 45 | B-3-1a |  |  | Transformer
PEHG1R | PEHG3- | 1.05 | 28.4 | 0 | 45 | B-3-1a |  |  | Transformer
PERS1Q | PERS2Q | 0.3363 | 8.9062 | -0.0412 | 240 | B-3-1a |  |  | Transformer
PERS1Q | PERS3- | 0.407 | 26.975 | 0 | 90 | B-3-1a |  |  | Transformer
PERS1R | PERS2R | 0.3341 | 8.8645 | -0.0419 | 240 | B-3-1a |  |  | Transformer
PERS1R | PERS3- | 0.407 | 26.975 | 0 | 90 | B-3-1a |  |  | Transformer
QUOI1- | QUOI5- | 1.34 | 33.13 | 0 | 30 | B-3-1a |  |  | Transformer
RANN1Q | RANN3Q | 0.43 | 24.66 | 0 | 90 | B-3-1a |  |  | Transformer
RANN1R | RANN3Q | 0.43 | 24.66 | 0 | 90 | B-3-1a |  |  | Transformer
REDM1Q | REDM3- | 0.91 | 27 | 0 | 60 | B-3-1a |  |  | Transformer
REDM1R | REDM3- | 0.9 | 27.83 | 0 | 60 | B-3-1a |  |  | Transformer
ROTI3- | ROTI4J | 0.556 | 25 | 0 | 120 | B-3-1a |  |  | Transformer
ROTI3- | ROTI4K | 0.556 | 25 | 0 | 120 | B-3-1a |  |  | Transformer
SFEE1C | SFEE5- | 1.8333 | 76.6667 | -0.0121 | 36 | B-3-1a |  |  | Transformer
SFEE1D | SFEE5- | 1.8333 | 76.6667 | -0.0121 | 36 | B-3-1a |  |  | Transformer
SHIN1- | SHIN3- | 0.425 | 26.05 | 0 | 90 | B-3-1a |  |  | Transformer
SHIN1- | SHIN3- | 0.437 | 26.22 | 0 | 90 | B-3-1a |  |  | Transformer
SHIN1- | SHIN5- | 1.4823 | 80.16 | 0 | 40 | B-3-1a |  |  | Transformer
SPIT1J | SPIT2J | 0.218 | 8.185 | -0.0007 | 240 | B-3-1a |  |  | Transformer
SPIT1J | SPIT2J | 0.218 | 8.23 | -0.0007 | 240 | B-3-1a |  |  | Transformer
SPIT1K | SPIT2K | 0.131 | 4.99 | -0.0006 | 360 | B-3-1a |  |  | Transformer
SPIT1M | SPIT2K | 0.129 | 4.99 | -0.0006 | 360 | B-3-1a |  |  | Transformer
STRB2- | STRB3W | 0.251 | 19.873 | 0 | 120 | B-3-1a |  |  | Transformer
STRI1Q | STRI3- | 0.407 | 26.975 | 0 | 90 | B-3-1a |  |  | Transformer
STRI1R | STRI3- | 0.407 | 26.975 | 0 | 90 | B-3-1a |  |  | Transformer
STRL1- | STRL3P | 0.2 | 17.74 | -0.01 | 120 | B-3-1a |  |  | Transformer
STRL1- | STRL3Q | 0.2 | 17.65 | -0.01 | 120 | B-3-1a |  |  | Transformer
STRL1- | STRL3R | 0.2 | 17.67 | -0.01 | 120 | B-3-1a |  |  | Transformer
STRW1- | STRW3- | 0.05 | 18 | 0 | 90 | B-3-1a |  |  | Transformer
TARL1Q | TARL3- | 2.42 | 41 | 0 | 30 | B-3-1a |  |  | Transformer
TARL1R | TARL3- | 2.13 | 38.53 | 0 | 30 | B-3-1a |  |  | Transformer
TAYN1Q | TAYN3- | 0.315 | 28.787 | 0 | 90 | B-3-1a |  |  | Transformer
TAYN1R | TAYN3- | 0.315 | 28.787 | 0 | 90 | B-3-1a |  |  | Transformer
TEAL1- | TEAL2J | 0.3619 | 10.1602 | -0.0118 | 180 | B-3-1a |  |  | Transformer
TEAL1- | TEAL2K | 0.2564 | 11.7305 | -0.0131 | 180 | B-3-1a |  |  | Transformer
TEAL1- | TEAL2K | 0.5506 | 11.8761 | -0.0008 | 180 | B-3-1a |  |  | Transformer
THUS1J | THUS2J | 0.0985 | 3.9363 | -0.0005 | 480 | B-3-1a |  |  | Transformer
THUS1J | THUS3- | 0.2621 | 24.6736 | -0.022 | 120 | B-3-1a |  |  | Transformer
THUS1K | THUS2K | 0.1 | 3.9362 | -0.0006 | 480 | B-3-1a |  |  | Transformer
THUS1K | THUS3- | 0.2614 | 24.7403 | -0.02 | 120 | B-3-1a |  |  | Transformer
TOMT1J | TOMT2J | 0.098 | 3.905 | -0.0006 | 480 | B-3-1a |  |  | Transformer
TOMT1K | TOMT2K | 0.098 | 3.905 | -0.0006 | 480 | B-3-1a |  |  | Transformer
WIOW1Q | WIOW3- | 0.88 | 24.5 | 0 | 60 | B-3-1a |  |  | Transformer
WIOW1R | WIOW3- | 0.88 | 24.5 | 0 | 60 | B-3-1a |  |  | Transformer
WOHI1Q | WOHI3- | 0.62 | 27.24 | 0 | 90 | B-3-1a |  |  | Transformer
WOHI1R | WOHI3- | 0.61 | 27.31 | 0 | 90 | B-3-1a |  |  | Transformer
AIKE3A | WESE1- | 0.5667 | 13.2333 | 0 | 90 | B-3-1b |  |  | Transformer
AIKE3B | WESE1- | 0.5667 | 13.2333 | 0 | 90 | B-3-1b |  |  | Transformer
AREC1- | AREC3- | 0.4634 | 24.4456 | -0.0064 | 60 | B-3-1b |  |  | Transformer
AREC1- | AREC3A | 0.3886 | 16.84 | -0.0241 | 90 | B-3-1b |  |  | Transformer
AREC1- | AREC3B | 0.3915 | 16.7288 | -0.0227 | 90 | B-3-1b |  |  | Transformer
AYR-2Q | AYR-3- | 0.4868 | 20.2441 | 0 | 120 | B-3-1b |  |  | Transformer
AYR-2R | AYR-3- | 0.2752 | 25.1818 | -0.0142 | 120 | B-3-1b |  |  | Transformer
BAGA1Q | BAGA3- | 0.741 | 27.0343 | 0 | 90 | B-3-1b |  |  | Transformer
BAGA1R | BAGA3- | 0.741 | 27.2233 | 0 | 90 | B-3-1b |  |  | Transformer
BAIN1Q | BAIN3- | 0.5545 | 26.2275 | -0.0056 | 60 | B-3-1b |  |  | Transformer
BAIN1R | BAIN3- | 0.491 | 26.2454 | -0.0056 | 60 | B-3-1b |  |  | Transformer
BERW1Q | BERW3- | 0.9683 | 26.4656 | -0.0061 | 60 | B-3-1b |  |  | Transformer
BERW1R | BERW3- | 0.7912 | 26.5549 | -0.0061 | 60 | B-3-1b |  |  | Transformer
BLAH1- | BLAH3A | 0.3363 | 27.798 | -0.0152 | 90 | B-3-1b |  |  | Transformer
BLAH1- | BLAH3A | 0.3386 | 27.9313 | -0.0106 | 90 | B-3-1b |  |  | Transformer
BLAH1- | BLAH3B | 0.3394 | 27.9424 | -0.015 | 90 | B-3-1b |  |  | Transformer
BLAH1- | BLAH3B | 0.342 | 28.0646 | -0.0103 | 90 | B-3-1b |  |  | Transformer
BLCW1- | BLCW3- | 0.3083 | 16.9083 | -0.0283 | 90 | B-3-1b |  |  | Transformer
BLKL1- | BLKL3A | 0.0943 | 18.6775 | 0 | 90 | B-3-1b |  |  | Transformer
BLKL1- | BLKL3B | 0.0955 | 18.6553 | 0 | 90 | B-3-1b |  |  | Transformer
BLLX1- | BLLX3- | 0.2833 | 16.8643 | -0.0133 | 90 | B-3-1b |  |  | Transformer
BONN1- | BONN3- | 0.4288 | 27.1188 | -0.0146 | 90 | B-3-1b |  |  | Transformer
BONN1- | BONN3- | 0.4334 | 27.5521 | -0.0092 | 90 | B-3-1b |  |  | Transformer
BONN2A | BONN1- | 0.1559 | 8.9445 | -0.1694 | 240 | B-3-1b |  |  | Transformer
BONN2B | BONN1- | 0.1559 | 8.9445 | -0.1694 | 240 | B-3-1b |  |  | Transformer
BPGR3J | GRMO2- | 0.3876 | 19.4628 | -0.0275 | 120 | B-3-1b |  |  | Transformer
BPGR3K | GRMO2- | 0.3093 | 18.8225 | -0.0373 | 120 | B-3-1b |  |  | Transformer
BRAP1- | BRAP3- | 0.728 | 26.6656 | 0 | 90 | B-3-1b |  |  | Transformer
BRAP1- | BRAP3- | 0.728 | 26.6656 | 0 | 90 | B-3-1b |  |  | Transformer
BROX1Q | BROX3- | 0.6814 | 27.7694 | -0.0487 | 90 | B-3-1b |  |  | Transformer
BROX1R | BROX3- | 0.6814 | 27.7694 | -0.0487 | 90 | B-3-1b |  |  | Transformer
CAFA1Q | CAFA5R | 1.0894 | 32.6818 | 0 | 30 | B-3-1b |  |  | Transformer
CATY1Q | CATY3- | 1.015 | 25.8801 | -0.1318 | 60 | B-3-1b |  |  | Transformer
CATY1R | CATY3- | 1.0164 | 25.6132 | -0.0966 | 60 | B-3-1b |  |  | Transformer
CCSS1- | CCSS3- | 0.273 | 13.8306 | -0.0276 | 120 | B-3-1b |  |  | Transformer
CHAP1- | CHAP3- | 0.4338 | 27.5299 | -0.0175 | 90 | B-3-1b |  |  | Transformer
CHAP1- | CHAP3- | 0.4294 | 27.5633 | -0.0188 | 90 | B-3-1b |  |  | Transformer
CHAS2Q | CHAS3C | 0.4875 | 18.1601 | -0.1331 | 120 | B-3-1b |  |  | Transformer
CHAS2R | CHAS3A | 0.5214 | 27.5617 | -0.1031 | 120 | B-3-1b |  |  | Transformer
CLYM2- | CLYM3A | 0.4722 | 20.2028 | -0.1542 | 120 | B-3-1b |  |  | Transformer
CLYM2- | CLYM3B | 0.4917 | 19.994 | -0.1425 | 120 | B-3-1b |  |  | Transformer
CLYN2Q | CLYN3A | 0.3432 | 13.0038 | -0.0115 | 120 | B-3-1b |  |  | Transformer
CLYN2Q | CLYN3B | 0.3423 | 12.9455 | -0.0108 | 120 | B-3-1b |  |  | Transformer
CLYN2Q | CLYN3C | 0.3414 | 13.0205 | -0.0094 | 120 | B-3-1b |  |  | Transformer
CLYN2Q | CLYN3D | 0.3472 | 12.9954 | -0.0133 | 120 | B-3-1b |  |  | Transformer
CLYS2R | CLYS3A | 0.3406 | 12.9789 | -0.0112 | 120 | B-3-1b |  |  | Transformer
CLYS2R | CLYS3X | 0.3475 | 13.0037 | -0.0112 | 120 | B-3-1b |  |  | Transformer
COAL4- | COAL1A | 0.1055 | 6.777 | -0.0931 | 360 | B-3-1b |  |  | Transformer
COAL4- | COAL1A | 0.1258 | 9.7909 | -0.0801 | 240 | B-3-1b |  |  | Transformer
COAL4- | COAL1B | 0.1258 | 9.7909 | -0.0801 | 240 | B-3-1b |  |  | Transformer
COAL4- | COAL1B | 0.0914 | 6.4382 | -0.0751 | 360 | B-3-1b |  |  | Transformer
COAT2Q | COAT3- | 0.2681 | 24.3152 | -0.021 | 120 | B-3-1b |  |  | Transformer
COAT2R | COAT3- | 0.2681 | 24.3152 | -0.021 | 120 | B-3-1b |  |  | Transformer
COCK2- | COCK3- | 0.2841 | 27.8235 | -0.0171 | 120 | B-3-1b |  |  | Transformer
COCK2- | COCK3- | 0.4792 | 18.7022 | -0.2214 | 120 | B-3-1b |  |  | Transformer
COCK4Q | COCK2- | 0.0135 | 1.6479 | -0.3338 | 1000 | B-3-1b |  |  | Transformer
COCK4R | COCK2- | 0.013 | 1.5999 | -0.2252 | 1000 | B-3-1b |  |  | Transformer
COYL1- | COYL3- | 0.9944 | 20.8596 | -0.0881 | 60 | B-3-1b |  |  | Transformer
COYL1- | COYL3- | 0.9217 | 21.6804 | 0 | 60 | B-3-1b |  |  | Transformer
COYL2- | COYL1- | 0.1035 | 8.6744 | -0.051 | 240 | B-3-1b |  |  | Transformer
COYL2- | COYL1- | 0.1036 | 8.7952 | -0.0513 | 240 | B-3-1b |  |  | Transformer
CROO1Q | CROO3J | 0.9311 | 19.9449 | -0.3719 | 60 | B-3-1b |  |  | Transformer
CROO1Q | CROO3K | 0.9748 | 26.6155 | -0.0058 | 60 | B-3-1b |  |  | Transformer
CROO1R | CROO3J | 0.9311 | 19.9449 | -0.3719 | 60 | B-3-1b |  |  | Transformer
CROO1R | CROO3K | 0.9758 | 26.6321 | -0.0063 | 60 | B-3-1b |  |  | Transformer
CRYR1- | CRYR31 | 0.2951 | 16.6641 | -0.2002 | 120 | B-3-1b |  |  | Transformer
CRYR1- | CRYR32 | 0.2951 | 16.6641 | -0.2002 | 120 | B-3-1b |  |  | Transformer
CRYR4- | CRYR1- | 0.1496 | 10.0489 | -0.0583 | 240 | B-3-1b |  |  | Transformer
CRYR4- | CRYR1A | 0.1217 | 9.8451 | -0.067 | 240 | B-3-1b |  |  | Transformer
CUMB1Q | CUMB3- | 0.7407 | 29.324 | -0.129 | 90 | B-3-1b |  |  | Transformer
CUMB1R | CUMB3- | 0.741 | 27.111 | 0 | 90 | B-3-1b |  |  | Transformer
CUPA1Q | CUPA3- | 0.4473 | 26.3962 | -0.0195 | 90 | B-3-1b |  |  | Transformer
CUPA1R | CUPA3- | 0.4518 | 26.4517 | -0.0195 | 90 | B-3-1b |  |  | Transformer
CURR1A | CURR5- | 3.225 | 79.0009 | 0 | 30 | B-3-1b |  |  | Transformer
CURR1B | CURR5- | 3.23 | 79.0007 | 0 | 30 | B-3-1b |  |  | Transformer
CURR2- | CURR1A | 0.1079 | 8.5702 | -0.0341 | 240 | B-3-1b |  |  | Transformer
CURR2- | CURR1A | 0.1148 | 8.4492 | -0.073 | 240 | B-3-1b |  |  | Transformer
CURR2- | CURR1B | 0.1205 | 8.4741 | -0.084 | 240 | B-3-1b |  |  | Transformer
DALM1- | DALM3- | 0.447 | 27.333 | 0 | 90 | B-3-1b |  |  | Transformer
DALM1- | DALM3- | 0.469 | 27.3326 | 0 | 90 | B-3-1b |  |  | Transformer
DALM2Q | DALM1- | 0.1653 | 8.7484 | -0.1176 | 240 | B-3-1b |  |  | Transformer
DALM2R | DALM1- | 0.1653 | 8.7484 | -0.1176 | 240 | B-3-1b |  |  | Transformer
DENN2- | DENN1- | 0.1452 | 8.6093 | -0.1299 | 240 | B-3-1b |  |  | Transformer
DENN4- | DENN2- | 0.0164 | 1.6449 | -0.1161 | 1000 | B-3-1b |  |  | Transformer
DESA1Q | DESA3- | 0.2828 | 16.831 | -0.0195 | 90 | B-3-1b |  |  | Transformer
DEVM1- | DEVM3- | 1.0878 | 19.9704 | -1.7577 | 60 | B-3-1b |  |  | Transformer
DEVM1- | DEVM3- | 1.0869 | 20.0038 | -1.8609 | 60 | B-3-1b |  |  | Transformer
DEVM4- | DEVM1- | 0.1335 | 8.3739 | -0.1562 | 240 | B-3-1b |  |  | Transformer
DEVM4- | DEVM1- | 0.1338 | 8.3739 | -0.2103 | 240 | B-3-1b |  |  | Transformer
DEVO1- | DEVO3- | 0.74 | 29.6674 | 0 | 90 | B-3-1b |  |  | Transformer
DEVO1- | DEVO3- | 0.4705 | 26.4736 | -0.0191 | 90 | B-3-1b |  |  | Transformer
DEWP2Q | DEWP3- | 0.2932 | 21.048 | -0.093 | 120 | B-3-1b |  |  | Transformer
DEWP2R | DEWP3- | 0.2936 | 21.0667 | -0.079 | 120 | B-3-1b |  |  | Transformer
DONO1- | DONO3A | 0.1922 | 14.207 | -0.0113 | 120 | B-3-1b |  |  | Transformer
DRCR1Q | DRCR3- | 0.5273 | 27.0838 | -0.0105 | 90 | B-3-1b |  |  | Transformer
DRCR1R | DRCR3- | 0.5227 | 26.8727 | -0.0109 | 90 | B-3-1b |  |  | Transformer
DRUM2Q | DRUM3- | 0.3963 | 23.9134 | -0.0247 | 120 | B-3-1b |  |  | Transformer
DRUM2R | DRUM3- | 0.3917 | 24.4135 | -0.0224 | 120 | B-3-1b |  |  | Transformer
DUMF1- | DUMF3A | 0.367 | 11.7276 | 0 | 90 | B-3-1b |  |  | Transformer
DUMF1- | DUMF3B | 0.375 | 11.794 | 0 | 90 | B-3-1b |  |  | Transformer
DUMF1- | DUMF3I | 0.766 | 20.5657 | 0 | 60 | B-3-1b |  |  | Transformer
DUNB1Q | DUNB3A | 0.8069 | 21.4849 | -0.3294 | 60 | B-3-1b |  |  | Transformer
DUNB1R | DUNB3A | 0.8069 | 21.4849 | -0.3294 | 60 | B-3-1b |  |  | Transformer
DUNB1S | DUNB3B | 0.4121 | 28.9304 | -0.0087 | 90 | B-3-1b |  |  | Transformer
DUNB1T | DUNB3B | 0.3569 | 28.82 | -0.0089 | 90 | B-3-1b |  |  | Transformer
DUNE1- | DUNE3- | 0.4271 | 19.5731 | -0.0091 | 90 | B-3-1b |  |  | Transformer
DUNE1- | DUNE3- | 0.4249 | 19.3175 | -0.0084 | 90 | B-3-1b |  |  | Transformer
DUNF1Q | DUNF3- | 0.7383 | 24.7112 | -0.0936 | 90 | B-3-1b |  |  | Transformer
DUNF1R | DUNF3- | 0.7383 | 24.7112 | -0.0936 | 90 | B-3-1b |  |  | Transformer
DUNH1S | DUNH3- | 0.3428 | 28.2868 | -0.0105 | 90 | B-3-1b |  |  | Transformer
DUNH1T | DUNH3- | 0.3495 | 28.1867 | -0.0166 | 90 | B-3-1b |  |  | Transformer
EAST1Q | EAST5- | 4.1511 | 74.885 | -0.1943 | 15 | B-3-1b |  |  | Transformer
ECCL1- | ECCL3- | 1.054 | 26.8827 | 0 | 60 | B-3-1b |  |  | Transformer
ECCL1- | ECCL3- | 1.04 | 26.7314 | 0 | 60 | B-3-1b |  |  | Transformer
ECCL4A | ECCL1- | 0.1103 | 9.7952 | -0.0791 | 240 | B-3-1b |  |  | Transformer
ECCL4B | ECCL1- | 0.1103 | 9.7952 | -0.0791 | 240 | B-3-1b |  |  | Transformer
EERH2- | EERH3- | 0.2569 | 25.607 | -0.0414 | 120 | B-3-1b |  |  | Transformer
EERH2- | EERH3- | 0.306 | 18.0724 | -0.0486 | 120 | B-3-1b |  |  | Transformer
EKIL2S | EKIL3A | 0.303 | 17.9224 | -0.0436 | 120 | B-3-1b |  |  | Transformer
EKIL2T | EKIL3B | 0.303 | 17.8441 | -0.0485 | 120 | B-3-1b |  |  | Transformer
EKIS2- | EKIS3A | 0.4948 | 24.3283 | -0.2487 | 120 | B-3-1b |  |  | Transformer
EKIS2- | EKIS3B | 0.4773 | 24.2453 | -0.2651 | 120 | B-3-1b |  |  | Transformer
ELDE1Q | ELDE3- | 0.9136 | 19.8123 | -0.3053 | 60 | B-3-1b |  |  | Transformer
ELDE1R | ELDE3- | 0.9136 | 19.9791 | -0.3053 | 60 | B-3-1b |  |  | Transformer
ELVA1- | ELVA3A | 0.4635 | 24.1789 | -0.0101 | 60 | B-3-1b |  |  | Transformer
ELVA2R | ELVA1- | 0.0984 | 5.8325 | -0.2121 | 360 | B-3-1b |  |  | Transformer
ELVA4- | ELVA2Q | 0.0309 | 3.2879 | -0.8983 | 500 | B-3-1b |  |  | Transformer
ELVA4- | ELVA2R | 0.031 | 3.2859 | -0.8082 | 500 | B-3-1b |  |  | Transformer
ERSK1Q | ERSK3- | 0.5259 | 26.8282 | -0.0075 | 60 | B-3-1b |  |  | Transformer
ERSK1R | ERSK3- | 0.5296 | 27.1115 | -0.0073 | 60 | B-3-1b |  |  | Transformer
EWEH1Q | EWEH3- | 0.2827 | 16.8532 | -0.0191 | 90 | B-3-1b |  |  | Transformer
FALL4- | FALL3A | 0.2564 | 16.6647 | 0 | 120 | B-3-1b |  |  | Transformer
FALL4- | FALL3B | 0.2564 | 16.6647 | 0 | 120 | B-3-1b |  |  | Transformer
FINN1Q | FINN3- | 0.5198 | 26.0837 | -0.0091 | 90 | B-3-1b |  |  | Transformer
FINN1R | FINN3- | 0.5221 | 25.9836 | -0.0092 | 90 | B-3-1b |  |  | Transformer
GALA1- | GALA3- | 0.4311 | 25.9297 | -0.0244 | 90 | B-3-1b |  |  | Transformer
GALA1- | GALA3- | 0.4452 | 26.6074 | -0.0132 | 90 | B-3-1b |  |  | Transformer
GAWH1Q | GAWH3- | 0.2843 | 16.9754 | -0.0173 | 90 | B-3-1b |  |  | Transformer
GLGL1Q | GLGL3- | 0.3327 | 27.8536 | -0.0092 | 90 | B-3-1b |  |  | Transformer
GLGL1R | GLGL3- | 0.3349 | 27.9091 | -0.0086 | 90 | B-3-1b |  |  | Transformer
GLLE1- | GLLE5- | 2.3889 | 72.9609 | 0 | 30 | B-3-1b |  |  | Transformer
GLLU1Q | GLLU3- | 0.961 | 24.5329 | 0 | 60 | B-3-1b |  |  | Transformer
GLLU1R | GLLU3- | 1.069 | 25.0839 | 0 | 60 | B-3-1b |  |  | Transformer
GLNI1- | GLNI3- | 0.6998 | 27.8134 | -0.1093 | 90 | B-3-1b |  |  | Transformer
GLNI1- | GLNI3- | 0.6894 | 27.7692 | -0.1102 | 90 | B-3-1b |  |  | Transformer
GLRO2- | GLRO3A | 0.479 | 24.4953 | 0 | 120 | B-3-1b |  |  | Transformer
GLRO2- | GLRO3B | 0.4763 | 24.412 | 0 | 120 | B-3-1b |  |  | Transformer
GORG1Q | GORG3- | 0.7875 | 26.555 | -0.0062 | 60 | B-3-1b |  |  | Transformer
GORG1R | GORG3- | 0.8167 | 26.9876 | -0.0071 | 60 | B-3-1b |  |  | Transformer
GOVA1Q | GOVA3- | 0.5223 | 26.1503 | -0.0083 | 90 | B-3-1b |  |  | Transformer
GOVA1R | GOVA3- | 0.5155 | 26.1727 | -0.0108 | 90 | B-3-1b |  |  | Transformer
GRMO2- | GRMO3C | 0.4781 | 25.1621 | -0.0871 | 120 | B-3-1b |  |  | Transformer
GRMO2- | GRMO3C | 0.4985 | 25.2451 | -0.0869 | 120 | B-3-1b |  |  | Transformer
GRNA4- | GRNA1- | 0.1472 | 10.0573 | -0.0558 | 240 | B-3-1b |  |  | Transformer
GRNA4- | GRNA1- | 0.1252 | 9.7909 | -0.081 | 240 | B-3-1b |  |  | Transformer
HADH1- | HADH3- | 0.438 | 13.3003 | 0 | 120 | B-3-1b |  |  | Transformer
HAGR1Q | HAGR3- | 0.5381 | 25.2943 | -0.0108 | 60 | B-3-1b |  |  | Transformer
HAGR1R | HAGR3- | 0.5478 | 25.8775 | -0.008 | 60 | B-3-1b |  |  | Transformer
HARE1- | HARE3A | 0.2433 | 16.789 | -0.0205 | 90 | B-3-1b |  |  | Transformer
HARE1- | HARE3B | 0.2411 | 16.8111 | -0.0205 | 90 | B-3-1b |  |  | Transformer
HAWI1- | HAWI3- | 1.0278 | 25.6127 | -0.1152 | 60 | B-3-1b |  |  | Transformer
HAWI1- | HAWI3- | 1.0136 | 25.8802 | -0.1316 | 60 | B-3-1b |  |  | Transformer
HELE1Q | HELE3- | 0.9544 | 20.8615 | 0 | 60 | B-3-1b |  |  | Transformer
HELE1R | HELE3- | 0.6843 | 28.6252 | -0.0082 | 60 | B-3-1b |  |  | Transformer
HUNF1Q | HUNF3- | 0.8042 | 16.5638 | -0.06 | 60 | B-3-1b |  |  | Transformer
HUNF1R | HUNF3- | 0.7893 | 16.4144 | -0.0596 | 60 | B-3-1b |  |  | Transformer
HUNN4A | HUNN2A | 0.0538 | 2.9466 | -0.0947 | 240 | B-3-1b |  |  | Transformer
HUNN4B | HUNN2B | 0.0537 | 2.9441 | -0.0946 | 240 | B-3-1b |  |  | Transformer
INKE1Q | INKE3- | 0.6185 | 23.7697 | 0 | 90 | B-3-1b |  |  | Transformer
INKE1R | INKE3- | 0.6222 | 23.7696 | 0 | 90 | B-3-1b |  |  | Transformer
JOHN1Q | JOHN3- | 0.7058 | 27.8077 | -0.0092 | 60 | B-3-1b |  |  | Transformer
JOHN1R | JOHN3- | 0.7078 | 27.9911 | -0.013 | 60 | B-3-1b |  |  | Transformer
KAIM2- | KAIM3A | 0.4944 | 20.244 | -0.245 | 120 | B-3-1b |  |  | Transformer
KAIM2- | KAIM3B | 0.4972 | 19.1602 | -0.2454 | 120 | B-3-1b |  |  | Transformer
KENE3- | MIDM1- | 0.3875 | 17.9673 | -0.0311 | 70 | B-3-1b |  |  | Transformer
KENN1- | KENN3- | 0.1922 | 14.207 | -0.0113 | 120 | B-3-1b |  |  | Transformer
KEOO1- | KEOO5- | 2.9 | 71.608 | -0.028 | 30 | B-3-1b |  |  | Transformer
KIER1Q | KIER3- | 0.4314 | 27.1188 | -0.0087 | 90 | B-3-1b |  |  | Transformer
KIER1R | KIER3- | 0.7227 | 25.3341 | 0 | 90 | B-3-1b |  |  | Transformer
KILB1Q | KILB3- | 0.9214 | 23.8656 | -0.6492 | 60 | B-3-1b |  |  | Transformer
KILB1Q | KILB5- | 4.3575 | 97.6528 | -0.0539 | 20 | B-3-1b |  |  | Transformer
KILB1R | KILB3- | 0.8919 | 23.8333 | -0.6287 | 60 | B-3-1b |  |  | Transformer
KILB1R | KILB5- | 4.3825 | 97.2012 | -0.059 | 20 | B-3-1b |  |  | Transformer
KILG2- | KILG3A | 0.1883 | 12.5319 | -0.0338 | 120 | B-3-1b |  |  | Transformer
KILG2- | KILG3B | 0.1869 | 12.5153 | -0.028 | 120 | B-3-1b |  |  | Transformer
KILG2- | KILG3C | 0.1866 | 12.4236 | -0.0359 | 120 | B-3-1b |  |  | Transformer
KILS2- | KILS1- | 0.143 | 8.6447 | -0.1299 | 240 | B-3-1b |  |  | Transformer
KILS2- | KILS3- | 0.4823 | 24.1619 | -0.2177 | 120 | B-3-1b |  |  | Transformer
KILS2- | KILS3- | 0.5013 | 24.0114 | -0.1726 | 120 | B-3-1b |  |  | Transformer
KILS4- | KILS2- | 0.018 | 1.6069 | -0.5085 | 1000 | B-3-1b |  |  | Transformer
KILS4- | KILS2- | 0.0134 | 1.6649 | -0.5095 | 1000 | B-3-1b |  |  | Transformer
KILS4T | KILS2- | 0.0148 | 1.6509 | -0.1193 | 1000 | B-3-1b |  |  | Transformer
KILT2Q | KILT3A | 0.5378 | 28.745 | -0.0524 | 120 | B-3-1b |  |  | Transformer
KILT2R | KILT3A | 0.5378 | 28.745 | -0.0524 | 120 | B-3-1b |  |  | Transformer
KILW1Q | KILW3- | 0.6968 | 27.7023 | -0.1233 | 90 | B-3-1b |  |  | Transformer
KILW1R | KILW3- | 0.6968 | 27.7023 | -0.1233 | 90 | B-3-1b |  |  | Transformer
KYPE1- | KYPE3- | 0.1922 | 14.207 | -0.0113 | 120 | B-3-1b |  |  | Transformer
KYPE1- | KYPE3A | 0.3076 | 16.875 | -0.0289 | 90 | B-3-1b |  |  | Transformer
LEVE1Q | LEVE3- | 0.979 | 20.6001 | 0 | 60 | B-3-1b |  |  | Transformer
LEVE1R | LEVE3- | 0.944 | 20.7502 | 0 | 60 | B-3-1b |  |  | Transformer
LING1Q | LING3- | 0.7346 | 29.6576 | -0.1478 | 90 | B-3-1b |  |  | Transformer
LING1R | LING3- | 0.7309 | 28.7685 | -0.109 | 90 | B-3-1b |  |  | Transformer
LINM1Q | LINM3- | 0.4309 | 27.7078 | -0.0186 | 90 | B-3-1b |  |  | Transformer
LINM1R | LINM3- | 0.4283 | 27.73 | -0.0186 | 90 | B-3-1b |  |  | Transformer
MAHI2- | MAHI1- | 0.1284 | 8.6824 | -0.2535 | 240 | B-3-1b |  |  | Transformer
MAHI2- | MAHI3- | 0.2928 | 12.1973 | -0.0267 | 120 | B-3-1b |  |  | Transformer
MAYB1- | MAYB3- | 1.84 | 33.2825 | 0 | 30 | B-3-1b |  |  | Transformer
MAYB1- | MAYB3- | 1.84 | 34.3174 | 0 | 30 | B-3-1b |  |  | Transformer
MIDM1- | MIDM3- | 0.4664 | 13.6087 | -0.0075 | 60 | B-3-1b |  |  | Transformer
MOFF1- | MOFF3A | 0.4635 | 24.1789 | -0.0101 | 60 | B-3-1b |  |  | Transformer
MOFF4- | MOFF1- | 0.1483 | 10.0614 | -0.3432 | 240 | B-3-1b |  |  | Transformer
MOFF4- | MOFF1- | 0.1483 | 10.0614 | -0.3432 | 240 | B-3-1b |  |  | Transformer
MOSH1Q | MOSH5J | 1.1896 | 19.9646 | 0 | 37 | B-3-1b |  |  | Transformer
MOSH1R | MOSH5K | 1.1896 | 19.9646 | 0 | 37 | B-3-1b |  |  | Transformer
MOSM1A | MOSM3Q | 1.4321 | 26.6282 | 0 | 45 | B-3-1b |  |  | Transformer
MOSM1B | MOSM3R | 1.4321 | 26.6282 | 0 | 45 | B-3-1b |  |  | Transformer
MOSM2- | MOSM1A | 0.151 | 8.332 | -0.1299 | 240 | B-3-1b |  |  | Transformer
MOSM2- | MOSM1B | 0.157 | 8.7486 | -0.1299 | 240 | B-3-1b |  |  | Transformer
NEAR2Q | NEAR3- | 0.4856 | 18.2435 | -0.1614 | 120 | B-3-1b |  |  | Transformer
NEAR2R | NEAR3- | 0.4856 | 18.1602 | -0.1723 | 120 | B-3-1b |  |  | Transformer
NECU2- | NECU1- | 0.1173 | 8.6992 | -0.0311 | 240 | B-3-1b |  |  | Transformer
NECU2- | NECU1- | 0.1173 | 8.5659 | -0.0322 | 240 | B-3-1b |  |  | Transformer
NECU2- | NECU1- | 0.1167 | 8.7367 | -0.0297 | 240 | B-3-1b |  |  | Transformer
NEIL2- | NEIL1- | 0.1509 | 8.4778 | -0.1862 | 240 | B-3-1b |  |  | Transformer
NEIL2- | NEIL1- | 0.1457 | 8.5196 | -0.1979 | 240 | B-3-1b |  |  | Transformer
NEIL4Q | NEIL1C | 0.1122 | 9.3882 | -0.2007 | 360 | B-3-1b |  |  | Transformer
NEIL4Q | NEIL2C | 0.0181 | 1.6169 | -0.4986 | 1000 | B-3-1b |  |  | Transformer
NEIL4R | NEIL2D | 0.0133 | 1.6749 | -0.3581 | 1000 | B-3-1b |  |  | Transformer
NETS1- | NETS3- | 0.8311 | 28.2878 | -0.0097 | 60 | B-3-1b |  |  | Transformer
PAIS1S | PAIS3- | 0.5609 | 26.1773 | -0.004 | 60 | B-3-1b |  |  | Transformer
PAIS1T | PAIS3- | 0.7736 | 20.352 | -0.216 | 60 | B-3-1b |  |  | Transformer
PART1Q | PART3- | 0.9103 | 21.2972 | 0 | 60 | B-3-1b |  |  | Transformer
PART1R | PART3- | 0.93 | 21.5299 | 0 | 60 | B-3-1b |  |  | Transformer
POOB2Q | POOB3- | 0.3244 | 20.4558 | -0.0158 | 120 | B-3-1b |  |  | Transformer
POOB2R | POOB3- | 0.3244 | 20.4558 | -0.0158 | 120 | B-3-1b |  |  | Transformer
PORD2Q | PORD3- | 0.3702 | 18.3296 | -0.1621 | 120 | B-3-1b |  |  | Transformer
REDH1- | REDH3- | 0.6267 | 27.5484 | 0 | 60 | B-3-1b |  |  | Transformer
REDH1- | REDH3- | 0.94 | 20.7787 | 0 | 90 | B-3-1b |  |  | Transformer
SACO1Q | SACO3J | 0.9444 | 24.4484 | 0 | 60 | B-3-1b |  |  | Transformer
SACO1Q | SACO3K | 0.9542 | 21.1451 | 0 | 60 | B-3-1b |  |  | Transformer
SACO1R | SACO3J | 0.9444 | 24.4484 | 0 | 60 | B-3-1b |  |  | Transformer
SACO1R | SACO3K | 0.9683 | 21.4114 | 0 | 60 | B-3-1b |  |  | Transformer
SAKN1- | SAKN3- | 0.325 | 9.9364 | -0.0113 | 120 | B-3-1b |  |  | Transformer
SANX1Q | SANX3- | 0.7366 | 27.1233 | -0.009 | 60 | B-3-1b |  |  | Transformer
SANX1R | SANX3- | 0.7377 | 27.19 | -0.0098 | 60 | B-3-1b |  |  | Transformer
SHRU2Q | SHRU3A | 0.535 | 28.5617 | -0.0629 | 120 | B-3-1b |  |  | Transformer
SHRU2R | SHRU3B | 0.2914 | 23.7232 | -0.0252 | 120 | B-3-1b |  |  | Transformer
SIGH2Q | SIGH3A | 0.4564 | 27.5518 | -0.032 | 180 | B-3-1b |  |  | Transformer
SIGH2R | SIGH3A | 0.4281 | 27.53 | -0.0372 | 180 | B-3-1b |  |  | Transformer
SMEA2- | SMEA1- | 0.1271 | 8.7241 | -0.043 | 240 | B-3-1b |  |  | Transformer
SMEA4R | SMEA2- | 0.0134 | 1.6639 | -0.2312 | 1000 | B-3-1b |  |  | Transformer
SPAV1Q | SPAV3- | 0.728 | 26.6656 | 0 | 90 | B-3-1b |  |  | Transformer
SPAV1R | SPAV3- | 0.728 | 26.6656 | 0 | 90 | B-3-1b |  |  | Transformer
STHA2A | STHA3- | 0.4557 | 30.1188 | -0.0331 | 90 | B-3-1b |  |  | Transformer
STHA2B | STHA3- | 0.4917 | 19.994 | -0.1424 | 114 | B-3-1b |  |  | Transformer
STHA4A | STHA2A | 0.018 | 1.7059 | -0.2252 | 1000 | B-3-1b |  |  | Transformer
STHA4B | STHA2B | 0.0134 | 1.6949 | -2.0384 | 1000 | B-3-1b |  |  | Transformer
STIR1S | STIR3- | 0.6 | 27.5446 | 0 | 90 | B-3-1b |  |  | Transformer
STIR1T | STIR3- | 0.503 | 27.1331 | 0 | 90 | B-3-1b |  |  | Transformer
STLE1Q | STLE3S | 0.4217 | 25.741 | -0.028 | 87 | B-3-1b |  |  | Transformer
STLE1R | STLE3S | 0.4235 | 25.6743 | -0.0254 | 87 | B-3-1b |  |  | Transformer
TELR1Q | TELR3- | 0.9688 | 26.4656 | -0.0572 | 60 | B-3-1b |  |  | Transformer
TELR1R | TELR3- | 0.6325 | 28.5763 | -0.0081 | 60 | B-3-1b |  |  | Transformer
TONG1- | TONG3- | 0.533 | 26.9114 | -0.0078 | 60 | B-3-1b |  |  | Transformer
TONG1- | TONG3- | 0.5309 | 27.0615 | -0.008 | 60 | B-3-1b |  |  | Transformer
TONG1- | TONG5- | 1.6834 | 33.9917 | -0.01 | 30 | B-3-1b |  |  | Transformer
TONG1- | TONG5- | 1.6721 | 34.0924 | -0.0269 | 30 | B-3-1b |  |  | Transformer
TORN4- | TORN1- | 0.1674 | 8.0399 | -0.0509 | 240 | B-3-1b |  |  | Transformer
TORN4- | TORN1- | 0.1688 | 8.0816 | -0.0663 | 240 | B-3-1b |  |  | Transformer
WFIE1A | WFIE3- | 0.6617 | 28.7591 | -0.0062 | 60 | B-3-1b |  |  | Transformer
WFIE1B | WFIE3- | 0.6619 | 28.6257 | -0.0112 | 60 | B-3-1b |  |  | Transformer
WFIE2- | WFIE1A | 0.1408 | 8.6113 | -0.1827 | 240 | B-3-1b |  |  | Transformer
WFIE2- | WFIE1B | 0.1264 | 8.7366 | -0.1602 | 240 | B-3-1b |  |  | Transformer
WGEO2Q | WGEO3- | 0.4889 | 18.2518 | -0.2083 | 120 | B-3-1b |  |  | Transformer
WHHO2Q | WHHO3- | 0.4128 | 24.9549 | -0.0345 | 120 | B-3-1b |  |  | Transformer
WHHO2R | WHHO3- | 0.5236 | 20.1599 | -0.1959 | 120 | B-3-1b |  |  | Transformer
WHTL1S | WHTL3- | 2 | 27.1108 | 0 | 45 | B-3-1b |  |  | Transformer
WHTL1T | WHTL3- | 2 | 27.1108 | 0 | 45 | B-3-1b |  |  | Transformer
WISH2- | WISH1- | 0.1297 | 8.8874 | -0.2192 | 215 | B-3-1b |  |  | Transformer
WISH2- | WISH3- | 0.4944 | 20.1606 | -0.2477 | 120 | B-3-1b |  |  | Transformer
WISH2- | WISH3- | 0.4824 | 24.1285 | -0.2277 | 120 | B-3-1b |  |  | Transformer
WISH2- | WISH3S | 0.4382 | 19.1617 | -0.195 | 120 | B-3-1b |  |  | Transformer
WISH2- | WISH3T | 0.4889 | 18.3268 | -0.1166 | 120 | B-3-1b |  |  | Transformer
WISH4- | WISH2- | 0.0163 | 1.6529 | -0.0792 | 1000 | B-3-1b |  |  | Transformer
WISH4- | WISH2- | 0.0134 | 1.6849 | -0.0814 | 1000 | B-3-1b |  |  | Transformer
WIYH2- | WIYH1- | 0.1568 | 8.4569 | -0.3494 | 240 | B-3-1b |  |  | Transformer
WIYH2- | WIYH1- | 0.1524 | 8.457 | -0.3487 | 240 | B-3-1b |  |  | Transformer
WIYH2- | WIYH1- | 0.0987 | 8.8078 | -0.0518 | 240 | B-3-1b |  |  | Transformer
WIYH4Q | WIYH2- | 0.0133 | 1.6699 | -0.3581 | 1000 | B-3-1b |  |  | Transformer
WLEE2- | WLEE3A | 0.2583 | 12.2648 | -0.0357 | 120 | B-3-1b |  |  | Transformer
WLEE2- | WLEE3B | 0.2592 | 12.1922 | -0.0271 | 120 | B-3-1b |  |  | Transformer
WLEE2- | WLEE3C | 0.26 | 12.3048 | -0.0301 | 120 | B-3-1b |  |  | Transformer
WLEX2- | WLEX3A | 0.2306 | 12.2562 | -0.0292 | 120 | B-3-1b |  |  | Transformer
WLEX2- | WLEX3B | 0.2306 | 12.2728 | -0.0271 | 120 | B-3-1b |  |  | Transformer
WLEX2- | WLEX3C | 0.2306 | 12.2728 | -0.0275 | 120 | B-3-1b |  |  | Transformer
ABHA4A | ABHA11 | 0.1658 | 8.4025 | -1.5604 | 275 | B-3-1c |  |  | Transformer
ABHA4B | ABHA12 | 0.1658 | 8.4025 | -1.5604 | 264 | B-3-1c |  |  | Transformer
ABTH21 | ABTH11 | 0.1366 | 8.0648 | -0.0471 | 279 | B-3-1c |  |  | Transformer
ABTH21 | ABTH12 | 0.1646 | 8.0383 | -0.1808 | 211 | B-3-1c |  |  | Transformer
ABTH21 | ABTH13 | 0.0977 | 8.1994 | -1.7127 | 212 | B-3-1c |  |  | Transformer
ALDW21 | ALDW31 | 0.4848 | 24.6692 | -0.018 | 135 | B-3-1c |  |  | Transformer
ALDW21 | ALDW31 | 0.3543 | 25.4142 | -0.4983 | 135 | B-3-1c |  |  | Transformer
ALDW21 | ALDW31 | 0.7076 | 26.5771 | -0.0784 | 83 | B-3-1c |  |  | Transformer
ALDW21 | ALDW32 | 0.656 | 25.925 | -0.297 | 98 | B-3-1c |  |  | Transformer
ALDW21 | ALDW32 | 0.656 | 25.925 | -0.297 | 98 | B-3-1c |  |  | Transformer
AMEM4A | AMEM11 | 0.1471 | 8.4008 | -0.1719 | 270 | B-3-1c |  |  | Transformer
AMEM4A | AMEM11 | 0.1303 | 7.8698 | -0.4285 | 240 | B-3-1c |  |  | Transformer
AMEM4B | AMEM11 | 0.1471 | 8.4008 | -0.1719 | 255 | B-3-1c |  |  | Transformer
AXMI41 | AXMI11 | 0.148 | 7.4973 | -0.3849 | 278 | B-3-1c |  |  | Transformer
AXMI41 | AXMI11 | 0.148 | 7.4973 | -0.3849 | 277 | B-3-1c |  |  | Transformer
BARK21 | BARK11 | 0.1264 | 8.6657 | -0.0342 | 278 | B-3-1c |  |  | Transformer
BARK21 | BARK11 | 0.1264 | 8.6657 | -0.0342 | 268 | B-3-1c |  |  | Transformer
BARK21 | BARW31 | 0.618 | 29.2635 | -0.2527 | 109 | B-3-1c |  |  | Transformer
BARK21 | BARW32 | 0.618 | 29.2635 | -0.2527 | 110 | B-3-1c |  |  | Transformer
BARK22 | BARK11 | 0.1221 | 8.0467 | -0.0391 | 217 | B-3-1c |  |  | Transformer
BARK22 | BARK11 | 0.1183 | 8.3927 | -0.2368 | 240 | B-3-1c |  |  | Transformer
BARK22 | BARW31 | 0.618 | 29.2635 | -0.2527 | 110 | B-3-1c |  |  | Transformer
BARK22 | BARW32 | 0.618 | 29.2635 | -0.2527 | 109 | B-3-1c |  |  | Transformer
BARK22 | BARW32 | 0.492 | 19.4438 | -0.4018 | 100 | B-3-1c |  |  | Transformer
BARK41 | BARK21 | 0.0268 | 2.7989 | -0.3188 | 817 | B-3-1c |  |  | Transformer
BARK41 | BARK22 | 0.0268 | 2.7989 | -0.3188 | 817 | B-3-1c |  |  | Transformer
BEDD21 | BEDD11 | 0.167 | 7.9774 | -0.2092 | 258 | B-3-1c |  |  | Transformer
BEDD21 | BEDD12 | 0.1067 | 8.0868 | -0.034 | 264 | B-3-1c |  |  | Transformer
BEDD21 | BEDT1A | 0.1007 | 8.1333 | -0.2371 | 133 | B-3-1c |  |  | Transformer
BEDD22 | BEDD12 | 0.1067 | 8.0868 | -0.034 | 273 | B-3-1c |  |  | Transformer
BEDD23 | BEDD11 | 0.167 | 7.9774 | -0.2092 | 273 | B-3-1c |  |  | Transformer
BEDD23 | BEDT1B | 0.2264 | 12.2479 | -0.6062 | 126 | B-3-1c |  |  | Transformer
BEDD4A | BEDD21 | 0.0258 | 2.6799 | -1.2431 | 797 | B-3-1c |  |  | Transformer
BEDD4A | BEDD23 | 0.0258 | 2.6799 | -1.2431 | 797 | B-3-1c |  |  | Transformer
BEDD4B | BEDD21 | 0.0258 | 2.6799 | -1.2431 | 800 | B-3-1c |  |  | Transformer
BEDD4B | BEDD22 | 0.0258 | 2.6805 | -1.2431 | 950 | B-3-1c |  |  | Transformer
BESW21 | BESW11 | 0.1004 | 8.1994 | -0.2371 | 240 | B-3-1c |  |  | Transformer
BESW21 | BESW11 | 0.1411 | 8.6331 | -0.2264 | 273 | B-3-1c |  |  | Transformer
BESW21 | BESW12 | 0.1411 | 8.6331 | -0.2264 | 267 | B-3-1c |  |  | Transformer
BESW21 | BESW12 | 0.1411 | 8.6331 | -0.2264 | 267 | B-3-1c |  |  | Transformer
BICF41 | BICF11 | 0.1307 | 7.9515 | -0.1098 | 278 | B-3-1c |  |  | Transformer
BICF41 | BICF11 | 0.1307 | 7.9515 | -0.1098 | 274 | B-3-1c |  |  | Transformer
BIGG41 | BIGG11 | 0.148 | 8.1678 | -0.3849 | 240 | B-3-1c |  |  | Transformer
BIGG41 | BIGG11 | 0.148 | 8.1678 | -0.3849 | 240 | B-3-1c |  |  | Transformer
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 261 | B-3-1c |  |  | Transformer
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 261 | B-3-1c |  |  | Transformer
BIRK21 | BIRK11 | 0.1594 | 8.6081 | -0.2215 | 261 | B-3-1c |  |  | Transformer
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 279 | B-3-1c |  |  | Transformer
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 279 | B-3-1c |  |  | Transformer
BISW21 | BISW11 | 0.0918 | 8.7537 | -0.0575 | 278 | B-3-1c |  |  | Transformer
BISW21 | BISW11 | 0.1623 | 8.097 | -1.5978 | 240 | B-3-1c |  |  | Transformer
BLYT21 | BLYT1A | 0.1666 | 8.378 | -0.1047 | 278 | B-3-1c |  |  | Transformer
BLYT21 | BLYT1B | 0.1666 | 8.378 | -0.1047 | 278 | B-3-1c |  |  | Transformer
BLYT21 | BLYT61 | 0.2275 | 10.8456 | -0.0697 | 209 | B-3-1c |  |  | Transformer
BLYT21 | BLYT61 | 0.45 | 16.8273 | -1.3475 | 138 | B-3-1c |  |  | Transformer
BLYT21 | BLYT61 | 0.45 | 16.8273 | -1.3475 | 138 | B-3-1c |  |  | Transformer
BLYT41 | BLYT21 | 0.0152 | 1.6463 | -0.1118 | 1148 | B-3-1c |  |  | Transformer
BLYT41 | BLYT21 | 0.0152 | 1.6463 | -0.1118 | 1148 | B-3-1c |  |  | Transformer
BODE41 | SASA11 | 0.1311 | 7.9055 | -0.1016 | 240 | B-3-1c |  |  | Transformer
BOLN41 | BOLN11 | 0.137 | 7.9818 | -0.1471 | 310 | B-3-1c |  |  | Transformer
BOLN41 | BOLN11 | 0.137 | 7.9818 | -0.1471 | 309 | B-3-1c |  |  | Transformer
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 276 | B-3-1c |  |  | Transformer
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 277 | B-3-1c |  |  | Transformer
BOLN41 | BOLN12 | 0.137 | 7.9818 | -0.1471 | 309 | B-3-1c |  |  | Transformer
BOTW41 | BOTW11 | 0.1139 | 8.1036 | -2.059 | 278 | B-3-1c |  |  | Transformer
BOTW41 | BOTW11 | 0.1139 | 8.1036 | -2.059 | 278 | B-3-1c |  |  | Transformer
BRAI4A | BRAI11 | 0.1373 | 8.1976 | -0.1719 | 240 | B-3-1c |  |  | Transformer
BRAI4B | BRAI11 | 0.1307 | 7.9515 | -0.1098 | 278 | B-3-1c |  |  | Transformer
BRAW21 | BRAW11 | 0.1719 | 8.2312 | -0.9928 | 279 | B-3-1c |  |  | Transformer
BRAW21 | BRAW11 | 0.1719 | 8.2312 | -0.9928 | 279 | B-3-1c |  |  | Transformer
BRAW21 | BRAW12 | 0.1719 | 8.2312 | -0.9928 | 279 | B-3-1c |  |  | Transformer
BRAW21 | BRAW12 | 0.1719 | 8.2312 | -0.9928 | 279 | B-3-1c |  |  | Transformer
BRAW4A | BRAW21 | 0.0175 | 1.5879 | -4.0069 | 1094 | B-3-1c |  |  | Transformer
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 278 | B-3-1c |  |  | Transformer
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 278 | B-3-1c |  |  | Transformer
BRED21 | BRED11 | 0.1266 | 8.6449 | -1.9406 | 278 | B-3-1c |  |  | Transformer
BRFO41 | BRFO11 | 0.1658 | 8.4025 | -1.5604 | 272 | B-3-1c |  |  | Transformer
BRFO41 | BRFO11 | 0.1658 | 8.4025 | -1.5604 | 271 | B-3-1c |  |  | Transformer
BRFO41 | BRFO11 | 0.1307 | 7.9515 | -0.1098 | 240 | B-3-1c |  |  | Transformer
BRFO41 | BRFO12 | 0.1658 | 8.4025 | -1.5604 | 267 | B-3-1c |  |  | Transformer
BRFO41 | BRFO12 | 0.1658 | 8.4025 | -1.5604 | 267 | B-3-1c |  |  | Transformer
BRIM2A | BRIM11 | 0.1688 | 8.3316 | -1.1711 | 263 | B-3-1c |  |  | Transformer
BRIM2B | BRIM11 | 0.1266 | 8.6449 | -1.9406 | 274 | B-3-1c |  |  | Transformer
BRIN41 | BRIN21 | 0.0146 | 1.609 | -1.8746 | 1117 | B-3-1c |  |  | Transformer
BRIN41 | BRIN22 | 0.0133 | 1.5936 | -1.2059 | 1100 | B-3-1c |  |  | Transformer
BRLE41 | BRLE11 | 0.103 | 7.9231 | -0.0638 | 275 | B-3-1c |  |  | Transformer
BRLE41 | BRLE12 | 0.1471 | 8.4008 | -0.1719 | 253 | B-3-1c |  |  | Transformer
BRLE41 | BRLE13 | 0.1471 | 8.4008 | -0.1719 | 253 | B-3-1c |  |  | Transformer
BRLE41 | BRLE14 | 0.103 | 7.9231 | -0.0638 | 270 | B-3-1c |  |  | Transformer
BRLE41 | BRLE1A | 0.1303 | 7.8698 | -0.4285 | 263 | B-3-1c |  |  | Transformer
BRLE41 | BRLE1B | 0.1303 | 7.8698 | -0.4285 | 263 | B-3-1c |  |  | Transformer
BRWA41 | BRWA11 | 0.1047 | 8.2285 | -0.0886 | 240 | B-3-1c |  |  | Transformer
BRWA42 | BRWA11 | 0.1047 | 8.2285 | -0.0886 | 240 | B-3-1c |  |  | Transformer
BURW41 | BURW11 | 0.1059 | 8.3327 | -0.671 | 264 | B-3-1c |  |  | Transformer
BURW41 | BURW11 | 0.1056 | 8.2208 | -0.6711 | 264 | B-3-1c |  |  | Transformer
BURW41 | BURW11 | 0.1347 | 7.9905 | -0.1259 | 278 | B-3-1c |  |  | Transformer
BUSH21 | BUSH11 | 0.1221 | 8.0467 | -0.0391 | 279 | B-3-1c |  |  | Transformer
BUSH21 | BUSH11 | 0.1221 | 8.0467 | -0.0391 | 279 | B-3-1c |  |  | Transformer
BUSH21 | BUSH11 | 0.1048 | 8.8443 | -0.0335 | 278 | B-3-1c |  |  | Transformer
BUST21 | BUST11 | 0.1688 | 8.3316 | -1.1711 | 279 | B-3-1c |  |  | Transformer
BUST21 | BUST11 | 0.1719 | 8.2312 | -0.9928 | 279 | B-3-1c |  |  | Transformer
BUST21 | BUST11 | 0.1719 | 8.2312 | -0.9928 | 278 | B-3-1c |  |  | Transformer
BUST21 | BUST11 | 0.1688 | 8.3316 | -1.1711 | 279 | B-3-1c |  |  | Transformer
BUST4A | BUST21 | 0.018 | 1.6146 | -1.5533 | 1100 | B-3-1c |  |  | Transformer
BUST4B | BUST21 | 0.018 | 1.6146 | -1.5533 | 1100 | B-3-1c |  |  | Transformer
CANT41 | CANT13 | 0.1509 | 8.2849 | -0.3279 | 264 | B-3-1c |  |  | Transformer
CANT41 | CANT14 | 0.1658 | 8.426 | -0.2939 | 264 | B-3-1c |  |  | Transformer
CAPE21 | CAPE11 | 0.1927 | 8.5256 | -0.5357 | 211 | B-3-1c |  |  | Transformer
CAPE21 | CAPE11 | 0.1927 | 8.5256 | -0.5357 | 211 | B-3-1c |  |  | Transformer
CAPE21 | CAPE11 | 0.196 | 8.3446 | -0.7059 | 198 | B-3-1c |  |  | Transformer
CAPE21 | CAPE1A | 0.1366 | 8.0648 | -0.0471 | 279 | B-3-1c |  |  | Transformer
CAPE21 | CAPE1B | 0.171 | 8.8392 | -0.0268 | 211 | B-3-1c |  |  | Transformer
CAPE4A | CAPE21 | 0.0178 | 1.5995 | -1.2431 | 845 | B-3-1c |  |  | Transformer
CAPE4B | CAPE21 | 0.0185 | 1.614 | -0.5638 | 886 | B-3-1c |  |  | Transformer
CARE21 | CARE11 | 0.0918 | 8.7537 | -0.0575 | 278 | B-3-1c |  |  | Transformer
CARE21 | CARE11 | 0.0918 | 8.7537 | -0.0575 | 278 | B-3-1c |  |  | Transformer
CARR21 | CARR11 | 0.1927 | 8.5256 | -0.5357 | 211 | B-3-1c |  |  | Transformer
CARR21 | CARR11 | 0.1681 | 8.3396 | -1.4878 | 201 | B-3-1c |  |  | Transformer
CARR21 | CARR12 | 0.1927 | 8.5256 | -0.5357 | 211 | B-3-1c |  |  | Transformer
CARR21 | CARR12 | 0.2264 | 12.2479 | -0.6062 | 129 | B-3-1c |  |  | Transformer
CARR21 | CARR12 | 0.2847 | 12.2467 | -1.4346 | 120 | B-3-1c |  |  | Transformer
CARR41 | CARR11 | 0.1372 | 8.0197 | -0.1238 | 272 | B-3-1c |  |  | Transformer
CARR4A | CARR21 | 0.0185 | 1.614 | -0.5638 | 886 | B-3-1c |  |  | Transformer
CARR4B | CARR21 | 0.0185 | 1.614 | -0.5638 | 886 | B-3-1c |  |  | Transformer
CELL41 | CELL11 | 0.1658 | 8.4025 | -1.5604 | 280 | B-3-1c |  |  | Transformer
CELL41 | CELL11 | 0.1307 | 7.9515 | -0.1098 | 278 | B-3-1c |  |  | Transformer
CELL41 | CELL11 | 0.1658 | 8.4025 | -1.5604 | 274 | B-3-1c |  |  | Transformer
CELL41 | CELL12 | 0.1373 | 8.1976 | -0.1719 | 278 | B-3-1c |  |  | Transformer
CELL41 | CELL12 | 0.1658 | 8.4025 | -1.5604 | 278 | B-3-1c |  |  | Transformer
CHIC41 | CHIC11 | 0.1471 | 8.4008 | -0.1719 | 254 | B-3-1c |  |  | Transformer
CHIC41 | CHIC11 | 0.1471 | 8.4008 | -0.1719 | 253 | B-3-1c |  |  | Transformer
CHSI21 | CHSI11 | 0.167 | 7.9774 | -0.2092 | 255 | B-3-1c |  |  | Transformer
CHSI21 | CHSI11 | 0.1411 | 8.6331 | -0.2264 | 249 | B-3-1c |  |  | Transformer
CHSI21 | CHSI1A | 0.0978 | 8.1332 | -0.0252 | 153 | B-3-1c |  |  | Transformer
CHSI21 | CHSI1B | 0.1411 | 8.6331 | -1.598 | 240 | B-3-1c |  |  | Transformer
CILF41 | CILF2A | 0.017 | 1.6132 | -5.1203 | 750 | B-3-1c |  |  | Transformer
CILF41 | CILF2B | 0.017 | 1.6132 | -5.1203 | 750 | B-3-1c |  |  | Transformer
CITR41 | CITR11 | 0.1373 | 8.1976 | -0.1719 | 278 | B-3-1c |  |  | Transformer
CITR41 | CITR11 | 0.1373 | 8.1976 | -0.1719 | 278 | B-3-1c |  |  | Transformer
CITR41 | CITR11 | 0.1229 | 8.3873 | -0.1147 | 269 | B-3-1c |  |  | Transformer
CITR41 | CITR11 | 0.1132 | 8.2492 | -0.1115 | 278 | B-3-1c |  |  | Transformer
CITR41 | CITR12 | 0.1264 | 7.974 | -0.1303 | 277 | B-3-1c |  |  | Transformer
CITR41 | CITR12 | 0.1132 | 8.2492 | -0.1115 | 278 | B-3-1c |  |  | Transformer
CONQ41 | CONQ11 | 0.1044 | 7.8701 | -0.103 | 261 | B-3-1c |  |  | Transformer
CONQ41 | CONQ11 | 0.1036 | 7.8606 | -0.1003 | 259 | B-3-1c |  |  | Transformer
CONQ41 | CONQ12 | 0.1045 | 7.8806 | -0.0998 | 263 | B-3-1c |  |  | Transformer
CONQ41 | CONQ13 | 0.1057 | 7.9352 | -0.339 | 240 | B-3-1c |  |  | Transformer
COVE21 | COVE11 | 0.1623 | 8.097 | -1.5978 | 273 | B-3-1c |  |  | Transformer
COVE21 | COVE11 | 0.1623 | 8.097 | -1.5978 | 272 | B-3-1c |  |  | Transformer
COVE21 | COVE12 | 0.1623 | 8.097 | -1.5978 | 266 | B-3-1c |  |  | Transformer
COVE21 | COVE12 | 0.1004 | 8.1994 | -0.2371 | 240 | B-3-1c |  |  | Transformer
COWL41 | COWL11 | 0.1307 | 7.9515 | -0.1098 | 278 | B-3-1c |  |  | Transformer
COWL41 | COWL11 | 0.1847 | 8.1296 | -0.2979 | 269 | B-3-1c |  |  | Transformer
COWL41 | COWL11 | 0.1847 | 8.1296 | -0.2979 | 269 | B-3-1c |  |  | Transformer
COWL41 | COWL12 | 0.1847 | 8.1296 | -0.2979 | 269 | B-3-1c |  |  | Transformer
COWL41 | COWL12 | 0.1847 | 8.1296 | -0.2979 | 269 | B-3-1c |  |  | Transformer
CREB41 | CREB11 | 0.1621 | 8.0984 | -0.0747 | 253 | B-3-1c |  |  | Transformer
CREB41 | CREB11 | 0.1621 | 8.0984 | -0.0747 | 274 | B-3-1c |  |  | Transformer
CREB41 | CREB12 | 0.1621 | 8.0984 | -0.0747 | 253 | B-3-1c |  |  | Transformer
CREB41 | CREB12 | 0.1621 | 8.0984 | -0.0747 | 253 | B-3-1c |  |  | Transformer
CREB41 | CREB2A | 0.0176 | 1.5826 | -0.1148 | 750 | B-3-1c |  |  | Transformer
CREB41 | CREB2A | 0.0176 | 1.5826 | -0.1148 | 750 | B-3-1c |  |  | Transformer
CREB41 | CREB2B | 0.0176 | 1.5826 | -0.1148 | 750 | B-3-1c |  |  | Transformer
CREB41 | CREB2B | 0.0176 | 1.5826 | -0.1148 | 750 | B-3-1c |  |  | Transformer
CULJ4A | CULJ31 | 0.069 | 25 | 0 | 90 | B-3-1c |  |  | Transformer
CULJ4A | CULJ32 | 0.069 | 25 | 0 | 90 | B-3-1c |  |  | Transformer
CULJ4A | CULJ33 | 0.069 | 25 | 0 | 90 | B-3-1c |  |  | Transformer
DIDC41 | MILP31 | 0.2087 | 15.2319 | -0.2971 | 150 | B-3-1c |  |  | Transformer
DIDC41 | MILP31 | 0.2099 | 15.2986 | -0.2971 | 150 | B-3-1c |  |  | Transformer
DRAK41 | DRAK11 | 0.1303 | 7.8698 | -0.4285 | 278 | B-3-1c |  |  | Transformer
DRAK41 | DRAK11 | 0.1044 | 7.881 | -0.0832 | 240 | B-3-1c |  |  | Transformer
DRAK41 | DRAK21 | 0.0178 | 1.5995 | -1.2431 | 849 | B-3-1c |  |  | Transformer
DRAX41 | DRAX11 | 0.1658 | 8.4025 | -1.5604 | 277 | B-3-1c |  |  | Transformer
DRAX41 | DRAX11 | 0.1658 | 8.4025 | -1.5604 | 274 | B-3-1c |  |  | Transformer
DRAX42 | CAML61 | 0.2216 | 14.1082 | -0.1552 | 206 | B-3-1c |  |  | Transformer
DRAX42 | CAML61 | 0.2216 | 14.1082 | -0.1552 | 206 | B-3-1c |  |  | Transformer
DUNG41 | DUNG21 | 0.017 | 1.6132 | -5.1203 | 440 | B-3-1c |  |  | Transformer
DUNG41 | DUNG21 | 0.017 | 1.6132 | -5.1203 | 440 | B-3-1c |  |  | Transformer
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 134 | B-3-1c |  |  | Transformer
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 134 | B-3-1c |  |  | Transformer
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 126 | B-3-1c |  |  | Transformer
EALI21 | EALI61 | 0.3062 | 11.0235 | -0.4552 | 126 | B-3-1c |  |  | Transformer
EASO41 | EASO12 | 0.103 | 7.9231 | -0.0638 | 263 | B-3-1c |  |  | Transformer
EASO41 | LITB11 | 0.1018 | 7.841 | -0.432 | 240 | B-3-1c |  |  | Transformer
EASO4A | EASO11 | 0.103 | 7.9231 | -0.0638 | 263 | B-3-1c |  |  | Transformer
ECLA41 | ECLA11 | 0.1175 | 8.6648 | -0.4173 | 264 | B-3-1c |  |  | Transformer
ECLA41 | ECLA11 | 0.1175 | 8.6648 | -0.4173 | 263 | B-3-1c |  |  | Transformer
ECLA41 | ECLA12 | 0.1139 | 8.1036 | -2.059 | 278 | B-3-1c |  |  | Transformer
ECLA41 | ECLA12 | 0.0997 | 8.0088 | -0.093 | 264 | B-3-1c |  |  | Transformer
ELLA21 | ELLA11 | 0.1221 | 8.0467 | -0.0391 | 272 | B-3-1c |  |  | Transformer
ELLA21 | ELLA11 | 0.1681 | 8.3396 | -1.4878 | 198 | B-3-1c |  |  | Transformer
ELLA21 | ELLA12 | 0.1221 | 8.0467 | -0.0391 | 279 | B-3-1c |  |  | Transformer
ELLA21 | ELLA12 | 0.1722 | 8.4551 | -0.2968 | 211 | B-3-1c |  |  | Transformer
ELST21 | ELST12 | 0.1221 | 8.0467 | -0.0391 | 279 | B-3-1c |  |  | Transformer
ELST21 | ELST13 | 0.1985 | 8.1167 | -0.4624 | 189 | B-3-1c |  |  | Transformer
ELST21 | ELST13 | 0.1954 | 8.0796 | -0.2295 | 189 | B-3-1c |  |  | Transformer
ELST22 | ELST11 | 0.1031 | 8.1045 | -0.0494 | 212 | B-3-1c |  |  | Transformer
ELST22 | ELST11 | 0.1923 | 8.081 | -1.4418 | 187 | B-3-1c |  |  | Transformer
ELST41 | ELST12 | 0.1039 | 7.8456 | -0.9345 | 240 | B-3-1c |  |  | Transformer
ELST41 | ELST22 | 0.0181 | 1.5835 | -3.6502 | 1201 | B-3-1c |  |  | Transformer
ELST4B | ELST21 | 0.0176 | 1.5828 | -0.1018 | 1137 | B-3-1c |  |  | Transformer
ENDE41 | ENDE11 | 0.1303 | 7.8698 | -0.4285 | 278 | B-3-1c |  |  | Transformer
ENDE41 | ENDE11 | 0.1118 | 8.3874 | -0.0906 | 278 | B-3-1c |  |  | Transformer
ENDE41 | ENDE11 | 0.1658 | 8.4025 | -1.5604 | 274 | B-3-1c |  |  | Transformer
ENDE41 | ENDE11 | 0.1658 | 8.4025 | -1.5604 | 273 | B-3-1c |  |  | Transformer
EXET41 | EXET11 | 0.1307 | 7.9515 | -0.1098 | 278 | B-3-1c |  |  | Transformer
EXET41 | EXET11 | 0.1509 | 8.2849 | -0.3279 | 278 | B-3-1c |  |  | Transformer
EXET41 | EXET11 | 0.1509 | 8.2849 | -0.3279 | 269 | B-3-1c |  |  | Transformer
FAWL41 | FAWL11 | 0.1509 | 7.9231 | -0.5982 | 268 | B-3-1c |  |  | Transformer
FAWL41 | FAWL11 | 0.1509 | 7.9231 | -0.5982 | 268 | B-3-1c |  |  | Transformer
FAWL41 | FAWL11 | 0.105 | 8.1922 | -0.1118 | 268 | B-3-1c |  |  | Transformer
FECK21 | FECK61 | 0.3142 | 15.7855 | -1.1826 | 139 | B-3-1c |  |  | Transformer
FECK41 | FECK21 | 0.0161 | 1.6372 | -0.0621 | 1100 | B-3-1c |  |  | Transformer
FECK41 | FECK61 | 0.1832 | 14.0317 | -0.1803 | 199 | B-3-1c |  |  | Transformer
FECK41 | FECK61 | 0.1867 | 13.8218 | -0.1803 | 194 | B-3-1c |  |  | Transformer
FECK41 | FECK61 | 0.1867 | 13.8218 | -0.1803 | 194 | B-3-1c |  |  | Transformer
FERR21 | FERR11 | 0.1147 | 8.673 | -0.0358 | 278 | B-3-1c |  |  | Transformer
FERR21 | FERR61 | 0.237 | 10.8633 | -0.263 | 204 | B-3-1c |  |  | Transformer
FERR23 | FERR11 | 0.1147 | 8.673 | -0.0358 | 278 | B-3-1c |  |  | Transformer
FERR23 | FERR61 | 0.237 | 10.8633 | -0.263 | 203 | B-3-1c |  |  | Transformer
FERR2A | FERR11 | 0.0918 | 8.7537 | -0.0575 | 278 | B-3-1c |  |  | Transformer
FERR4A | FERR22 | 0.0133 | 1.5936 | -1.2059 | 1100 | B-3-1c |  |  | Transformer
FERR4A | FERR23 | 0.0186 | 1.5729 | -7.729 | 1113 | B-3-1c |  |  | Transformer
FIDF21 | FIDF11 | 0.1392 | 8.4361 | -0.781 | 271 | B-3-1c |  |  | Transformer
FIDF21 | FIDF12 | 0.1594 | 8.6081 | -0.2215 | 261 | B-3-1c |  |  | Transformer
FLEE41 | FLEE11 | 0.1557 | 8.3736 | -0.4146 | 279 | B-3-1c |  |  | Transformer
FLEE41 | FLEE11 | 0.1368 | 8.5406 | -0.262 | 232 | B-3-1c |  |  | Transformer
FLEE41 | FLEE11 | 0.1557 | 8.3736 | -0.4146 | 274 | B-3-1c |  |  | Transformer
FLEE41 | FLEE11 | 0.1372 | 8.0197 | -0.1238 | 278 | B-3-1c |  |  | Transformer
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 279 | B-3-1c |  |  | Transformer
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 279 | B-3-1c |  |  | Transformer
FLEE41 | FLEE12 | 0.1557 | 8.3736 | -0.4146 | 279 | B-3-1c |  |  | Transformer
FOUR21 | FOUR31 | 0.306 | 19.9977 | -0.5499 | 100 | B-3-1c |  |  | Transformer
FOUR21 | FOUR71 | 1.2544 | 65.7103 | -0.0257 | 45 | B-3-1c |  |  | Transformer
FOUR21 | FOUR71 | 1.2544 | 65.7103 | -0.0257 | 45 | B-3-1c |  |  | Transformer
FROD21 | FROD11 | 0.1927 | 8.5256 | -0.5357 | 211 | B-3-1c |  |  | Transformer
FROD22 | FROD11 | 0.1392 | 8.4361 | -0.781 | 269 | B-3-1c |  |  | Transformer
FROD41 | FROD11 | 0.054 | 4.8906 | -0.1253 | 499 | B-3-1c |  |  | Transformer
FROD41 | FROD21 | 0.0176 | 1.5828 | -0.1018 | 1000 | B-3-1c |  |  | Transformer
FROD41 | FROD22 | 0.0132 | 1.6756 | -0.4337 | 1063 | B-3-1c |  |  | Transformer
FROD41 | WEAV71 | 0.0032 | 0.0205 | -0.1224 | 80 | B-3-1c |  |  | Transformer
FROD41 | WEAV71 | 0.0032 | 0.0205 | -0.1224 | 80 | B-3-1c |  |  | Transformer
GRAI41 | GRAI11 | 0.1307 | 7.9515 | -0.1098 | 263 | B-3-1c |  |  | Transformer
GRAI41 | GRAI11 | 0.1307 | 7.9515 | -0.1098 | 263 | B-3-1c |  |  | Transformer
GREN41 | GREN11 | 0.1557 | 8.3736 | -0.4146 | 279 | B-3-1c |  |  | Transformer
GREN41 | GREN11 | 0.1312 | 7.9156 | -0.537 | 278 | B-3-1c |  |  | Transformer
GREN41 | GREN11 | 0.1557 | 8.3736 | -0.4146 | 278 | B-3-1c |  |  | Transformer
GREN41 | GREN12 | 0.1557 | 8.3736 | -0.4146 | 279 | B-3-1c |  |  | Transformer
GREN41 | GREN12 | 0.1035 | 7.8472 | -0.0758 | 274 | B-3-1c |  |  | Transformer
GRIW41 | GRIW11 | 0.1658 | 8.4025 | -1.5604 | 273 | B-3-1c |  |  | Transformer
GRIW41 | GRIW12 | 0.1658 | 8.4025 | -1.5604 | 268 | B-3-1c |  |  | Transformer
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278 | B-3-1c |  |  | Transformer
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278 | B-3-1c |  |  | Transformer
HACK41 | HACK11 | 0.1303 | 7.8698 | -0.4285 | 278 | B-3-1c |  |  | Transformer
HAMH41 | HAMH2A | 0.0175 | 1.5879 | -4.0069 | 1147 | B-3-1c |  |  | Transformer
HAMH41 | LEMR11 | 0.1094 | 8.5335 | -0.0989 | 278 | B-3-1c |  |  | Transformer
HAMH41 | LEMR11 | 0.1118 | 8.3874 | -0.0906 | 263 | B-3-1c |  |  | Transformer
HAMH41 | LEMR11 | 0.1118 | 8.3874 | -0.0906 | 263 | B-3-1c |  |  | Transformer
HAMH41 | LEMR11 | 0.1094 | 8.5335 | -0.0989 | 263 | B-3-1c |  |  | Transformer
HARM21 | HARM61 | 0.3726 | 16.7215 | -0.6945 | 127 | B-3-1c |  |  | Transformer
HARM21 | HARM61 | 0.3726 | 16.7215 | -0.6945 | 127 | B-3-1c |  |  | Transformer
HAWP21 | HAWP61 | 0.2793 | 13.3304 | -0.6737 | 192 | B-3-1c |  |  | Transformer
HAWP21 | HAWP61 | 0.2793 | 13.3304 | -0.6737 | 191 | B-3-1c |  |  | Transformer
HAWP4A | HAWP21 | 0.0132 | 1.6756 | -0.4337 | 1063 | B-3-1c |  |  | Transformer
HEYS41 | HEYS11 | 0.122 | 8.1963 | -0.2446 | 277 | B-3-1c |  |  | Transformer
HEYS41 | HEYS11 | 0.1658 | 8.4025 | -1.5604 | 275 | B-3-1c |  |  | Transformer
HEYS41 | HEYS11 | 0.1372 | 8.0197 | -0.1238 | 278 | B-3-1c |  |  | Transformer
HIBU41 | ISLI11 | 0.1264 | 8.4534 | -0.357 | 240 | B-3-1c |  |  | Transformer
HIBU41 | ISLI11 | 0.1264 | 8.4534 | -0.357 | 240 | B-3-1c |  |  | Transformer
HIBU41 | ISLI11 | 0.1264 | 8.4534 | -0.357 | 240 | B-3-1c |  |  | Transformer
HINP41 | HINP21 | 0.0363 | 2.4397 | -2.1073 | 539 | B-3-1c |  |  | Transformer
HINP41 | HINP22 | 0.0376 | 2.3797 | -3.9009 | 539 | B-3-1c |  |  | Transformer
HUMR41 | HUMR31 | 0.6667 | 22.467 | -0.1612 | 90 | B-3-1c |  |  | Transformer
HUMR41 | HUMR31 | 0.6667 | 22.256 | -0.1612 | 90 | B-3-1c |  |  | Transformer
HURS21 | HURS1B | 0.1221 | 8.0467 | -0.0391 | 279 | B-3-1c |  |  | Transformer
HURS21 | HURS1C | 0.1382 | 8.1742 | -0.1786 | 279 | B-3-1c |  |  | Transformer
HURS21 | HURS1D | 0.1392 | 8.4361 | -0.781 | 279 | B-3-1c |  |  | Transformer
HUTT41 | HUTT11 | 0.1621 | 8.0984 | -0.0747 | 265 | B-3-1c |  |  | Transformer
HUTT41 | HUTT11 | 0.1621 | 8.0984 | -0.0747 | 264 | B-3-1c |  |  | Transformer
HUTT41 | HUTT71 | 0.0032 | 0.0208 | 0 | 80 | B-3-1c |  |  | Transformer
HUTT41 | HUTT71 | 0.0032 | 0.0208 | 0 | 80 | B-3-1c |  |  | Transformer
IMPP41 | IMPP31 | 0.2262 | 15.019 | -0.0538 | 143 | B-3-1c |  |  | Transformer
IMPP41 | IMPP31 | 0.2262 | 15.019 | -0.0538 | 143 | B-3-1c |  |  | Transformer
INDQ41 | INDQ11 | 0.1302 | 8.4532 | -10.3672 | 278 | B-3-1c |  |  | Transformer
INDQ41 | INDQ11 | 0.1303 | 7.8698 | -0.4285 | 278 | B-3-1c |  |  | Transformer
INDQ41 | INDQ11 | 0.1278 | 8.0061 | -0.2276 | 256 | B-3-1c |  |  | Transformer
INDQ41 | INDQ11 | 0.1471 | 8.4008 | -0.1719 | 254 | B-3-1c |  |  | Transformer
IROA21 | IROA11 | 0.1221 | 8.0467 | -0.0391 | 279 | B-3-1c |  |  | Transformer
IROA21 | IROA11 | 0.1366 | 8.0648 | -0.0471 | 279 | B-3-1c |  |  | Transformer
IROA21 | IROA12 | 0.1053 | 8.0652 | -0.0304 | 217 | B-3-1c |  |  | Transformer
IROA21 | IROA12 | 0.1685 | 7.8148 | -1.385 | 210 | B-3-1c |  |  | Transformer
IROA21 | IROA13 | 0.1266 | 8.6449 | -1.9406 | 250 | B-3-1c |  |  | Transformer
IROA21 | IROA13 | 0.1685 | 7.8148 | -1.385 | 210 | B-3-1c |  |  | Transformer
IRON41 | IRON11 | 0.1557 | 8.3736 | -0.4146 | 278 | B-3-1c |  |  | Transformer
IRON41 | IRON12 | 0.1557 | 8.3736 | -0.4146 | 277 | B-3-1c |  |  | Transformer
IRON41 | IRON13 | 0.1372 | 8.0197 | -0.1238 | 278 | B-3-1c |  |  | Transformer
IVER21 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 279 | B-3-1c |  |  | Transformer
IVER21 | IVER11 | 0.1221 | 8.0467 | -0.0391 | 279 | B-3-1c |  |  | Transformer
IVER21 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 265 | B-3-1c |  |  | Transformer
IVER21 | IVER61 | 0.2856 | 11.1999 | -2.5672 | 153 | B-3-1c |  |  | Transformer
IVER21 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 125 | B-3-1c |  |  | Transformer
IVER21 | IVER61 | 0.3931 | 16.4953 | -2.1281 | 125 | B-3-1c |  |  | Transformer
IVER22 | IVER11 | 0.1366 | 8.0648 | -0.0471 | 279 | B-3-1c |  |  | Transformer
IVER22 | IVER61 | 0.2856 | 11.1999 | -2.5672 | 153 | B-3-1c |  |  | Transformer
IVER4A | IVER21 | 0.0176 | 1.5828 | -0.1018 | 1135 | B-3-1c |  |  | Transformer
IVER4A | IVER22 | 0.0133 | 1.5936 | -1.2059 | 1100 | B-3-1c |  |  | Transformer
IVER4B | IVER21 | 0.0326 | 2.3798 | -3.9003 | 572 | B-3-1c |  |  | Transformer
IVER4B | IVER2A | 0.0132 | 1.4627 | -2.0624 | 841 | B-3-1c |  |  | Transformer
JORD21 | JORD31 | 0.593 | 20.7915 | -0.122 | 110 | B-3-1c |  |  | Transformer
JORD21 | JORD31 | 0.593 | 20.7915 | -0.122 | 110 | B-3-1c |  |  | Transformer
KEAD41 | KEAD11 | 0.1621 | 8.0984 | -0.0747 | 256 | B-3-1c |  |  | Transformer
KEAD41 | KEAD11 | 0.1302 | 8.4532 | -10.3672 | 274 | B-3-1c |  |  | Transformer
KEAD42 | KEAD11 | 0.1118 | 8.3874 | -0.0906 | 278 | B-3-1c |  |  | Transformer
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278 | B-3-1c |  |  | Transformer
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278 | B-3-1c |  |  | Transformer
KEAR21 | KEAR11 | 0.1266 | 8.6449 | -1.9406 | 278 | B-3-1c |  |  | Transformer
KEAR21 | KEAR11 | 0.1041 | 8.1035 | -0.0269 | 280 | B-3-1c |  |  | Transformer
KEAR21 | KEAR31 | 0.4848 | 24.6692 | -0.018 | 96 | B-3-1c |  |  | Transformer
KEAR21 | KEAR31 | 0.4848 | 24.6692 | -0.018 | 96 | B-3-1c |  |  | Transformer
KEAR41 | KEAR21 | 0.0117 | 1.591 | -4.4806 | 1098 | B-3-1c |  |  | Transformer
KEAR41 | KEAR21 | 0.0175 | 1.5879 | -4.0069 | 1000 | B-3-1c |  |  | Transformer
KEMS41 | KEMS11 | 0.1658 | 8.426 | -0.2939 | 268 | B-3-1c |  |  | Transformer
KEMS41 | KEMS11 | 0.1139 | 8.1036 | -2.059 | 264 | B-3-1c |  |  | Transformer
KEMS41 | SHEE11 | 0.1621 | 8.0984 | -0.0747 | 236 | B-3-1c |  |  | Transformer
KIBY21 | KIBY11 | 0.1221 | 8.0467 | -0.0391 | 279 | B-3-1c |  |  | Transformer
KIBY21 | KIBY11 | 0.1221 | 8.0467 | -0.0391 | 279 | B-3-1c |  |  | Transformer
KIBY21 | KIBY11 | 0.1392 | 8.4361 | -0.781 | 279 | B-3-1c |  |  | Transformer
KIBY21 | KIBY11 | 0.1594 | 8.6081 | -0.2215 | 261 | B-3-1c |  |  | Transformer
KIBY21 | KIBY11 | 0.1681 | 8.3396 | -1.4878 | 211 | B-3-1c |  |  | Transformer
KINO41 | KINO11 | 0.1301 | 7.8864 | -0.5157 | 278 | B-3-1c |  |  | Transformer
KINO41 | KINO11 | 0.1758 | 8.1226 | -0.2746 | 274 | B-3-1c |  |  | Transformer
KIRK21 | KIRK11 | 0.1366 | 8.0648 | -0.0471 | 279 | B-3-1c |  |  | Transformer
KIRK21 | KIRK11 | 0.1147 | 8.673 | -0.0358 | 264 | B-3-1c |  |  | Transformer
KIRK21 | KIRK11 | 0.097 | 8.0997 | -0.027 | 266 | B-3-1c |  |  | Transformer
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279 | B-3-1c |  |  | Transformer
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279 | B-3-1c |  |  | Transformer
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279 | B-3-1c |  |  | Transformer
KITW21 | KITW11 | 0.1688 | 8.3316 | -1.1711 | 279 | B-3-1c |  |  | Transformer
KNAR21 | KNAR11 | 0.1441 | 8.6238 | -0.2707 | 240 | B-3-1c |  |  | Transformer
KNAR21 | KNAR11 | 0.1441 | 8.6238 | -0.2707 | 240 | B-3-1c |  |  | Transformer
LACK21 | GRTO61 | 0.262 | 16.5813 | -0.4096 | 133 | B-3-1c |  |  | Transformer
LACK21 | GRTO61 | 0.262 | 16.5813 | -0.4096 | 133 | B-3-1c |  |  | Transformer
LACK21 | LACK61 | 0.3726 | 16.7215 | -0.6945 | 128 | B-3-1c |  |  | Transformer
LACK21 | LACK61 | 0.4736 | 16.5344 | -0.54 | 126 | B-3-1c |  |  | Transformer
LACK21 | LACK61 | 0.3726 | 16.7215 | -0.6945 | 126 | B-3-1c |  |  | Transformer
LACK41 | LACK21 | 0.0175 | 1.5879 | -4.0069 | 1100 | B-3-1c |  |  | Transformer
LACK41 | LACK21 | 0.0174 | 1.598 | -0.1503 | 1154 | B-3-1c |  |  | Transformer
LACK41 | LACK2A | 0.0152 | 1.6463 | -0.1118 | 1185 | B-3-1c |  |  | Transformer
LACK41 | LACK2B | 0.0182 | 1.5763 | -0.0904 | 1210 | B-3-1c |  |  | Transformer
LALE21 | LALE11 | 0.1266 | 8.6449 | -1.9406 | 278 | B-3-1c |  |  | Transformer
LALE21 | LALE11 | 0.1266 | 8.6449 | -1.9406 | 278 | B-3-1c |  |  | Transformer
LALE21 | LALE11 | 0.1954 | 8.0796 | -0.2295 | 201 | B-3-1c |  |  | Transformer
LALE21 | LALE11 | 0.196 | 8.3446 | -0.7059 | 200 | B-3-1c |  |  | Transformer
LALE21 | LALE31 | 0.4848 | 24.6692 | -0.018 | 120 | B-3-1c |  |  | Transformer
LALE21 | LALE31 | 0.4848 | 24.6692 | -0.018 | 120 | B-3-1c |  |  | Transformer
LAND41 | LAND11 | 0.1372 | 8.0197 | -0.1238 | 278 | B-3-1c |  |  | Transformer
LAND41 | LAND11 | 0.148 | 7.4973 | -0.3849 | 278 | B-3-1c |  |  | Transformer
LAND42 | LAND11 | 0.1057 | 7.9352 | -0.339 | 263 | B-3-1c |  |  | Transformer
LEGA41 | LEGA11 | 0.1372 | 8.0197 | -0.1238 | 278 | B-3-1c |  |  | Transformer
LEGA41 | LEGA11 | 0.1372 | 8.0197 | -0.1238 | 278 | B-3-1c |  |  | Transformer
LEGA41 | LEGA11 | 0.1175 | 8.6648 | -0.4173 | 263 | B-3-1c |  |  | Transformer
LEGA41 | LEGA11 | 0.1303 | 7.8698 | -0.4285 | 278 | B-3-1c |  |  | Transformer
LEIS4A | LEIS11 | 0.1057 | 7.8601 | -0.432 | 272 | B-3-1c |  |  | Transformer
LISD21 | LISD11 | 0.1221 | 8.0467 | -0.0391 | 279 | B-3-1c |  |  | Transformer
LISD21 | LISD11 | 0.1441 | 8.6238 | -0.2707 | 266 | B-3-1c |  |  | Transformer
LISD21 | LISD11 | 0.1441 | 8.6238 | -0.2707 | 266 | B-3-1c |  |  | Transformer
LISD21 | LISD11 | 0.1266 | 8.6449 | -1.9406 | 262 | B-3-1c |  |  | Transformer
LITT41 | LITT11 | 0.1621 | 8.0984 | -0.0747 | 240 | B-3-1c |  |  | Transformer
LITT41 | LITT11 | 0.0997 | 8.0088 | -0.093 | 240 | B-3-1c |  |  | Transformer
LITT41 | LITT11 | 0.103 | 7.9231 | -0.0638 | 278 | B-3-1c |  |  | Transformer
LITT41 | LITT2A | 0.014 | 2.6567 | -0.1528 | 1028 | B-3-1c |  |  | Transformer
LITT41 | LITT2B | 0.014 | 2.6567 | -0.1528 | 1028 | B-3-1c |  |  | Transformer
LOVE41 | LOVE11 | 0.1303 | 7.8698 | -0.4285 | 278 | B-3-1c |  |  | Transformer
LOVE41 | LOVE11 | 0.1042 | 7.831 | 0 | 274 | B-3-1c |  |  | Transformer
LOVE41 | LOVE12 | 0.1758 | 8.1226 | -0.2746 | 274 | B-3-1c |  |  | Transformer
LOVE41 | LOVE12 | 0.1847 | 8.1296 | -0.2979 | 269 | B-3-1c |  |  | Transformer
MACC21 | MACC31 | 0.688 | 24.5904 | -0.1031 | 113 | B-3-1c |  |  | Transformer
MACC21 | MACC31 | 0.688 | 24.5904 | -0.1031 | 113 | B-3-1c |  |  | Transformer
MACC41 | MACC21 | 0.018 | 1.6146 | -1.5533 | 884 | B-3-1c |  |  | Transformer
MAGA21 | GRAN61 | 0.1642 | 10.921 | -0.0326 | 207 | B-3-1c |  |  | Transformer
MAGA21 | GRAN61 | 0.1757 | 10.5541 | -0.0326 | 205 | B-3-1c |  |  | Transformer
MANN41 | MANN11 | 0.1759 | 7.9134 | -0.267 | 279 | B-3-1c |  |  | Transformer
MANN41 | MANN11 | 0.1758 | 8.1226 | -0.2746 | 272 | B-3-1c |  |  | Transformer
MANN41 | MANN11 | 0.1758 | 8.1226 | -0.2746 | 272 | B-3-1c |  |  | Transformer
MANN41 | MANN11 | 0.1326 | 8.774 | -0.7141 | 259 | B-3-1c |  |  | Transformer
MANN41 | MANN11 | 0.1303 | 7.8698 | -0.4285 | 278 | B-3-1c |  |  | Transformer
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 278 | B-3-1c |  |  | Transformer
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 278 | B-3-1c |  |  | Transformer
MELK41 | MELK11 | 0.1184 | 8.3643 | -0.0435 | 278 | B-3-1c |  |  | Transformer
MELK41 | MELK11 | 0.1041 | 7.8535 | -0.0851 | 265 | B-3-1c |  |  | Transformer
MELK41 | MELK2A | 0.017 | 1.6132 | -5.1203 | 750 | B-3-1c |  |  | Transformer
MELK41 | MELK2B | 0 | 1.692 | 0 | 886 | B-3-1c |  |  | Transformer
MILH2A | MILH11 | 0.1266 | 8.6449 | -1.9406 | 264 | B-3-1c |  |  | Transformer
MILH2A | MILH11 | 0.179 | 8.3648 | -4.7616 | 211 | B-3-1c |  |  | Transformer
MILH2B | MILH12 | 0.1266 | 8.6449 | -1.9406 | 264 | B-3-1c |  |  | Transformer
MILH2B | MILH12 | 0.1004 | 8.1994 | -0.2371 | 240 | B-3-1c |  |  | Transformer
MITY41 | MITY11 | 0.1139 | 8.1036 | -2.059 | 263 | B-3-1c |  |  | Transformer
MITY41 | MITY11 | 0.122 | 8.1963 | -0.2446 | 274 | B-3-1c |  |  | Transformer
MITY41 | MITY12 | 0.1057 | 7.9352 | -0.339 | 263 | B-3-1c |  |  | Transformer
MITY41 | MITY12 | 0.1812 | 9.1787 | -0.1253 | 278 | B-3-1c |  |  | Transformer
MONF41 | MONF21 | 0.0181 | 1.6409 | -0.1418 | 1100 | B-3-1c |  |  | Transformer
MONF41 | MONF22 | 0.0181 | 1.6409 | -0.1418 | 1100 | B-3-1c |  |  | Transformer
NECH21 | NECH11 | 0.1411 | 8.6331 | -0.2264 | 270 | B-3-1c |  |  | Transformer
NECH21 | NECH11 | 0.1411 | 8.6331 | -0.2264 | 269 | B-3-1c |  |  | Transformer
NECH21 | NECH12 | 0.1411 | 8.6331 | -0.2264 | 267 | B-3-1c |  |  | Transformer
NECH21 | NECH12 | 0.1411 | 8.6331 | -0.2264 | 270 | B-3-1c |  |  | Transformer
NEEP21 | NEEP31 | 0.5083 | 24.0899 | -0.1921 | 120 | B-3-1c |  |  | Transformer
NEEP21 | NEEP31 | 0.5083 | 24.0899 | -0.1921 | 120 | B-3-1c |  |  | Transformer
NEEP4A | NEEP21 | 0.021 | 1.669 | -12.6082 | 1100 | B-3-1c |  |  | Transformer
NEWX21 | NEWX11 | 0.1338 | 8.0531 | -0.1824 | 279 | B-3-1c |  |  | Transformer
NEWX21 | NEWX11 | 0.1338 | 8.0531 | -0.1824 | 279 | B-3-1c |  |  | Transformer
NEWX21 | NEWX11 | 0.1053 | 8.0451 | -0.0277 | 280 | B-3-1c |  |  | Transformer
NEWX21 | NEWX61 | 0.2188 | 10.8367 | -0.1908 | 180 | B-3-1c |  |  | Transformer
NEWX21 | NEWX61 | 0.3204 | 14.3298 | -0.2424 | 180 | B-3-1c |  |  | Transformer
NEWX21 | NEWX62 | 0.2972 | 12.4333 | -0.1533 | 209 | B-3-1c |  |  | Transformer
NEWX21 | NEWX62 | 0.1868 | 10.9484 | -0.0207 | 180 | B-3-1c |  |  | Transformer
NFLE41 | NFLE11 | 0.139 | 8.0987 | -0.1363 | 268 | B-3-1c |  |  | Transformer
NFLE41 | NFLE11 | 0.139 | 8.0987 | -0.1363 | 261 | B-3-1c |  |  | Transformer
NFLE41 | NFLE12 | 0.139 | 8.0987 | -0.1363 | 269 | B-3-1c |  |  | Transformer
NFLE41 | NFLE12 | 0.139 | 8.0987 | -0.1363 | 260 | B-3-1c |  |  | Transformer
NHYD2A | NHYD61 | 0.3062 | 11.0235 | -0.4552 | 187 | B-3-1c |  |  | Transformer
NHYD2B | NHYD61 | 0.3062 | 11.0235 | -0.4552 | 187 | B-3-1c |  |  | Transformer
NHYD2B | NHYD61 | 0.2364 | 13.3312 | -0.1908 | 180 | B-3-1c |  |  | Transformer
NINF41 | NINF11 | 0.1303 | 7.8698 | -0.4285 | 278 | B-3-1c |  |  | Transformer
NINF41 | NINF11 | 0.1658 | 8.4025 | -1.5604 | 273 | B-3-1c |  |  | Transformer
NINF41 | NINF12 | 0.1658 | 8.4025 | -1.5604 | 273 | B-3-1c |  |  | Transformer
NINF41 | NINF12 | 0.1054 | 7.888 | -0.0784 | 259 | B-3-1c |  |  | Transformer
NORL2A | NORL31 | 0.545 | 19.7925 | -0.1407 | 114 | B-3-1c |  |  | Transformer
NORL2B | NORL31 | 0.545 | 19.7925 | -0.1407 | 114 | B-3-1c |  |  | Transformer
NORM41 | NORM11 | 0.1264 | 8.4534 | -0.357 | 277 | B-3-1c |  |  | Transformer
NORM41 | NORM11 | 0.1307 | 7.9515 | -0.1098 | 240 | B-3-1c |  |  | Transformer
NORM41 | NORM12 | 0.1118 | 8.3874 | -0.0906 | 278 | B-3-1c |  |  | Transformer
NORM41 | NORM1A | 0.1509 | 7.9378 | -0.9251 | 253 | B-3-1c |  |  | Transformer
NORM41 | NORM1B | 0.1509 | 7.9378 | -0.9251 | 267 | B-3-1c |  |  | Transformer
NORT21 | NORT11 | 0.1594 | 8.6081 | -0.2215 | 262 | B-3-1c |  |  | Transformer
NORT21 | NORT11 | 0.1594 | 8.6081 | -0.2215 | 262 | B-3-1c |  |  | Transformer
NORT21 | NORT11 | 0.1748 | 8.3565 | -0.2684 | 240 | B-3-1c |  |  | Transformer
NORT21 | NORT11 | 0.1748 | 8.3565 | -0.2684 | 280 | B-3-1c |  |  | Transformer
NORT41 | NORT21 | 0.0186 | 1.5729 | -7.729 | 1136 | B-3-1c |  |  | Transformer
NORT41 | NORT21 | 0.0117 | 1.591 | -4.4806 | 1133 | B-3-1c |  |  | Transformer
NURS41 | NURS11 | 0.1471 | 8.4008 | -0.1719 | 252 | B-3-1c |  |  | Transformer
NURS41 | NURS11 | 0.1471 | 8.4008 | -0.1719 | 253 | B-3-1c |  |  | Transformer
NURS4A | NURS11 | 0.103 | 7.9231 | -0.0638 | 262 | B-3-1c |  |  | Transformer
OCKH21 | OCKH11 | 0.1221 | 8.0467 | -0.0391 | 279 | B-3-1c |  |  | Transformer
OCKH21 | OCKH11 | 0.1221 | 8.0467 | -0.0391 | 279 | B-3-1c |  |  | Transformer
OCKH21 | OCKH11 | 0.179 | 8.3648 | -4.7616 | 202 | B-3-1c |  |  | Transformer
OFFE21 | OFFE31 | 0.5135 | 18.2228 | -0.5477 | 115 | B-3-1c |  |  | Transformer
OFFE21 | OFFE32 | 0.5135 | 18.2228 | -0.5477 | 113 | B-3-1c |  |  | Transformer
OLDB21 | OLDB11 | 0.1594 | 8.6081 | -0.2215 | 261 | B-3-1c |  |  | Transformer
OLDB21 | OLDB11 | 0.1594 | 8.6081 | -0.2215 | 261 | B-3-1c |  |  | Transformer
OLDB2A | OLDB11 | 0.1004 | 8.3615 | -0.2374 | 261 | B-3-1c |  |  | Transformer
OLDB4A | OLDB21 | 0.0146 | 1.609 | -1.8746 | 1172 | B-3-1c |  |  | Transformer
OSBA41 | OSBA11 | 0.103 | 7.9231 | -0.0638 | 269 | B-3-1c |  |  | Transformer
OSBA41 | OSBA11 | 0.103 | 7.9231 | -0.0638 | 269 | B-3-1c |  |  | Transformer
OSBA42 | OSBA11 | 0.1372 | 8.0197 | -0.1238 | 278 | B-3-1c |  |  | Transformer
PADI41 | PADI11 | 0.1373 | 8.1976 | -0.1719 | 274 | B-3-1c |  |  | Transformer
PADI41 | PADI11 | 0.1051 | 7.8585 | -0.0834 | 262 | B-3-1c |  |  | Transformer
PELH41 | PELH11 | 0.1175 | 8.6648 | -0.4173 | 264 | B-3-1c |  |  | Transformer
PELH41 | PELH12 | 0.1175 | 8.6648 | -0.4173 | 264 | B-3-1c |  |  | Transformer
PEMB41 | PEMB11 | 0.1658 | 8.4025 | -1.5604 | 276 | B-3-1c |  |  | Transformer
PEMB41 | PEMB11 | 0.1471 | 8.4008 | -0.1719 | 275 | B-3-1c |  |  | Transformer
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266 | B-3-1c |  |  | Transformer
PENN21 | PENN11 | 0.1441 | 8.6238 | -0.2707 | 266 | B-3-1c |  |  | Transformer
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266 | B-3-1c |  |  | Transformer
PENN21 | PENN11 | 0.1623 | 8.097 | -1.5978 | 266 | B-3-1c |  |  | Transformer
PENN4A | PENN21 | 0.0176 | 1.5828 | -0.1018 | 1138 | B-3-1c |  |  | Transformer
PENN4B | PENN21 | 0.0132 | 1.6756 | -0.4337 | 1063 | B-3-1c |  |  | Transformer
PENT41 | PENT11 | 0.1471 | 8.4008 | -0.1719 | 257 | B-3-1c |  |  | Transformer
PENT41 | PENT11 | 0.1621 | 8.0984 | -0.0747 | 255 | B-3-1c |  |  | Transformer
PEWO2A | PENW11 | 0.1594 | 8.6081 | -0.2215 | 261 | B-3-1c |  |  | Transformer
PEWO2B | PENW11 | 0.1594 | 8.6081 | -0.2215 | 261 | B-3-1c |  |  | Transformer
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265 | B-3-1c |  |  | Transformer
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265 | B-3-1c |  |  | Transformer
PEWO41 | PENE11 | 0.1372 | 8.0197 | -0.1238 | 265 | B-3-1c |  |  | Transformer
PEWO41 | PENW11 | 0.1311 | 7.9055 | -0.1016 | 278 | B-3-1c |  |  | Transformer
PEWO41 | PEWO2A | 0.0189 | 1.6132 | -0.7226 | 1129 | B-3-1c |  |  | Transformer
PEWO41 | PEWO2A | 0.0178 | 1.5995 | -1.2431 | 845 | B-3-1c |  |  | Transformer
PEWO41 | PEWO2B | 0.0175 | 1.5879 | -4.0069 | 1139 | B-3-1c |  |  | Transformer
PEWO41 | PEWO2B | 0.021 | 1.669 | -12.6082 | 876 | B-3-1c |  |  | Transformer
PITS21 | PITS31 | 0.4975 | 20.4439 | -0.2606 | 110 | B-3-1c |  |  | Transformer
PITS21 | PITS31 | 0.4975 | 20.4439 | -0.2606 | 110 | B-3-1c |  |  | Transformer
PITS21 | PITS32 | 0.2998 | 20.1311 | -0.3705 | 120 | B-3-1c |  |  | Transformer
PITS21 | PITS32 | 0.2998 | 20.1311 | -0.3705 | 120 | B-3-1c |  |  | Transformer
POPP21 | POPP31 | 0.4905 | 24.145 | -0.1894 | 110 | B-3-1c |  |  | Transformer
POPP21 | POPP31 | 0.2731 | 30.5821 | -0.0312 | 110 | B-3-1c |  |  | Transformer
PYLE21 | PYLE11 | 0.1366 | 8.0648 | -0.0471 | 279 | B-3-1c |  |  | Transformer
PYLE21 | PYLE11 | 0.2009 | 8.1596 | -0.5003 | 211 | B-3-1c |  |  | Transformer
RAIN21 | RAIN11 | 0.1927 | 8.5256 | -0.5357 | 211 | B-3-1c |  |  | Transformer
RAIN21 | RAIN11 | 0.1927 | 8.5256 | -0.5357 | 211 | B-3-1c |  |  | Transformer
RAIN21 | RAIN12 | 0.1927 | 8.5256 | -0.5357 | 211 | B-3-1c |  |  | Transformer
RAIN21 | RAIN12 | 0.1927 | 8.5256 | -0.5357 | 211 | B-3-1c |  |  | Transformer
RASS41 | RASS11 | 0.0996 | 8.0568 | -1.1981 | 270 | B-3-1c |  |  | Transformer
RASS41 | RASS11 | 0.0996 | 8.0568 | -1.1981 | 273 | B-3-1c |  |  | Transformer
RATS41 | RATS11 | 0.1042 | 7.841 | -0.0895 | 240 | B-3-1c |  |  | Transformer
RATS41 | RATS11 | 0.1047 | 8.2285 | -0.0886 | 262 | B-3-1c |  |  | Transformer
RATS41 | RATS12 | 0.1373 | 8.1976 | -0.1719 | 278 | B-3-1c |  |  | Transformer
RATS41 | RATS12 | 0.1278 | 8.0061 | -0.2276 | 277 | B-3-1c |  |  | Transformer
RATS41 | RATS2A | 0.0146 | 1.609 | -1.8746 | 1125 | B-3-1c |  |  | Transformer
RAYL41 | RAYM11 | 0.1309 | 7.8656 | -0.4549 | 262 | B-3-1c |  |  | Transformer
RAYL41 | RAYM11 | 0.1045 | 7.8618 | -0.0882 | 240 | B-3-1c |  |  | Transformer
RAYL41 | RAYM11 | 0.1035 | 7.8568 | -0.0758 | 240 | B-3-1c |  |  | Transformer
RAYL41 | RAYM11 | 0.1303 | 7.8698 | -0.4285 | 262 | B-3-1c |  |  | Transformer
REBR21 | REBR32 | 0.665 | 28.1922 | -0.151 | 111 | B-3-1c |  |  | Transformer
REBR22 | REBR31 | 0.3375 | 30.6481 | -0.1769 | 132 | B-3-1c |  |  | Transformer
REBR22 | REBR31 | 0.665 | 28.1922 | -0.151 | 112 | B-3-1c |  |  | Transformer
RICH41 | RICH11 | 0.1186 | 7.8741 | -0.3958 | 240 | B-3-1c |  |  | Transformer
RICH41 | RICH11 | 0.1181 | 7.9033 | -0.3958 | 240 | B-3-1c |  |  | Transformer
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 278 | B-3-1c |  |  | Transformer
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 278 | B-3-1c |  |  | Transformer
ROCH21 | ROCH11 | 0.1183 | 8.3927 | -0.0783 | 278 | B-3-1c |  |  | Transformer
ROCH21 | ROCH12 | 0.1183 | 8.3927 | -0.2368 | 140 | B-3-1c |  |  | Transformer
ROCH4A | ROCH21 | 0.0098 | 1.5863 | -0.0631 | 1100 | B-3-1c |  |  | Transformer
ROCK41 | ROCK1A | 0.054 | 4.8906 | -0.1253 | 460 | B-3-1c |  |  | Transformer
RUGE41 | RUGE11 | 0.1139 | 8.1036 | -2.059 | 267 | B-3-1c |  |  | Transformer
RUGE41 | RUGE11 | 0.1139 | 8.1036 | -2.059 | 267 | B-3-1c |  |  | Transformer
RYEH41 | RYEH13 | 0.1372 | 8.0197 | -0.1238 | 253 | B-3-1c |  |  | Transformer
RYEH42 | RYEH12 | 0.1055 | 8.2414 | -0.0848 | 267 | B-3-1c |  |  | Transformer
RYEH43 | RYEH11 | 0.1326 | 8.774 | -0.7141 | 260 | B-3-1c |  |  | Transformer
SAEN21 | SAEN11 | 0.1531 | 8.6564 | -0.0254 | 211 | B-3-1c |  |  | Transformer
SAEN21 | SAEN11 | 0.1531 | 8.6564 | -0.0254 | 211 | B-3-1c |  |  | Transformer
SAFO41 | SAFO11 | 0.1054 | 8.1656 | -0.1095 | 240 | B-3-1c |  |  | Transformer
SAFO41 | SAFO11 | 0.1054 | 8.1606 | -0.1098 | 240 | B-3-1c |  |  | Transformer
SALH21 | SALH11 | 0.1392 | 8.4361 | -0.781 | 240 | B-3-1c |  |  | Transformer
SALH21 | SALH11 | 0.1392 | 8.4361 | -0.781 | 240 | B-3-1c |  |  | Transformer
SEAB41 | SEAB11 | 0.1303 | 7.8698 | -0.4285 | 256 | B-3-1c |  |  | Transformer
SEAB41 | SEAB11 | 0.1303 | 7.8698 | -0.4285 | 256 | B-3-1c |  |  | Transformer
SELL4A | SELL11 | 0.0996 | 8.0568 | -1.1981 | 275 | B-3-1c |  |  | Transformer
SELL4A | SELL11 | 0.0996 | 8.0568 | -1.1981 | 273 | B-3-1c |  |  | Transformer
SELL4A | SELL12 | 0.103 | 7.9231 | -0.0638 | 270 | B-3-1c |  |  | Transformer
SELL4A | SELL13 | 0.1621 | 8.0984 | -0.0747 | 256 | B-3-1c |  |  | Transformer
SHEC21 | SHEC31 | 0.593 | 20.7915 | -0.122 | 115 | B-3-1c |  |  | Transformer
SHEC21 | SHEC31 | 0.593 | 20.7915 | -0.122 | 114 | B-3-1c |  |  | Transformer
SHRE4B | SHRE11 | 0.1057 | 7.9352 | -0.339 | 240 | B-3-1c |  |  | Transformer
SIZE41 | SIZE11 | 0.103 | 7.9231 | -0.0638 | 267 | B-3-1c |  |  | Transformer
SIZE41 | SIZE12 | 0.103 | 7.9231 | -0.0638 | 268 | B-3-1c |  |  | Transformer
SIZE41 | SIZE1A | 0.103 | 7.9231 | -0.0638 | 268 | B-3-1c |  |  | Transformer
SIZE41 | SIZE1B | 0.103 | 7.9231 | -0.0638 | 269 | B-3-1c |  |  | Transformer
SJOW41 | LODR61 | 0.1529 | 12.1324 | -0.0623 | 273 | B-3-1c |  |  | Transformer
SJOW41 | LODR61 | 0.1403 | 12.3367 | -0.6356 | 240 | B-3-1c |  |  | Transformer
SJOW41 | LODR62 | 0.1455 | 13.3242 | -0.0759 | 240 | B-3-1c |  |  | Transformer
SJOW41 | LODR62 | 0.1307 | 7.9515 | -0.1098 | 268 | B-3-1c |  |  | Transformer
SJOW41 | SJOW11 | 0.1229 | 8.3873 | -0.1147 | 271 | B-3-1c |  |  | Transformer
SJOW41 | SJOW11 | 0.1229 | 8.3873 | -0.1147 | 272 | B-3-1c |  |  | Transformer
SJOW41 | SJOW12 | 0.1229 | 8.3873 | -0.1147 | 271 | B-3-1c |  |  | Transformer
SJOW41 | SJOW12 | 0.1229 | 8.3873 | -0.1147 | 270 | B-3-1c |  |  | Transformer
SJOW41 | SJOW13 | 0.1055 | 8.1881 | -0.0865 | 240 | B-3-1c |  |  | Transformer
SKLG21 | SKLG11 | 0.1147 | 8.673 | -0.0358 | 264 | B-3-1c |  |  | Transformer
SKLG21 | SKLG11 | 0.1264 | 8.6657 | -0.0342 | 278 | B-3-1c |  |  | Transformer
SKLG21 | SKLG11 | 0.1264 | 8.6657 | -0.0342 | 270 | B-3-1c |  |  | Transformer
SKLG21 | SKLG11 | 0.1147 | 8.673 | -0.0358 | 240 | B-3-1c |  |  | Transformer
SMAN21 | SMAN11 | 0.1052 | 8.2077 | -0.6621 | 279 | B-3-1c |  |  | Transformer
SMAN21 | SMAN11 | 0.1441 | 8.6238 | -0.2707 | 266 | B-3-1c |  |  | Transformer
SMAN21 | SMAN12 | 0.1441 | 8.6238 | -0.2707 | 266 | B-3-1c |  |  | Transformer
SMAN21 | SMAN12 | 0.1221 | 8.0467 | -0.0391 | 279 | B-3-1c |  |  | Transformer
SPEN41 | SPEN11 | 0.1293 | 7.8614 | -0.537 | 278 | B-3-1c |  |  | Transformer
SPEN41 | SPEN11 | 0.1305 | 7.8823 | -0.5369 | 278 | B-3-1c |  |  | Transformer
SPEN42 | SPEN11 | 0.1315 | 7.8822 | -0.5369 | 278 | B-3-1c |  |  | Transformer
SSHI22 | SSHI31 | 0.4975 | 20.4439 | -0.2606 | 110 | B-3-1c |  |  | Transformer
SSHI22 | SSHI31 | 0.4975 | 20.4439 | -0.2606 | 110 | B-3-1c |  |  | Transformer
STAH4A | STAH11 | 0.122 | 8.1963 | -0.2446 | 274 | B-3-1c |  |  | Transformer
STAH4B | STAH11 | 0.1046 | 7.8493 | -0.0881 | 271 | B-3-1c |  |  | Transformer
STAL21 | STAL11 | 0.2188 | 8.097 | -1.9861 | 280 | B-3-1c |  |  | Transformer
STAL21 | STAL11 | 0.1221 | 8.0467 | -0.0391 | 279 | B-3-1c |  |  | Transformer
STAL21 | STAL11 | 0.1681 | 8.3396 | -1.4878 | 198 | B-3-1c |  |  | Transformer
STAL21 | STAL11 | 0.1954 | 8.0796 | -0.2295 | 189 | B-3-1c |  |  | Transformer
STAL4A | STAL21 | 0.0146 | 1.609 | -1.8746 | 1117 | B-3-1c |  |  | Transformer
STAY41 | STYC11 | 0.103 | 7.9231 | -0.0638 | 266 | B-3-1c |  |  | Transformer
STAY41 | STYC12 | 0.1046 | 7.8493 | -0.0881 | 271 | B-3-1c |  |  | Transformer
STEW21 | STEN11 | 0.3328 | 11.6619 | -0.9523 | 138 | B-3-1c |  |  | Transformer
STEW21 | STEN11 | 0.3328 | 11.6619 | -0.9523 | 137 | B-3-1c |  |  | Transformer
STEW21 | STEN11 | 0.0933 | 8.4245 | -0.0567 | 179 | B-3-1c |  |  | Transformer
STEW21 | STES11 | 0.1366 | 8.0648 | -0.0471 | 274 | B-3-1c |  |  | Transformer
STEW21 | STES11 | 0.3328 | 11.6619 | -0.9523 | 137 | B-3-1c |  |  | Transformer
STEW21 | STES11 | 0.3328 | 11.6619 | -0.9523 | 137 | B-3-1c |  |  | Transformer
STEW41 | STEW21 | 0.0211 | 1.6463 | -14.2471 | 1172 | B-3-1c |  |  | Transformer
STEW41 | STEW21 | 0.0107 | 1.5596 | -0.0734 | 1165 | B-3-1c |  |  | Transformer
STOB41 | STOB11 | 0.1307 | 7.9515 | -0.1098 | 274 | B-3-1c |  |  | Transformer
STOB41 | STOB11 | 0.1307 | 7.9515 | -0.1098 | 271 | B-3-1c |  |  | Transformer
SUND41 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 252 | B-3-1c |  |  | Transformer
SUND41 | SUND11 | 0.13 | 7.8739 | -0.5372 | 278 | B-3-1c |  |  | Transformer
SUND41 | SUND31 | 0.2106 | 15.2133 | -0.0768 | 150 | B-3-1c |  |  | Transformer
SUND42 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 254 | B-3-1c |  |  | Transformer
SUND42 | SUND11 | 0.1675 | 8.2453 | -0.6567 | 250 | B-3-1c |  |  | Transformer
SWAN22 | SWAN11 | 0.1646 | 8.0383 | -0.1808 | 211 | B-3-1c |  |  | Transformer
SWAN22 | SWAN11 | 0.1923 | 8.2361 | -0.4425 | 211 | B-3-1c |  |  | Transformer
SWAN41 | SWAN11 | 0.1303 | 7.8698 | -0.4285 | 256 | B-3-1c |  |  | Transformer
SWAN41 | SWAN12 | 0.1303 | 7.8698 | -0.4285 | 256 | B-3-1c |  |  | Transformer
SWAN41 | SWAN21 | 0.0182 | 1.5763 | -0.0904 | 1210 | B-3-1c |  |  | Transformer
SWAN4A | SWAN22 | 0.0178 | 1.5995 | -1.2431 | 851 | B-3-1c |  |  | Transformer
SWAN4B | SWAN12 | 0.1307 | 7.9515 | -0.1098 | 263 | B-3-1c |  |  | Transformer
TAUN41 | TAUN11 | 0.1049 | 8.1792 | -0.1104 | 274 | B-3-1c |  |  | Transformer
TAUN42 | TAUN11 | 0.1459 | 8.045 | -0.2605 | 279 | B-3-1c |  |  | Transformer
TEMP21 | TEMP31 | 0.7076 | 26.5771 | -0.0784 | 76 | B-3-1c |  |  | Transformer
TEMP22 | TEMP31 | 0.7076 | 26.5771 | -0.0784 | 76 | B-3-1c |  |  | Transformer
THOM21 | THOM61 | 0.3985 | 16.203 | -0.4431 | 122 | B-3-1c |  |  | Transformer
THOM41 | THOM21 | 0.0189 | 1.6132 | -0.7226 | 879 | B-3-1c |  |  | Transformer
THOM41 | THOM21 | 0.0185 | 1.614 | -0.5638 | 879 | B-3-1c |  |  | Transformer
THOM42 | THOM2A | 0.0152 | 1.6463 | -0.1118 | 1100 | B-3-1c |  |  | Transformer
THOM42 | THOM61 | 0.1844 | 13.1765 | -0.0474 | 180 | B-3-1c |  |  | Transformer
THUR21 | THUR61 | 0.2288 | 10.3241 | -0.0437 | 209 | B-3-1c |  |  | Transformer
THUR21 | THUR61 | 0.2288 | 10.3241 | -0.0437 | 209 | B-3-1c |  |  | Transformer
THUR21 | THUR61 | 0.1699 | 10.8431 | -0.0403 | 200 | B-3-1c |  |  | Transformer
TILB21 | TILB11 | 0.1004 | 8.1994 | -0.2371 | 240 | B-3-1c |  |  | Transformer
TILB21 | TILB12 | 0.1 | 8.0952 | -0.2374 | 240 | B-3-1c |  |  | Transformer
TILB41 | TILB13 | 0.1307 | 7.9515 | -0.1098 | 240 | B-3-1c |  |  | Transformer
TILB41 | TILB14 | 0.1303 | 7.8698 | -0.4285 | 278 | B-3-1c |  |  | Transformer
TILB4A | TILB21 | 0.0376 | 2.1949 | -10.6848 | 1153 | B-3-1c |  |  | Transformer
TILB4B | TILB21 | 0.0117 | 1.591 | -4.4806 | 1102 | B-3-1c |  |  | Transformer
TINP21 | TINP31 | 0.4758 | 20.0944 | -0.4489 | 111 | B-3-1c |  |  | Transformer
TINP21 | TINP32 | 0.5083 | 24.0899 | -0.1921 | 135 | B-3-1c |  |  | Transformer
TINP22 | TINP31 | 0.4758 | 20.0944 | -0.4489 | 111 | B-3-1c |  |  | Transformer
TINP22 | TINP32 | 0.5083 | 24.0899 | -0.1921 | 120 | B-3-1c |  |  | Transformer
TODP21 | TODP61 | 0.3931 | 16.4953 | -2.1281 | 139 | B-3-1c |  |  | Transformer
TODP21 | TODP61 | 0.459 | 16.6187 | -0.1963 | 101 | B-3-1c |  |  | Transformer
TOTT21 | TOTT11 | 0.1266 | 8.6449 | -1.9406 | 265 | B-3-1c |  |  | Transformer
TOTT22 | TOTT11 | 0.1266 | 8.6449 | -1.9406 | 265 | B-3-1c |  |  | Transformer
TOTT23 | TOTT12 | 0.1688 | 8.3316 | -1.1711 | 265 | B-3-1c |  |  | Transformer
TOTT24 | TOTT12 | 0.179 | 8.3648 | -4.7616 | 198 | B-3-1c |  |  | Transformer
TRAW21 | TRAW11 | 0.1004 | 8.1994 | -0.2371 | 240 | B-3-1c |  |  | Transformer
TRAW21 | TRAW11 | 0.0937 | 8.437 | -0.1095 | 150 | B-3-1c |  |  | Transformer
TRAW41 | TRAW21 | 0.0132 | 1.6756 | -0.4337 | 966 | B-3-1c |  |  | Transformer
TRAW41 | TRAW21 | 0.021 | 1.669 | -12.6082 | 888 | B-3-1c |  |  | Transformer
TREM21 | TREM31 | 0.4636 | 17.894 | -0.1238 | 116 | B-3-1c |  |  | Transformer
TREM21 | TREM31 | 0.593 | 20.7915 | -0.122 | 115 | B-3-1c |  |  | Transformer
TYNE21 | TYNE11 | 0.1221 | 8.0467 | -0.0391 | 279 | B-3-1c |  |  | Transformer
TYNE21 | TYNE11 | 0.1411 | 8.6331 | -0.2264 | 267 | B-3-1c |  |  | Transformer
TYNE21 | TYNE51 | 1.2306 | 53.1493 | -0.0143 | 44 | B-3-1c |  |  | Transformer
TYNE2A | TYNE51 | 1.2306 | 53.1493 | -0.0143 | 44 | B-3-1c |  |  | Transformer
UPPB21 | UPPB31 | 0.4636 | 17.894 | -0.1238 | 113 | B-3-1c |  |  | Transformer
UPPB21 | UPPB31 | 0.5107 | 17.9527 | -0.2251 | 113 | B-3-1c |  |  | Transformer
UPPB22 | UPPB11 | 0.0979 | 8.4411 | -0.0271 | 262 | B-3-1c |  |  | Transformer
UPPB22 | UPPB11 | 0.097 | 8.457 | -0.0263 | 222 | B-3-1c |  |  | Transformer
USKM21 | ALST31 | 0.5135 | 18.2228 | -0.5477 | 116 | B-3-1c |  |  | Transformer
USKM21 | ALST32 | 0.5107 | 17.9527 | -0.2251 | 116 | B-3-1c |  |  | Transformer
USKM21 | USKM11 | 0.1221 | 8.0467 | -0.0391 | 263 | B-3-1c |  |  | Transformer
USKM21 | USKM11 | 0.1221 | 8.0467 | -0.0391 | 279 | B-3-1c |  |  | Transformer
USKM21 | USKM12 | 0.1221 | 8.0467 | -0.0391 | 263 | B-3-1c |  |  | Transformer
WALH41 | PORH11 | 0.1471 | 8.4008 | -0.1719 | 253 | B-3-1c |  |  | Transformer
WALH41 | PORH11 | 0.103 | 7.9231 | -0.0638 | 275 | B-3-1c |  |  | Transformer
WALH41 | PORH11 | 0.1372 | 8.0197 | -0.1238 | 278 | B-3-1c |  |  | Transformer
WALH41 | PORH11 | 0.1036 | 7.8597 | -0.0784 | 274 | B-3-1c |  |  | Transformer
WALP41 | WALP11 | 0.1042 | 7.891 | -0.4318 | 274 | B-3-1c |  |  | Transformer
WALP41 | WALP11 | 0.1304 | 7.9364 | -0.479 | 278 | B-3-1c |  |  | Transformer
WALP41 | WALP11 | 0.1509 | 8.2849 | -0.3279 | 275 | B-3-1c |  |  | Transformer
WALP41 | WALP11 | 0.1621 | 8.0984 | -0.0747 | 275 | B-3-1c |  |  | Transformer
WALP41 | WALP11 | 0.1759 | 7.9134 | -0.4285 | 274 | B-3-1c |  |  | Transformer
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 278 | B-3-1c |  |  | Transformer
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 278 | B-3-1c |  |  | Transformer
WARL21 | WARL11 | 0.1266 | 8.6449 | -1.9406 | 264 | B-3-1c |  |  | Transformer
WASF2A | WASF1A | 0.197 | 7.9698 | -0.2553 | 207 | B-3-1c |  |  | Transformer
WASF2B | WASF1B | 0.197 | 7.9698 | -0.2553 | 207 | B-3-1c |  |  | Transformer
WATS21 | WATS11 | 0.1382 | 8.1742 | -0.1786 | 279 | B-3-1c |  |  | Transformer
WATS21 | WATS12 | 0.3567 | 11.136 | -0.7303 | 127 | B-3-1c |  |  | Transformer
WATS21 | WATS12 | 0.3567 | 11.136 | -0.7303 | 126 | B-3-1c |  |  | Transformer
WATS22 | WATS11 | 0.1392 | 8.4361 | -0.781 | 266 | B-3-1c |  |  | Transformer
WATS22 | WATS11 | 0.1923 | 8.081 | -1.4418 | 189 | B-3-1c |  |  | Transformer
WBOL21 | WBOL61 | 0.1809 | 10.9763 | -0.023 | 180 | B-3-1c |  |  | Transformer
WBOL21 | WBOL61 | 0.4736 | 16.5344 | -0.54 | 134 | B-3-1c |  |  | Transformer
WBOL21 | WBOL61 | 0.3726 | 16.7215 | -0.6945 | 127 | B-3-1c |  |  | Transformer
WBOL21 | WBOL61 | 0.3726 | 16.7215 | -0.6945 | 127 | B-3-1c |  |  | Transformer
WBUR41 | WBUR11 | 0.1056 | 8.2208 | -0.6711 | 274 | B-3-1c |  |  | Transformer
WBUR42 | WBUR11 | 0.1175 | 8.6648 | -0.4173 | 263 | B-3-1c |  |  | Transformer
WBUR42 | WBUR12 | 0.1175 | 8.6648 | -0.4173 | 265 | B-3-1c |  |  | Transformer
WHAM41 | WHAM11 | 0.1057 | 7.9352 | -0.339 | 264 | B-3-1c |  |  | Transformer
WHAM41 | WHAM11 | 0.103 | 7.9231 | -0.0638 | 263 | B-3-1c |  |  | Transformer
WHAM41 | WHAM12 | 0.103 | 7.9231 | -0.0638 | 271 | B-3-1c |  |  | Transformer
WHAM41 | WHAM12 | 0.1057 | 7.9352 | -0.339 | 263 | B-3-1c |  |  | Transformer
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 279 | B-3-1c |  |  | Transformer
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 279 | B-3-1c |  |  | Transformer
WHGA21 | WHGA11 | 0.1623 | 8.097 | -1.5978 | 279 | B-3-1c |  |  | Transformer
WHSO21 | WHSO31 | 0.4435 | 14.3532 | -0.577 | 100 | B-3-1c |  |  | Transformer
WHSO21 | WHSO31 | 0.4435 | 14.3532 | -0.577 | 100 | B-3-1c |  |  | Transformer
WHSO21 | WHSO32 | 0.4435 | 14.3131 | -0.577 | 100 | B-3-1c |  |  | Transformer
WHSO22 | WHSO32 | 0.4435 | 14.3532 | -0.577 | 100 | B-3-1c |  |  | Transformer
WHSO41 | WHSO22 | 0.0185 | 1.614 | -0.5638 | 886 | B-3-1c |  |  | Transformer
WIBA21 | WIBA31 | 0.6006 | 25.9931 | -0.0335 | 114 | B-3-1c |  |  | Transformer
WIBA21 | WIBA31 | 0.6006 | 25.9931 | -0.0335 | 114 | B-3-1c |  |  | Transformer
WIEN2A | WIEN11 | 0.1 | 8.1202 | -0.2373 | 240 | B-3-1c |  |  | Transformer
WIEN2B | WIEN11 | 0.1366 | 8.0648 | -0.0471 | 279 | B-3-1c |  |  | Transformer
WILE41 | WILL11 | 0.1046 | 7.8493 | -0.0881 | 271 | B-3-1c |  |  | Transformer
WILE41 | WILL11 | 0.1303 | 7.8698 | -0.4285 | 269 | B-3-1c |  |  | Transformer
WILE41 | WILL11 | 0.1056 | 8.2208 | -0.6711 | 686 | B-3-1c |  |  | Transformer
WILE41 | WILL12 | 0.1035 | 8.3458 | -0.0962 | 278 | B-3-1c |  |  | Transformer
WILT2A | GRST61 | 0.3151 | 12.4456 | -0.1391 | 207 | B-3-1c |  |  | Transformer
WILT2B | GRST61 | 0.3151 | 12.4456 | -0.1391 | 207 | B-3-1c |  |  | Transformer
WILT2C | GRST61 | 0.2275 | 10.8456 | -0.0697 | 198 | B-3-1c |  |  | Transformer
WILT2D | GRST61 | 0.2972 | 12.4333 | -0.1533 | 206 | B-3-1c |  |  | Transformer
WIMB41 | WIMB11 | 0.1354 | 7.753 | -0.4285 | 240 | B-3-1c |  |  | Transformer
WIMB41 | WIMB11 | 0.1303 | 7.8698 | -0.4285 | 240 | B-3-1c |  |  | Transformer
WIMB41 | WIMB11 | 0.1366 | 7.753 | -0.4285 | 240 | B-3-1c |  |  | Transformer
WIMB41 | WIMB11 | 0.1303 | 7.8698 | -0.4285 | 240 | B-3-1c |  |  | Transformer
WIMB41 | WIMB11 | 0.1303 | 7.8698 | -0.4285 | 240 | B-3-1c |  |  | Transformer
WIMB41 | WIMB11 | 0.1303 | 7.8698 | -0.4285 | 240 | B-3-1c |  |  | Transformer
WIMB41 | WIMB21 | 0.014 | 2.6567 | -0.1528 | 950 | B-3-1c |  |  | Transformer
WIMB41 | WIMB21 | 0.014 | 2.6567 | -0.1528 | 950 | B-3-1c |  |  | Transformer
WISD21 | WISD11 | 0.1845 | 7.8956 | -0.1938 | 240 | B-3-1c |  |  | Transformer
WISD21 | WISD11 | 0.167 | 7.9774 | -0.2092 | 257 | B-3-1c |  |  | Transformer
WISD21 | WISD11 | 0.167 | 7.9774 | -0.2092 | 240 | B-3-1c |  |  | Transformer
WISD21 | WISD11 | 0.0723 | 8.433 | -0.2375 | 240 | B-3-1c |  |  | Transformer
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 200 | B-3-1c |  |  | Transformer
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 201 | B-3-1c |  |  | Transformer
WISD21 | WISD61 | 0.3204 | 14.3298 | -0.2424 | 200 | B-3-1c |  |  | Transformer
WISD41 | WISD21 | 0.0152 | 1.6463 | -0.1118 | 949 | B-3-1c |  |  | Transformer
WISD42 | WISD21 | 0.0152 | 1.6463 | -0.1118 | 949 | B-3-1c |  |  | Transformer
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 130 | B-3-1c |  |  | Transformer
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 130 | B-3-1c |  |  | Transformer
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 129 | B-3-1c |  |  | Transformer
WMEL21 | WMEL11 | 0.2264 | 12.2479 | -0.6062 | 129 | B-3-1c |  |  | Transformer
WMEL21 | WMEL12 | 0.1492 | 8.2209 | -0.7333 | 199 | B-3-1c |  |  | Transformer
WMEL21 | WMEL12 | 0.1492 | 8.2209 | -0.7333 | 199 | B-3-1c |  |  | Transformer
WMEL21 | WMEL12 | 0.1923 | 8.2361 | -0.4425 | 197 | B-3-1c |  |  | Transformer
WTHU4A | WTHU31 | 0.5201 | 31.2457 | -0.1063 | 100 | B-3-1c |  |  | Transformer
WTHU4B | WTHU31 | 0.5201 | 31.2457 | -0.1063 | 100 | B-3-1c |  |  | Transformer
WWEY21 | WWEY11 | 0.2188 | 8.097 | -1.9861 | 280 | B-3-1c |  |  | Transformer
WWEY21 | WWEY12 | 0.1382 | 8.4614 | -0.1786 | 250 | B-3-1c |  |  | Transformer
WWEY22 | WWEY11 | 0.1007 | 8.1333 | -0.2371 | 240 | B-3-1c |  |  | Transformer
WWEY22 | WWEY12 | 0.1382 | 8.4489 | -0.1786 | 240 | B-3-1c |  |  | Transformer
WWEY4A | WWEY21 | 0.017 | 1.6132 | -5.1203 | 750 | B-3-1c |  |  | Transformer
WWEY4A | WWEY22 | 0.0185 | 1.614 | -0.5638 | 886 | B-3-1c |  |  | Transformer
WWEY4B | WWEY21 | 0.0178 | 1.5995 | -1.2431 | 845 | B-3-1c |  |  | Transformer
WWEY4B | WWEY2A | 0.0178 | 1.5995 | -1.2431 | 845 | B-3-1c |  |  | Transformer
WYLF41 | WYLF11 | 0.1509 | 8.2849 | -0.3279 | 276 | B-3-1c |  |  | Transformer
WYLF41 | WYLF11 | 0.1229 | 8.3873 | -0.1147 | 269 | B-3-1c |  |  | Transformer
WYMO41 | WYMO11 | 0.1509 | 8.2849 | -0.3279 | 273 | B-3-1c |  |  | Transformer
WYMO41 | WYMO11 | 0.1303 | 7.8698 | -0.4285 | 273 | B-3-1c |  |  | Transformer
CONN1J | CONN2K | 0.143 | 5.3036 | -0.0006 | 360 | B-3-2a | 2025 | Addition | Transformer
CONN1K | CONN2J | 0.143 | 5.3036 | -0.0006 | 360 | B-3-2a | 2025 | Addition | Transformer
ERRO1J | ERRO3- | 0.5 | 25 | 0 | 90 | B-3-2a | 2025 | Addition | Transformer
ERRO1K | ERRO3- | 0.5 | 25 | 0 | 90 | B-3-2a | 2025 | Addition | Transformer
GREM1J | GREM3- | 0.5828 | 24.9932 | 0 | 90 | B-3-2a | 2025 | Addition | Transformer
GREM1K | GREM3- | 0.5828 | 24.9932 | 0 | 90 | B-3-2a | 2025 | Addition | Transformer
ACHE1- | ACHE3- | 0.36 | 18 | 0 | 120 | B-3-2a | 2027 | Addition | Transformer
AIGN1- | AIGN5- | 1.76 | 44.89 | 0 | 36 | B-3-2a | 2027 | Addition | Transformer
ALYT2A | ALYT4J | 0.0252 | 1.1997 | -0.0005 | 1200 | B-3-2a | 2027 | Addition | Transformer
ALYT2B | ALYT4K | 0.0253 | 1.2081 | -0.0005 | 1200 | B-3-2a | 2027 | Addition | Transformer
BEAU1J | BEAU2J | 0.1486 | 5.3035 | -0.0006 | 360 | B-3-2a | 2027 | Change | Transformer
BLBS3- | BLBS4- | 0.09 | 4.475 | 0 | 400 | B-3-2a | 2027 | Addition | Transformer
BLEX1- | BLEX3- | 0.36 | 18 | 0 | 120 | B-3-2a | 2027 | Addition | Transformer
BLHI1J | BLHI2J | 0.1486 | 5.3035 | -0.0006 | 360 | B-3-2a | 2027 | Addition | Transformer
CAID2- | CAID3- | 0.36 | 18 | 0 | 120 | B-3-2a | 2027 | Addition | Transformer
CLGO1- | CLGO2- | 0.1486 | 5.3035 | -0.0006 | 360 | B-3-2a | 2027 | Addition | Transformer
CLGO1- | CLGO2A | 0.1486 | 5.3035 | -0.0006 | 360 | B-3-2a | 2027 | Addition | Transformer
CULL1A | CULL5- | 1.733 | 37.56 | 0 | 36 | B-3-2a | 2027 | Addition | Transformer
DEAW1- | DEAW5- | 1.14 | 25.05 | 0 | 45 | B-3-2a | 2027 | Addition | Transformer
DOUN1- | DOUN3- | 0.5 | 25 | 0 | 120 | B-3-2a | 2027 | Change | Transformer
DOUN1- | DOUN3- | 0.5 | 25 | 0 | 120 | B-3-2a | 2027 | Change | Transformer
ELCH1- | ELCH3- | 0.75 | 15 | 0 | 120 | B-3-2a | 2027 | Addition | Transformer
FARI1J | FARI2J | 0.2184 | 8.2304 | -0.0007 | 240 | B-3-2a | 2027 | Change | Transformer
FARI1K | FARI2K | 0.2184 | 8.2304 | -0.0007 | 240 | B-3-2a | 2027 | Change | Transformer
FETT1- | FETT4J | 0.108 | 3.9569 | -0.0007 | 480 | B-3-2a | 2027 | Addition | Transformer
KINT1- | KINT2K | 0.3751 | 10.2314 | -0.015 | 240 | B-3-2a | 2027 | Change | Transformer
KINT1- | KINT3- | 0.5 | 25 | 0 | 120 | B-3-2a | 2027 | Change | Transformer
KION1- | KION5- | 1.78 | 45.42 | 0 | 36 | B-3-2a | 2027 | Addition | Transformer
LAIS1B | LAIS3- | 0.36 | 18 | 0 | 60 | B-3-2a | 2027 | Addition | Transformer
LUNA1Q | LUNA3- | 0.5 | 25 | 0 | 120 | B-3-2a | 2027 | Change | Transformer
LUNA1R | LUNA3- | 0.5 | 25 | -0.0222 | 120 | B-3-2a | 2027 | Change | Transformer
SFIL1Q | SFIL5- | 1.99 | 39.48 | 0 | 45 | B-3-2a | 2027 | Change | Transformer
STNG1E | STNG3- | 0.2151 | 25.124 | -0.009 | 120 | B-3-2a | 2027 | Addition | Transformer
STNG1E | STNG3- | 0.2151 | 25.124 | -0.009 | 120 | B-3-2a | 2027 | Addition | Transformer
STSO1B | STSO3A | 0.36 | 18 | 0 | 120 | B-3-2a | 2027 | Addition | Transformer
STSO1B | STSO3B | 0.36 | 18 | 0 | 120 | B-3-2a | 2027 | Addition | Transformer
STWO1- | STWO3- | 0.36 | 18 | 0 | 90 | B-3-2a | 2027 | Addition | Transformer
ANSN2- | ANSN3- | 0.258 | 20.06 | 0 | 120 | B-3-2a | 2029 | Addition | Transformer
ARBR1Q | ARBR3- | 0.5 | 25 | 0 | 120 | B-3-2a | 2029 | Change | Transformer
ARBR1R | ARBR3- | 0.5 | 25 | 0 | 120 | B-3-2a | 2029 | Change | Transformer
ASBS1- | ASBS4B | 0.08 | 4 | 0 | 480 | B-3-2a | 2029 | Addition | Transformer
ASBS1- | ASBS4B | 0.08 | 4 | 0 | 480 | B-3-2a | 2029 | Addition | Transformer
BANN4J | SPIT2J | 0.026 | 1.533 | -0.0005 | 1200 | B-3-2a | 2029 | Addition | Transformer
BANN4K | SPIT2K | 0.026 | 1.533 | -0.0005 | 1200 | B-3-2a | 2029 | Addition | Transformer
BEWF1- | BEWF3- | 0.36 | 17.9968 | 0 | 90 | B-3-2a | 2029 | Addition | Transformer
BING4- | FASN1A | 0.106 | 3.957 | -0.0007 | 480 | B-3-2a | 2029 | Addition | Transformer
BING4- | FASN1B | 0.106 | 3.957 | -0.0007 | 480 | B-3-2a | 2029 | Addition | Transformer
BRCW1A | BRCW3- | 0.4181 | 24.9965 | 0 | 120 | B-3-2a | 2029 | Addition | Transformer
BRCW1A | CMBS4A | 0.106 | 3.957 | -0.0007 | 480 | B-3-2a | 2029 | Addition | Transformer
BRCW1B | BRCW3- | 0.4181 | 24.9965 | 0 | 120 | B-3-2a | 2029 | Addition | Transformer
BRCW1B | CMBS4B | 0.106 | 3.957 | -0.0007 | 480 | B-3-2a | 2029 | Addition | Transformer
BROA1- | BROA3- | 1.19 | 39 | 0 | 30 | B-3-2a | 2029 | Addition | Transformer
BROA1- | BROA3- | 0.5 | 25 | 0 | 45 | B-3-2a | 2029 | Addition | Transformer
CLOI1- | CLOI3- | 0.36 | 18 | 0 | 120 | B-3-2a | 2029 | Addition | Transformer
COST1- | COST3- | 0.54 | 18 | 0 | 45 | B-3-2a | 2029 | Addition | Transformer
CRAS2- | CRAS3- | 0.258 | 20.06 | 0 | 120 | B-3-2a | 2029 | Addition | Transformer
CRDH1J | CRDH2J | 0.098 | 3.936 | -0.0006 | 480 | B-3-2a | 2029 | Addition | Transformer
CRDH1K | CRDH2K | 0.098 | 3.936 | -0.0006 | 480 | B-3-2a | 2029 | Addition | Transformer
CRMU2J | CRMU3- | 0.42 | 20 | 0 | 120 | B-3-2a | 2029 | Addition | Transformer
CRMU2K | CRMU3- | 0.42 | 20 | 0 | 120 | B-3-2a | 2029 | Addition | Transformer
CRSN1Q | CRSN2Q | 0.098 | 3.936 | -0.0006 | 480 | B-3-2a | 2029 | Addition | Transformer
CRSN1R | CRSN2R | 0.098 | 3.936 | -0.0006 | 480 | B-3-2a | 2029 | Addition | Transformer
CRSS1X | CRSS2A | 0.2466 | 9.0008 | -0.0005 | 240 | B-3-2a | 2029 | Addition | Transformer
CRSS1Y | CRSS2B | 0.2459 | 9.0175 | -0.0005 | 240 | B-3-2a | 2029 | Addition | Transformer
DUNO1Q | DUNO3- | 0.5 | 25 | 0 | 120 | B-3-2a | 2029 | Change | Transformer
DUNO1R | DUNO3- | 0.5 | 25 | 0 | 120 | B-3-2a | 2029 | Change | Transformer
EARR2B | EARR3- | 0.258 | 20.06 | 0 | 120 | B-3-2a | 2029 | Addition | Transformer
EDIN1J | EDIN3- | 0.558 | 16.991 | 0 | 60 | B-3-2a | 2029 | Addition | Transformer
EDIN1J | EDIN8B | 0.16 | 8 | 0 | 125 | B-3-2a | 2029 | Addition | Transformer
EDIN1K | EDIN3A | 0.2578 | 24.757 | 0 | 120 | B-3-2a | 2029 | Addition | Transformer
EDIN1K | EDIN8A | 0.16 | 8 | 0 | 125 | B-3-2a | 2029 | Addition | Transformer
ERED2- | ERED3- | 0.258 | 20.06 | 0 | 120 | B-3-2a | 2029 | Addition | Transformer
FASN1A | FASN3- | 0.4181 | 24.9965 | 0 | 120 | B-3-2a | 2029 | Addition | Transformer
FASN1B | FASN3- | 0.4181 | 24.9965 | 0 | 120 | B-3-2a | 2029 | Addition | Transformer
FASQ1J | FASQ3- | 0.75 | 15 | 0 | 120 | B-3-2a | 2029 | Addition | Transformer
FAUG1- | FAUG4J | 0.2149 | 8.0138 | -0.013 | 240 | B-3-2a | 2029 | Addition | Transformer
FAUG1- | FAUG4J | 0.3185 | 8.4523 | -0.013 | 240 | B-3-2a | 2029 | Addition | Transformer
FETT1- | FETT4K | 0.108 | 3.9569 | -0.0007 | 480 | B-3-2a | 2029 | Addition | Transformer
FINS1- | FINS2A | 0.044 | 5.833 | 0 | 360 | B-3-2a | 2029 | Addition | Transformer
FINS1- | FINS3- | 0.451 | 25 | 0 | 120 | B-3-2a | 2029 | Addition | Transformer
FINS1- | FINS3- | 0.451 | 25 | 0 | 120 | B-3-2a | 2029 | Addition | Transformer
FINS1- | HEST3- | 0.54 | 18 | 0 | 45 | B-3-2a | 2029 | Addition | Transformer
GLNU1- | GLNU3- | 0.36 | 18 | 0 | 60 | B-3-2a | 2029 | Addition | Transformer
GREM1N | MSHL3- | 0.5828 | 24.9932 | 0 | 90 | B-3-2a | 2029 | Addition | Transformer
KINA4A | TUMM1J | 0.2149 | 8.0138 | -0.013 | 240 | B-3-2a | 2029 | Addition | Transformer
KINA4B | TUMM1K | 0.2149 | 8.0138 | -0.013 | 240 | B-3-2a | 2029 | Addition | Transformer
KRKN1- | KRKN3- | 0.36 | 18 | 0 | 90 | B-3-2a | 2029 | Addition | Transformer
LOCL1J | LOCL4K | 0.108 | 3.957 | -0.0007 | 480 | B-3-2a | 2029 | Addition | Transformer
LOCL1K | LOCL4J | 0.106 | 3.957 | -0.0007 | 480 | B-3-2a | 2029 | Addition | Transformer
SLOY1L | SLOY5L | 0.8557 | 25 | 0 | 60 | B-3-2a | 2029 | Change | Transformer
SLOY1M | SLOY5M | 0.862 | 25 | 0 | 60 | B-3-2a | 2029 | Change | Transformer
SLOY1N | SLOY5N | 0.859 | 25 | 0 | 60 | B-3-2a | 2029 | Change | Transformer
SLOY1P | SLOY5P | 0.862 | 25 | 0 | 60 | B-3-2a | 2029 | Change | Transformer
TNGF1A | TNGF3- | 0.36 | 18 | 0 | 120 | B-3-2a | 2029 | Addition | Transformer
AREX1- | AREX3- | 0.2843 | 16.9754 | -0.0173 | 90 | B-3-2b | 2025 | Addition | Transformer
BENB1- | BENB3- | 0.1922 | 14.207 | -0.0113 | 120 | B-3-2b | 2025 | Addition | Transformer
CLAU1- | CLAU3- | 0.1922 | 14.207 | -0.0113 | 120 | B-3-2b | 2025 | Addition | Transformer
CUMW1- | CUMW3- | 0.1922 | 14.207 | -0.0113 | 120 | B-3-2b | 2025 | Addition | Transformer
DENN4- | DENN2- | 0.0164 | 1.6449 | -0.1161 | 1000 | B-3-2b | 2025 | Addition | Transformer
GIFF2Q | GIFF3A | 0.4557 | 30.1188 | -0.0331 | 90 | B-3-2b | 2025 | Change | Transformer
HUNE4- | HUNE1- | 0.1122 | 9.3465 | -0.2007 | 360 | B-3-2b | 2025 | Addition | Transformer
HUNE4- | HUNE1- | 0.1134 | 9.4715 | -0.1992 | 360 | B-3-2b | 2025 | Addition | Transformer
MAHI2- | MAHI1C | 0.1284 | 8.6824 | -0.2535 | 240 | B-3-2b | 2025 | Addition | Transformer
MOFF1- | MOFF3- | 0.4635 | 24.1789 | -0.0101 | 60 | B-3-2b | 2025 | Addition | Transformer
MOFF4- | MOFF1A | 0.0914 | 6.4382 | -0.0751 | 360 | B-3-2b | 2025 | Addition | Transformer
NECU2- | NECU1B | 0.1161 | 8.5534 | -0.0293 | 240 | B-3-2b | 2025 | Addition | Transformer
NECU2- | NECU1B | 0.1476 | 8.7488 | -0.1299 | 240 | B-3-2b | 2025 | Addition | Transformer
NECU2- | NECU1B | 0.1164 | 8.5534 | -0.0287 | 240 | B-3-2b | 2025 | Addition | Transformer
NECU2- | NECU1C | 0.1111 | 6.6657 | -0.0006 | 360 | B-3-2b | 2025 | Addition | Transformer
NECU2- | NECU1C | 0.1111 | 6.6657 | -0.0006 | 360 | B-3-2b | 2025 | Addition | Transformer
NETS1- | NETS3- | 0.8311 | 28.2878 | -0.0097 | 60 | B-3-2b | 2025 | Addition | Transformer
OHLL1- | OHLL3- | 0.4635 | 24.1789 | -0.0101 | 60 | B-3-2b | 2025 | Addition | Transformer
PORD2R | PORD3- | 0.4557 | 30.1188 | -0.0331 | 90 | B-3-2b | 2025 | Change | Transformer
STOC1- | STOC3- | 0.1922 | 14.207 | -0.0113 | 120 | B-3-2b | 2025 | Addition | Transformer
WGEO2R | WGEO3- | 0.4557 | 30.1188 | -0.0331 | 90 | B-3-2b | 2025 | Change | Transformer
ARCR2- | ARCR3A | 0.1883 | 12.5319 | -0.0338 | 120 | B-3-2b | 2027 | Addition | Transformer
ARCR2- | ARCR3B | 0.1883 | 12.5319 | -0.0338 | 120 | B-3-2b | 2027 | Addition | Transformer
COBA4- | COBA3- | 0.2383 | 11.6642 | -0.0232 | 120 | B-3-2b | 2027 | Addition | Transformer
DEBS2- | DEBS3A | 0.1883 | 12.5319 | -0.0338 | 120 | B-3-2b | 2027 | Addition | Transformer
DEBS2- | DEBS3B | 0.1883 | 12.5319 | -0.0338 | 120 | B-3-2b | 2027 | Addition | Transformer
DEBS2- | DEBS3C | 0.1883 | 12.5319 | -0.0338 | 120 | B-3-2b | 2027 | Addition | Transformer
DEBS2- | DEBS3D | 0.1883 | 12.5319 | -0.0338 | 120 | B-3-2b | 2027 | Addition | Transformer
DEBS2- | DEBS3E | 0.1883 | 12.5319 | -0.0338 | 120 | B-3-2b | 2027 | Addition | Transformer
FELL1- | FELL3- | 0.4635 | 24.1789 | -0.0101 | 60 | B-3-2b | 2027 | Addition | Transformer
GALA1- | GALA3- | 0.917 | 55.0024 | 0 | 10 | B-3-2b | 2027 | Addition | Transformer
GALA1- | GALA3- | 0.917 | 55.0024 | 0 | 10 | B-3-2b | 2027 | Addition | Transformer
GHPS1- | GHPS3A | 0.1922 | 14.207 | -0.0113 | 120 | B-3-2b | 2027 | Addition | Transformer
GHPS1- | GHPS3B | 0.1922 | 14.207 | -0.0113 | 120 | B-3-2b | 2027 | Addition | Transformer
GIFF2R | GIFF3B | 0.4557 | 30.1188 | -0.0331 | 120 | B-3-2b | 2027 | Change | Transformer
GNSH1- | GNSH3- | 0.4635 | 24.1789 | -0.0101 | 60 | B-3-2b | 2027 | Addition | Transformer
HORI1- | HORI3A | 0.2843 | 16.9754 | -0.0173 | 90 | B-3-2b | 2027 | Addition | Transformer
HORI1- | HORI3B | 0.4635 | 24.1789 | -0.0101 | 60 | B-3-2b | 2027 | Addition | Transformer
KINN4- | KINN2A | 0.0152 | 1.6463 | -0.1118 | 1100 | B-3-2b | 2027 | Addition | Transformer
KINN4- | KINN2B | 0.0152 | 1.6463 | -0.1118 | 1100 | B-3-2b | 2027 | Addition | Transformer
LETH1- | LETH3- | 0.2843 | 16.9754 | -0.0173 | 90 | B-3-2b | 2027 | Addition | Transformer
LETH1- | LETH3- | 0.2843 | 16.9754 | -0.0173 | 90 | B-3-2b | 2027 | Addition | Transformer
LORG1- | LORG3- | 0.2843 | 16.9754 | -0.0173 | 90 | B-3-2b | 2027 | Addition | Transformer
OFOA1- | OFOA3- | 0.4635 | 24.1789 | -0.0101 | 60 | B-3-2b | 2027 | Addition | Transformer
REDS1A | REDS3A | 0.4635 | 24.1789 | -0.0101 | 60 | B-3-2b | 2027 | Addition | Transformer
REDS4- | REDS1A | 0.1119 | 9.3882 | -0.1905 | 360 | B-3-2b | 2027 | Addition | Transformer
REDS4- | REDS1A | 0.1119 | 9.3882 | -0.1905 | 360 | B-3-2b | 2027 | Addition | Transformer
TRSN1- | TRSN3- | 0.2843 | 16.9754 | -0.0173 | 90 | B-3-2b | 2027 | Addition | Transformer
CLFO1- | CLFO3- | 0.1922 | 14.207 | -0.0113 | 120 | B-3-2b | 2029 | Addition | Transformer
CLYM4- | CLYM2- | 0.015 | 1.6499 | -0.2252 | 1000 | B-3-2b | 2029 | Addition | Transformer
CLYM4- | CLYM2- | 0.015 | 1.6499 | -0.2252 | 1000 | B-3-2b | 2029 | Addition | Transformer
CRCK2- | CRCK3- | 0.2857 | 19.998 | 0 | 90 | B-3-2b | 2029 | Addition | Transformer
DAER1- | DAER3- | 0.1922 | 14.207 | -0.0113 | 120 | B-3-2b | 2029 | Addition | Transformer
DUNE1- | DUNE3A | 0.1922 | 14.207 | -0.0113 | 120 | B-3-2b | 2029 | Addition | Transformer
EUCH1- | EUCH3- | 0.1922 | 14.207 | -0.0113 | 120 | B-3-2b | 2029 | Addition | Transformer
FALL4- | FALL3C | 0.2564 | 16.6647 | 0 | 120 | B-3-2b | 2029 | Addition | Transformer
GALN4- | GALN1Q | 0.1119 | 9.3882 | -0.1905 | 360 | B-3-2b | 2029 | Addition | Transformer
GALN4- | GALN1R | 0.1119 | 9.3882 | -0.1905 | 360 | B-3-2b | 2029 | Addition | Transformer
GHPS4- | GHPS1- | 0.1119 | 9.3882 | -0.1905 | 360 | B-3-2b | 2029 | Addition | Transformer
GHPS4- | GHPS1- | 0.1119 | 9.3882 | -0.1905 | 360 | B-3-2b | 2029 | Addition | Transformer
GHPS4- | GHPS1- | 0.1119 | 9.3882 | -0.1905 | 360 | B-3-2b | 2029 | Addition | Transformer
HLND1- | HLND3- | 0.2843 | 16.9754 | -0.0173 | 90 | B-3-2b | 2029 | Addition | Transformer
KNOK1- | KNOK3- | 0.1922 | 14.207 | -0.0113 | 120 | B-3-2b | 2029 | Addition | Transformer
LEGO1Q | LEGO3- | 0.3119 | 21.8311 | 0 | 60 | B-3-2b | 2029 | Addition | Transformer
LEGO1R | LEGO3- | 0.3119 | 21.8311 | 0 | 60 | B-3-2b | 2029 | Addition | Transformer
NLEI1- | NLEI3A | 0.2843 | 16.9754 | -0.0173 | 90 | B-3-2b | 2029 | Addition | Transformer
NLEI1- | NLEI3B | 0.2843 | 16.9754 | -0.0173 | 90 | B-3-2b | 2029 | Addition | Transformer
NOKY1- | NOKY3A | 0.2226 | 14.49 | -0.0076 | 120 | B-3-2b | 2029 | Change | Transformer
NOKY1- | NOKY3B | 0.2344 | 14.3231 | -0.0107 | 120 | B-3-2b | 2029 | Change | Transformer
QUAN1- | QUAN3- | 0.1922 | 14.207 | -0.0113 | 120 | B-3-2b | 2029 | Addition | Transformer
SPRB1- | SPRB3- | 0.1857 | 12.9987 | 0 | 160 | B-3-2b | 2029 | Addition | Transformer
WIYH4Q | WIYH2- | 0.0133 | 1.6699 | -0.3581 | 1000 | B-3-2b | 2029 | Addition | Transformer
WLER2- | WLER3A | 0.4321 | 27.7744 | -0.0372 | 180 | B-3-2b | 2029 | Addition | Transformer
WLER2- | WLER3C | 0.4321 | 27.7744 | -0.0372 | 180 | B-3-2b | 2029 | Addition | Transformer
WLER2- | WLER3E | 0.4321 | 27.7744 | -0.0372 | 180 | B-3-2b | 2029 | Addition | Transformer
BENR41 | BENR11 | 0.1303 | 7.8698 | -0.4285 | 240 | B-3-2c | 2025 | Addition | Transformer
BENR41 | BENR11 | 0.1303 | 7.8698 | -0.4285 | 240 | B-3-2c | 2025 | Addition | Transformer
HARG41 | HARG11 | 0.148 | 7.4973 | -0.3849 | 240 | B-3-2c | 2025 | Addition | Transformer
HARG41 | HARG11 | 0.148 | 7.4973 | -0.3849 | 240 | B-3-2c | 2025 | Addition | Transformer
HARG41 | HARG11 | 0.148 | 7.4973 | -0.3849 | 240 | B-3-2c | 2025 | Addition | Transformer
HARG41 | HARG11 | 0.148 | 7.4973 | -0.3849 | 240 | B-3-2c | 2025 | Addition | Transformer
LHOR4A | LHOR11 | 0.1373 | 8.1976 | -0.1719 | 240 | B-3-2c | 2025 | Addition | Transformer
LHOR4B | LHOR11 | 0.1307 | 7.9515 | -0.1098 | 240 | B-3-2c | 2025 | Addition | Transformer
NEWX41 | NEWX21 | 0.0132 | 1.4627 | -2.0624 | 1100 | B-3-2c | 2025 | Addition | Transformer
NEWX41 | NEWX21 | 0.0132 | 1.4627 | -2.0624 | 1100 | B-3-2c | 2025 | Addition | Transformer
ALVE41 | ALVE11 | 0.1118 | 8.3874 | -0.0906 | 278 | B-3-2c | 2027 | Addition | Transformer
ALVE41 | ALVE11 | 0.1621 | 8.0984 | -0.0747 | 275 | B-3-2c | 2027 | Addition | Transformer
BRIM4C | BRIM11 | 0.1264 | 7.974 | -0.1303 | 262 | B-3-2c | 2027 | Addition | Transformer
BRIM4D | BRIM11 | 0.1264 | 7.974 | -0.1303 | 262 | B-3-2c | 2027 | Addition | Transformer
HACK41 | HACK61 | 0.1529 | 12.1324 | -0.0623 | 278 | B-3-2c | 2027 | Addition | Transformer
HACK41 | HACK61 | 0.1529 | 12.1324 | -0.0623 | 278 | B-3-2c | 2027 | Addition | Transformer
HARG41 | HARG11 | 0.148 | 7.4973 | -0.3849 | 240 | B-3-2c | 2027 | Addition | Transformer
HARG41 | HARG11 | 0.148 | 7.4973 | -0.3849 | 240 | B-3-2c | 2027 | Addition | Transformer
HARG41 | HARG21 | 0.0152 | 1.6463 | -0.1118 | 1100 | B-3-2c | 2027 | Addition | Transformer
HARG41 | HARG2A | 0.0152 | 1.6463 | -0.1118 | 1100 | B-3-2c | 2027 | Addition | Transformer
HARG41 | HARG2A | 0.0152 | 1.6463 | -0.1118 | 1100 | B-3-2c | 2027 | Addition | Transformer
MONF42 | MFSN21 | 0.0152 | 1.6463 | -0.1118 | 1100 | B-3-2c | 2027 | Addition | Transformer
MONF42 | MFSN21 | 0.0152 | 1.6463 | -0.1118 | 1100 | B-3-2c | 2027 | Addition | Transformer
MONF42 | MFSN21 | 0.0152 | 1.6463 | -0.1118 | 1100 | B-3-2c | 2027 | Addition | Transformer
MONF42 | MFSN21 | 0.0152 | 1.6463 | -0.1118 | 1100 | B-3-2c | 2027 | Addition | Transformer
MONF42 | MONF21 | 0.0176 | 1.5828 | -0.1018 | 1000 | B-3-2c | 2027 | Addition | Transformer
OSBA42 | OSBA11 | 0.1373 | 8.1976 | -0.1238 | 278 | B-3-2c | 2027 | Addition | Transformer
POAB41 | POAB11 | 0.0282 | 4.3546 | -0.2109 | 460 | B-3-2c | 2027 | Addition | Transformer
POAB41 | POAB11 | 0.0282 | 4.3546 | -0.2109 | 460 | B-3-2c | 2027 | Addition | Transformer
POAB41 | POAB11 | 0.0282 | 4.3546 | -0.2109 | 460 | B-3-2c | 2027 | Addition | Transformer
WALX41 | WALX2A | 0.0176 | 1.5828 | -0.1018 | 1136 | B-3-2c | 2027 | Addition | Transformer
WALX41 | WALX2A | 0.0176 | 1.5828 | -0.1018 | 1136 | B-3-2c | 2027 | Addition | Transformer
YORK4A | OVER21 | 0.0152 | 1.6463 | -0.1118 | 1100 | B-3-2c | 2027 | Addition | Transformer
YORK4A | OVER21 | 0.0152 | 1.6463 | -0.1118 | 1100 | B-3-2c | 2027 | Addition | Transformer
YORK4B | OVER21 | 0.0152 | 1.6463 | -0.1118 | 1100 | B-3-2c | 2027 | Addition | Transformer
YORK4B | OVER21 | 0.0152 | 1.6463 | -0.1118 | 1100 | B-3-2c | 2027 | Addition | Transformer
CHTE41 | CHTE11 | 0.1307 | 7.9515 | -0.1098 | 261 | B-3-2c | 2029 | Addition | Transformer
CHTE41 | CHTE11 | 0.1307 | 7.9515 | -0.1098 | 251 | B-3-2c | 2029 | Addition | Transformer
CHTE41 | CHTE12 | 0.0997 | 8.0088 | -0.093 | 278 | B-3-2c | 2029 | Addition | Transformer
CHTE41 | CHTE12 | 0.1307 | 7.9515 | -0.1098 | 251 | B-3-2c | 2029 | Addition | Transformer
CHTE41 | CHTE21 | 0.0132 | 1.6756 | -0.4337 | 1096 | B-3-2c | 2029 | Addition | Transformer
CHTE41 | CHTE21 | 0.0132 | 1.6756 | -0.4337 | 1096 | B-3-2c | 2029 | Addition | Transformer
HAWP41 | HAWP21 | 0.0132 | 1.6756 | -0.4337 | 1000 | B-3-2c | 2029 | Addition | Transformer
HIMB41 | HIMB21 | 0.0186 | 1.5729 | -7.729 | 1044 | B-3-2c | 2029 | Addition | Transformer
POAB41 | POAB11 | 0.0282 | 4.3546 | -0.2109 | 460 | B-3-2c | 2029 | Addition | Transformer
SJOW41 | LODR61 | 0.3062 | 11.0235 | -0.4552 | 198 | B-3-2c | 2029 | Addition | Transformer
SJOW41 | SJOW11 | 0.1373 | 8.1976 | -0.9295 | 249 | B-3-2c | 2029 | Addition | Transformer
TWIN4A | TWIN11 | 0.1373 | 8.1976 | -0.1719 | 278 | B-3-2c | 2029 | Addition | Transformer
TWIN4B | TWIN11 | 0.1373 | 8.1976 | -0.1719 | 278 | B-3-2c | 2029 | Addition | Transformer

## Quadbooster
Node 1 | Node 2 | R (% on 100MVA) | X (% on 100MVA) | B (% on 100MVA) | Winter Rating (MVA) | Sheet_Name | Year | Status | Transformer Type
BEAU1J | BEAU1P | 0.177 | 3.6 | 0 | 150 | B-3-1a |  |  | Quadbooster
BEAU1K | BEAU1Q | 0.177 | 3.6 | 0 | 150 | B-3-1a |  |  | Quadbooster
ERRO1A | ERRO1J | 0.04 | 1.942 | 0 | 240 | B-3-1a |  |  | Quadbooster
ERRO1B | ERRO1K | 0.04 | 1.942 | 0 | 240 | B-3-1a |  |  | Quadbooster
ERRO1J | ERRO1T | 0.068 | 3.73 | 0 | 150 | B-3-1a |  |  | Quadbooster
FIDD1B | FIDD1R | 0.11 | 4.11 | 0 | 150 | B-3-1a |  |  | Quadbooster
PEHE1- | PEHE1- | 0.2649 | 9.2254 | -0.0005 | 240 | B-3-1a |  |  | Quadbooster
TEAL2A | TEAL2J | 0.005 | 1.185 | 0 | 700 | B-3-1a |  |  | Quadbooster
TEAL2B | TEAL2K | 0.005 | 1.185 | 0 | 700 | B-3-1a |  |  | Quadbooster
TONG1R | TONG1- | 0.0267 | 1.3331 | 0 | 90 | B-3-1b |  |  | Quadbooster
TONG1R | TONG1Q | 0.0125 | 2.5 | 0 | 90 | B-3-1b |  |  | Quadbooster
KEAD4C | KEAD41 | 0.0002 | 0.4178 | 0 | 2750 | B-3-1c |  |  | Quadbooster
KEAD4D | KEAD41 | 0.0002 | 0.2873 | 0 | 2750 | B-3-1c |  |  | Quadbooster
KEMS41 | KEMS4A | 0.0071 | 0.2875 | 0 | 2750 | B-3-1c |  |  | Quadbooster
KEMS41 | KEMS4B | 0.0071 | 0.2875 | 0 | 2750 | B-3-1c |  |  | Quadbooster
KIRK21 | KIRK2A | 0.002 | 0.9802 | 0 | 760 | B-3-1c |  |  | Quadbooster
LEGA4A | LEGA41 | 0.001 | 0.35 | 0 | 2002 | B-3-1c |  |  | Quadbooster
LEGA4B | LEGA41 | 0.001 | 0.35 | 0 | 2002 | B-3-1c |  |  | Quadbooster
OCKH21 | OCKH2A | 0.0104 | 0.867 | -4.0354 | 760 | B-3-1c |  |  | Quadbooster
PEWO41 | PEWO4A | 0.0046 | 0.2858 | -16.2245 | 2750 | B-3-1c |  |  | Quadbooster
PEWO41 | PEWO4B | 0.0071 | 0.2875 | -16.2245 | 2750 | B-3-1c |  |  | Quadbooster
STAY41 | STAY4A | 0.0002 | 0.4178 | -13.831 | 2695 | B-3-1c |  |  | Quadbooster
STSB4B | STSB4A | 0.0003 | 0.1825 | 0 | 1999 | B-3-1c |  |  | Quadbooster
WHAM41 | WHAM4A | 0.001 | 0.35 | 0 | 2000 | B-3-1c |  |  | Quadbooster
WHAM41 | WHAM4B | 0.001 | 0.35 | 0 | 2000 | B-3-1c |  |  | Quadbooster
WHSO21 | WHSO2A | 0.005 | 0.463 | 0 | 750 | B-3-1c |  |  | Quadbooster
WHSO22 | WHSO2B | 0.005 | 0.463 | 0 | 750 | B-3-1c |  |  | Quadbooster
WISD21 | WISD2A | 0.002 | 0.6673 | 0 | 750 | B-3-1c |  |  | Quadbooster
BLHI2A | BLHI2J | 0.005 | 0.4 | 0 | 865 | B-3-2a | 2029 | Addition | Quadbooster
BLHI2B | BLHI2K | 0.005 | 0.4 | 0 | 865 | B-3-2a | 2029 | Addition | Quadbooster
CRSS1J | CRSS1X | 0.0582 | 2.145 | 0 | 240 | B-3-2a | 2029 | Addition | Quadbooster
CRSS1K | CRSS1Y | 0.0582 | 2.1492 | 0 | 240 | B-3-2a | 2029 | Addition | Quadbooster
DOUN2- | DOUN2A | 0.066 | 5.333 | 0 | 360 | B-3-2a | 2029 | Addition | Quadbooster
PELH41 | PELH4A | 0.0071 | 0.2875 | 0 | 2750 | B-3-2c | 2027 | Addition | Quadbooster
PELH41 | PELH4A | 0.0071 | 0.2875 | 0 | 2750 | B-3-2c | 2027 | Addition | Quadbooster
HIGM41 | HIGM41 | 0.0002 | 0.2873 | 0 | 2750 | B-3-2c | 2029 | Addition | Quadbooster

## Shunt Reactor - SGT tertiary
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV) | Sheet_Name | Year | Status
BEAULY | BEAU3U | 1 | 0 | 90 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
BEAULY | BEAU3V | 2 | 0 | 90 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
CROSSAIG | CRSS3W | 1 | 0 | 60 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
CROSSAIG | CRSS3X | 1 | 0 | 60 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
DOUNREAY | DOUN3W | 1 | 0 | 60 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
DOUNREAY | DOUN3X | 2 | 0 | 60 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
FORT AUGUSTUS | FAUG3W | 1 | 0 | 60 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
FORT AUGUSTUS | FAUG3X | 2 | 0 | 60 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
FORT AUGUSTUS | FAUG3Y | 3 | 0 | 60 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
FORT AUGUSTUS | FAUG3Z | 4 | 0 | 60 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
KINTORE | KINT3W | 1 | 0 | 60 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
KINTORE | KINT3Y | 2 | 0 | 60 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
TEALING | TEAL3W | 1 | 0 | 28.96 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
TEALING | TEAL3Y | 1 | 0 | 28.89 | Shunt Reactor - SGT tertiary | 33 | B-4-1a
DOUNREAY | DOUN3Y | 1 | 0 | 90 | Shunt Reactor - SGT tertiary | 33 | B-4-2a | 2029 | Addition
ORKNEY FINSTOWN | FINS3Y | 1 | 0 | 90 | Shunt Reactor - SGT tertiary | 33 | B-4-2a | 2029 | Addition

## Mechanically Switched Capacitor
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV) | Sheet_Name | Year | Status
BEAULY | BEAU1J | 1 | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1a
BEAULY | BEAU1K | 1 | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1a
MACDUFF | MACD3- | 1 | 10 | 0 | Mechanically Switched Capacitor | 33 | B-4-1a
TEALING | TEAL1- | 1 | 90 | 0 | Mechanically Switched Capacitor | 132 | B-4-1a
Cockenzie | COCK2- | 1 | 231 | 0 | Mechanically Switched Capacitor | 275 | B-4-1b
Elvanfoot | ELVA4- | 1 | 226 | 0 | Mechanically Switched Capacitor | 400 | B-4-1b
Moffat | MOFF4- | 1 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1b
Windyhill | WIYH2- | 1 | 150 | 0 | Mechanically Switched Capacitor | 275 | B-4-1b
Aberthaw | ABTH11 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Aberthaw | ABTH11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Abham | ABHA11 | 3 | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Abham | ABHA12 | 1 | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Alverdiscott | ALVE11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Beddington | BEDD21 | 4B | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Beddington | BEDD22 | 3B | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Berkswell | BESW11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Berkswell | BESW12 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Berkswell | BESW12 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bishops Wood | BISW11 | 2B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bishops Wood | BISW11 | 2C | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Blyth | BLYT21 | 2 | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Blyth | BLYT21 | 1 | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Bolney | BOLN11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bolney | BOLN11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bolney | BOLN12 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bolney | BOLN12 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bolney | BOLN41 | 7 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Bolney | BOLN41 | 5 | 228 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Bradford West | BRAW11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bramford | BRFO11 | 1B | 59 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bramford | BRFO11 | 1A | 59 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bramford | BRFO11 | 1C | 59 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bridgewater | BRWA11 | 1A | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bridgewater | BRWA11 | 1B | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Burwell Main | BURW41 | -2 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Burwell Main | BURW41 | -1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Bushbury | BUSH11 | 1A | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bushbury | BUSH11 | 1C | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bushbury | BUSH11 | 1B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Bushbury | BUSH21 | 2 | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Capenhurst | CAPE21 | 1 | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Cellarhead | CELL11 | 2A | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Cellarhead | CELL11 | 2B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Cellarhead | CELL12 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Cellarhead | CELL12 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Cellarhead | CELL41 | 7 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Cellarhead | CELL41 | 8 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Chickerell | CHIC4A | 2 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
City Road | CITR41 | 2 | 56 | 0 | Mechanically Switched Capacitor | 13 | B-4-1c
City Road | CITR41 | 4 | 56 | 0 | Mechanically Switched Capacitor | 13 | B-4-1c
Coventry | COVE11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Coventry | COVE11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Coventry | COVE12 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Cowley | COWL11 | 2B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Cowley | COWL11 | 2C | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Cowley | COWL11 | 2A | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Drakelow | DRAK41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Drakelow | DRAK41 | 3 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
East Claydon | ECLA12 | 3 | 61 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
East Claydon | ECLA41 | 5 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Enderby | ENDE41 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Enderby | ENDE41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Exeter | EXET11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Exeter | EXET41 | 1 | 28 | 0 | Mechanically Switched Capacitor | 13 | B-4-1c
Exeter | EXET41 | 2 | 28 | 0 | Mechanically Switched Capacitor | 13 | B-4-1c
Fleet | FLEE11 | 2B | 53 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Fleet | FLEE11 | 2C | 53 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Fleet | FLEE11 | 2A | 53 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Fleet | FLEE41 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Grendon | GREN11 | 1A | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Grendon | GREN11 | 1C | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Grendon | GREN11 | 1B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Grendon | GREN41 | 6 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Grendon | GREN41 | 5 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Grendon | GREN41 | 3 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Grendon | GREN41 | 4 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Hams Hall | HAMH41 | 3 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Hams Hall | HAMH41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Hurst | HURS21 | 2B | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Hutton | HUTT41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Indian Queens | INDQ11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Indian Queens | INDQ11 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Indian Queens | INDQ11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Indian Queens | INDQ41 | 5 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Iron Acton | IROA11 | 6 | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Ironbridge | IRON11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Ironbridge | IRON12 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Ironbridge | IRON12 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Ironbridge | IRON41 | 5 | 231 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Kearsley | KEAR11 | 1C | 53 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Kearsley | KEAR11 | 1B | 53 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Kearsley | KEAR11 | 1A | 53 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Kirkby | KIBY11 | 1A | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Kirkby | KIBY11 | 4A | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Kirkby | KIBY11 | 2A | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Kirkby | KIBY11 | 3B | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Kirkstall | KIRK21 | 3 | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Landulph | LAND11 | 1 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Legacy | LEGA41 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Lovedean | LOVE41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Mannington | MANN11 | 1C | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Mannington | MANN11 | 2A | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Mannington | MANN11 | 1B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Mannington | MANN11 | 1A | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Mannington | MANN11 | 2B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Mannington | MANN11 | 2C | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Melksham | MELK11 | 1C | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Melksham | MELK11 | 1A | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Melksham | MELK11 | 1B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Monk Fryston | MONF21 | 1 | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Ninfield | NINF41 | 2 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Ocker Hill | OCKH21 | 2 | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Pelham | PELH41 | -1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Pelham | PELH41 | -2 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Port Ham | PORH11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Port Ham | PORH11 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Rainhill | RAIN11 | 2 | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Rainhill | RAIN11 | 4 | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Rainhill | RAIN12 | 1 | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Rainhill | RAIN12 | 3 | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Richborough | RICH41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Rochdale | ROCH11 | 1A | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Rochdale | ROCH11 | 1C | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Rochdale | ROCH11 | 1B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Rye House | RYEH41 | -1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Rye House | RYEH41 | -2 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Skelton Grange | SKLG11 | 3 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Skelton Grange | SKLG11 | 4 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Skelton Grange | SKLG11 | 2 | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Skelton Grange | SKLG21 | 6 | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
St. Johns Wood | SJOW11 | 2C | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
St. Johns Wood | SJOW11 | 2B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
St. Johns Wood | SJOW11 | 2A | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Stella West | STEW41 | 2 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Stella West | STEW41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Sundon | SUND41 | 1 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Sundon | SUND42 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Uskmouth | USKM12 | 1 | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Walham | WALH41 | 1 | 57 | 0 | Mechanically Switched Capacitor | 13 | B-4-1c
Walpole | WALP11 | 2C | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Walpole | WALP11 | 2B | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Walpole | WALP11 | 2A | 60 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Warley | WARL11 | 1C | 52 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Warley | WARL11 | 1B | 52 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Warley | WARL11 | 1A | 52 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
West Ham | WHAM41 | 4 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
West Melton | WMEL12 | 3C | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
West Melton | WMEL12 | 3A | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
West Melton | WMEL12 | 3B | 45 | 0 | Mechanically Switched Capacitor | 132 | B-4-1c
Whitegate | WHGA21 | 2 | 154 | 0 | Mechanically Switched Capacitor | 275 | B-4-1c
Wymondley | WYMO41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
Wymondley | WYMO41 | 2 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-1c
ALYTH | ALYT4J | 1 | 100 | 0 | Mechanically Switched Capacitor | 400 | B-4-2a | 2027 | Addition
KINARDOCHY | KINA4B | 1 | 100 | 0 | Mechanically Switched Capacitor | 400 | B-4-2a | 2029 | Addition
Kincardine | KINC2- | 2 | 232 | 0 | Mechanically Switched Capacitor | 275 | B-4-2b | 2029 | Addition
Kincardine | KINC2- | 1 | 232 | 0 | Mechanically Switched Capacitor | 275 | B-4-2b | 2029 | Addition
Harker GIS | HARG41 | 4 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-2c | 2027 | Addition
Harker GIS | HARG41 | 5A | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-2c | 2027 | Addition
Harker GIS | HARG41 | 5B | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-2c | 2027 | Addition
Lackenby | LACK41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-2c | 2027 | Addition
Norton | NORT41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-2c | 2027 | Addition
Spennymoor | SPEN41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-2c | 2027 | Addition
Penwortham | PEWO41 | 1 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-2c | 2028 | Addition
Penwortham | PEWO41 | 2 | 225 | 0 | Mechanically Switched Capacitor | 400 | B-4-2c | 2028 | Addition
Harker GIS | HARG41 | 4 | 230 | 0 | Mechanically Switched Capacitor | 400 | B-4-2c | 2029 | Addition

## SVC
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV) | Sheet_Name | Year | Status
BEAULY | BEAU2J | 1 | 150 | 150 | SVC | 275 | B-4-1a
TEALING | TEAL2J | 1 | 225 | 75 | SVC | 275 | B-4-1a
Bolney | BOLN41 | 6 | 225 | 100 | SVC | 32 | B-4-1c
Cellarhead | CELL41 | 6 | 150 | 95 | SVC | 7.9 | B-4-1c
Cellarhead | CELL41 | 5 | 150 | 95 | SVC | 7.9 | B-4-1c
Exeter | ELLA21 | 5 | 150 | 95 | SVC | 7.9 | B-4-1c
Exeter | ELLA21 | 3 | 150 | 95 | SVC | 7.9 | B-4-1c
FECKENHAM | FECK21 | 6 | 150 | 75 | SVC | 275 | B-4-1c
Landulph | LAND42 | H | 60 | 60 | SVC | 13 | B-4-1c
Lovedean | LOVE41 | 5 | 150 | 95 | SVC | 7.9 | B-4-1c
Ninfield | NINF41 | 5 | 225 | 100 | SVC | 56.6 | B-4-1c
NINFIELD | NINF41 | 6 | 150 | 150 | SVC | 400 | B-4-1c
Richborough | RICH41 | 1 | 225 | 100 | SVC | 32 | B-4-1c
Sellindge Compound A | SELL4A | 2 | 150 | 150 | SVC | 56.6 | B-4-1c
Sellindge Compound A | SELL4A | 1 | 150 | 150 | SVC | 56.6 | B-4-1c
ALYTH | ALYT4J | 1 | 225 | 225 | SVC | 400 | B-4-2a | 2027 | Addition
KINARDOCHY | KINA4A | 1 | 225 | 225 | SVC | 400 | B-4-2a | 2029 | Addition
Mannington | MANN41 | 2 | 150 | 95 | SVC | 400 | B-4-2c | 2025 | Addition

## Shunt Reactor
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV) | Sheet_Name | Year | Status
KINTORE | KINT1- | 1 | 0 | 100 | Shunt Reactor | 132 | B-4-1a
KINTORE | KINT1B | 2 | 0 | 100 | Shunt Reactor | 132 | B-4-1a
TEALING | TEAL1- | 1 | 0 | 100 | Shunt Reactor | 132 | B-4-1a
Bonnybridge | BONN3U | 1 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Bonnybridge | BONN3V | 2 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Coalburn | COAL3U | 1 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Coalburn | COAL3V | 2 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Crystal Rig | CRYR3V | 2 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Currie | CURR3W | 3 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Dewar Place | DEWP3- | 1 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Dewar Place | DEWP3- | 2 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Eccles | ECCL3V | 1 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Elvanfoot | ELVA3V | 2 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Hunterston North | HUNN3W | 1 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Hunterston North | HUNN3X | 2 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Kilgallioch | KILG2- | 1 | 0 | 60 | Shunt Reactor | 275 | B-4-1b
Kilmarnock South | KILS3U | 4 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Kilmarnock South | KILS3X | 6 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Mark Hill | MAHI3U | 2 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Moffat | MOFF3U | 1 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Neilston | NEIL3U | 1 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Neilston | NEIL3V | 2 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Smeaton | SMEA3U | 1 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Smeaton | SMEA3V | 2 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Strathaven | STHA3V | 4 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Torness | TORN4- | 1 | 0 | 150 | Shunt Reactor | 400 | B-4-1b
Torness | TORN4- | 2 | 0 | 150 | Shunt Reactor | 400 | B-4-1b
Wishaw (Gowkthrapple) | WISH3W | 1 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Windyhill | WIYH3W | 3 | 0 | 60 | Shunt Reactor | 33 | B-4-1b
Barking | BARK22 | 2B WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Barking | BARK22 | 2B WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Barking | BARK22 | 4B WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Barking | BARK22 | 4B WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Beddington | BEDD21 | 3B | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Beddington | BEDD21 | 1B | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Beddington | BEDD21 | 5B | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Beddington | BEDD22 | 4B | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Beddington | BEDD23 | 2B | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Beddington | BEDD23 | 6A | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Birkenhead | BIRK21 | 4 WDG B | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Birkenhead | BIRK21 | 4 WDG A | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Bolney | BOLN41 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Bolney | BOLN41 | 1 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Bradford West | BRAW21 | 4 WDG B | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Bradford West | BRAW21 | 4 WDG A | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Bradford West | BRAW21 | 3 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Bradford West | BRAW21 | 5 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Bramford | BRFO41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Bredbury | BRED21 | 102 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Bredbury | BRED21 | 101 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Bredbury | BRED21 | 301 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Bredbury | BRED21 | 302 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Bushbury | BUSH21 | 3 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Bustleholme | BUST21 | 1 WDG A | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Bustleholme | BUST21 | 1 WDG B | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Bustleholme | BUST21 | 4 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Canterbury North | CANT41 | 4 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Cellarhead | CELL41 | 2 WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Cellarhead | CELL41 | 3 WDG B | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Cellarhead | CELL41 | 2 WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Cellarhead | CELL41 | 3 WDG A | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Chesterfield | CHTE21 | 4 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Chickerell | CHIC41 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Chickerell | CHIC41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Chickerell | CHIC4A | 3 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Cilfynydd | CILF41 | 1 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Cilfynydd | CILF41 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Cilfynydd | CILF41 | 6 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Cilfynydd | CILF41 | 4 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
City Road | CITR41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Coventry | COVE21 | 3 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Cowley | COWL41 | 2 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Cowley | COWL41 | 3 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Drakelow | DRAK41 | 6 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Drakelow | DRAK41 | 4 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Drax | DRAX41 | 1 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Drax | DRAX41 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
East Claydon | ECLA41 | 1 WDG B | 0 | 30 | Shunt Reactor | 13 | B-4-1c
East Claydon | ECLA41 | 2 WDG B | 0 | 30 | Shunt Reactor | 13 | B-4-1c
East Claydon | ECLA41 | 2 WDG A | 0 | 30 | Shunt Reactor | 13 | B-4-1c
East Claydon | ECLA41 | 1 WDG A | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Elland | ELLA21 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Elstree | ELST41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Feckenham | FECK41 | 4 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Feckenham | FECK41 | 4 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Fleet | FLEE41 | 3 WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Fleet | FLEE41 | 4A WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Fleet | FLEE41 | 4A WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Fleet | FLEE41 | 3 WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Frodsham | FROD41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Grain | GRAI41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Grendon | GREN41 | 1 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Greystones A | GRST2A | 1 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Greystones B | GRST2B | 3 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Hams Hall | HAMH41 | 4 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Hurst | HURS21 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Hurst | HURS21 | 3 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Hurst | HURS21 | 4 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Hurst | HURS21 | 7 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Hurst | HURS21 | 2A | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Hurst | HURS21 | 1 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Indian Queens | INDQ41 | 1 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Indian Queens | INDQ41 | 2 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Iver | IVER21 | 1A | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Iver | IVER21 | 3A | 0 | 60 | Shunt Reactor | 13 | B-4-1c
IVER | IVER4A | 6B | 0 | 55 | Shunt Reactor | 400 | B-4-1c
IVER | IVER4B | 5A | 0 | 55 | Shunt Reactor | 400 | B-4-1c
Jordanthorpe 33kV | JORD31 | 2 | 0 | 60 | Shunt Reactor | 33 | B-4-1c
Kearsley | KEAR21 | 3A | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Kingsnorth | KINO41 | 2 WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Kingsnorth | KINO41 | 1 WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Kingsnorth | KINO41 | 2 WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Kingsnorth | KINO41 | 1 WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Kingsnorth | KINO41 | 4 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Kingsnorth | KINO41 | 3 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Kirkstall | KIRK21 | 4 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Kirkstall | KIRK21 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Laleham | LALE21 | 1 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Laleham | LALE21 | 2 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Laleham | LALE21 | 3 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Landulph | LAND41 | 2 WDG B | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Landulph | LAND41 | 2 WDG A | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Landulph | LAND42 | 3 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Legacy | LEGA41 | 1 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Legacy | LEGA41 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Lister Drive | LISD21 | 1 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Lovedean | LOVE41 | 3 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Lovedean | LOVE41 | 4A | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Lovedean | LOVE41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Lovedean | LOVE41 | 7 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Melksham | MELK41 | 5 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Melksham | MELK41 | 6 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Melksham | MELK41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Mill Hill | MILH2A | 2A WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Mill Hill | MILH2A | 1B WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Mill Hill | MILH2A | 1B WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Mill Hill | MILH2B | 2A WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Nechells | NECH21 | 4 WDG B | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Nechells | NECH21 | 1 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Nechells | NECH21 | 4 WDG A | 0 | 30 | Shunt Reactor | 13 | B-4-1c
New Cross | NEWX21 | 6 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
New Cross | NEWX21 | 5 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Ninfield | NINF41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Nursling | NURS41 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Oldbury | OLDB21 | 2 WDG B | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Oldbury | OLDB21 | 2 WDG A | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Pelham | PELH41 | 3 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Pembroke | PEMB41 | 1 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Pembroke | PEMB41 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Pentir | PENT41 | 2 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Pentir | PENT41 | 5 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Penwortham | PEWO41 | 6 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Pitsmoor 33kV | PITS31 | 4 | 0 | 60 | Shunt Reactor | 33 | B-4-1c
Pitsmoor 33kV | PITS31 | 3 | 0 | 60 | Shunt Reactor | 33 | B-4-1c
Ratcliffe-On-Soar | RATS41 | 2 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Rayleigh | RAYL41 | 5 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Sandford | SAFO41 | 3 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Sandford | SAFO41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Skelton Grange | SKLG21 | 3 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Spennymoor | SPEN41 | 1 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
St. Johns Wood | SJOW41 | 2 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
St. Johns Wood | SJOW41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
St. Johns Wood | SJOW41 | 4 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Stalybridge | STAL4A | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Stella West | STEW21 | 2 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Stocksbridge | STSB4A | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Sundon | SUND41 | 5 WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Sundon | SUND41 | 5 WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Sundon | SUND42 | 8 WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Sundon | SUND42 | 8 WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Thorpe Marsh | THOM42 | 6 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Tottenham | TOTT21 | 5 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Tottenham | TOTT21 | 1 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Tottenham | TOTT22 | 3 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Tynemouth | TYNE21 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Walham | WALH41 | 3 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Walham | WALH41 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Walham | WALH41 | 4 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Walpole | WALP41 | 1 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Walpole | WALP41 | 2 | 0 | 60 | Shunt Reactor | 13 | B-4-1c
West Ham | WHAM41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
West Weybridge | WWEY21 | 1 | 0 | 100 | Shunt Reactor | 275 | B-4-1c
Whitegate | WHGA21 | 4B | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Whitegate | WHGA21 | 4A | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Willesden | WISD21 | 2B | 0 | 60 | Shunt Reactor | 13 | B-4-1c
Willesden | WISD21 | 3B WDG 1 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Willesden | WISD21 | 3B WDG 2 | 0 | 30 | Shunt Reactor | 13 | B-4-1c
Wimbledon | WIMB41 | -5 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Wimbledon | WIMB41 | 6 | 0 | 225 | Shunt Reactor | 400 | B-4-1c
Wylfa | WYLF41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
Wymondley | WYMO41 | 3 | 0 | 200 | Shunt Reactor | 400 | B-4-1c
BROADFORD | BROA1A | 1 | 0 | 60 | Shunt Reactor | 132 | B-4-2a | 2029 | Addition
BROADFORD | BROA1B | 1 | 0 | 60 | Shunt Reactor | 132 | B-4-2a | 2029 | Addition
EDINBANE | EDIN1A | 1 | 0 | 60 | Shunt Reactor | 132 | B-4-2a | 2029 | Addition
EDINBANE | EDIN1B | 1 | 0 | 60 | Shunt Reactor | 132 | B-4-2a | 2029 | Addition
Arecleoch Repowering Windfarm | ARCR2- | 1 | 0 | 60 | Shunt Reactor | 275 | B-4-2b | 2027 | Addition
Gretna | GRNA3U | 1 | 0 | 60 | Shunt Reactor | 33 | B-4-2b | 2027 | Addition
HUNE4- | HUNE4- | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-2b | 2025 | Addition
Cottam | COTT41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-2c | 2025 | Addition
East Claydon | ECLA41 | 3 | 0 | 200 | Shunt Reactor | 400 | B-4-2c | 2025 | Addition
Ironbridge | IRON41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-2c | 2025 | Addition
Melksham | MELK41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-2c | 2025 | Addition
Rowdown | ROWD41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-2c | 2025 | Addition
Taunton | TAUN42 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-2c | 2025 | Addition
Willington East | WILE41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-2c | 2025 | Addition
Bramford | BRFO41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-2c | 2029 | Addition
Bramford | BRFO41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-2c | 2029 | Addition
Chesterfield | CHTE41 | 4 | 0 | 60 | Shunt Reactor | 400 | B-4-2c | 2029 | Addition
Elstree | ELST41 | 1 | 0 | 200 | Shunt Reactor | 400 | B-4-2c | 2029 | Addition
Feckenham | FECK41 | 1 | 0 | 230 | Shunt Reactor | 400 | B-4-2c | 2029 | Addition
Melksham | MELK41 | 1 | 0 | 230 | Shunt Reactor | 400 | B-4-2c | 2029 | Addition

## STATCOM
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV) | Sheet_Name | Year | Status
MELGARVE | MELG4J | 1 | 100 | 100 | STATCOM | 400 | B-4-1a
MELGARVE | MELG4K | 1 | 100 | 100 | STATCOM | 400 | B-4-1a
Hunterston Converter Station | HUCS4- | 1 | 248 | 382 | STATCOM | 400 | B-4-1b
PHOENIX HYBRID REACTIVE COMPENSATION | NEIL2- | 1 | 70 | 70 | STATCOM | 275 | B-4-1b
ECCLES | ECCL4A | 1 | 150 | 150 | STATCOM | 400 | B-4-2b | 2025 | Addition
ECCLES | ECCL4B | 1 | 150 | 150 | STATCOM | 400 | B-4-2b | 2025 | Addition

## Sync Comp
Site Name | Node | Unit Number | MVAr Generation | MVAr Absorption | Compensation Type | Connection Voltage (kV) | Sheet_Name | Year | Status
PHOENIX HYBRID REACTIVE COMPENSATION | NEIL2- | 1 | 70 | 33 | Sync Comp | 275 | B-4-1b
ORKNEY FINSTOWN | FINS1- | 1 | 70 | 35 | Sync Comp | 132 | B-4-2a | 2029 | Addition
ORKNEY FINSTOWN | FINS1- | 2 | 70 | 35 | Sync Comp | 132 | B-4-2a | 2029 | Addition
EDINBANE | EDIN8A | 1 | 125 | 50 | Sync Comp | 132 | B-4-2a | 2029 | Addition
EDINBANE | EDIN8B | 1 | 125 | 50 | Sync Comp | 132 | B-4-2a | 2029 | Addition
ECCLES | ECCL4A | 1 | 150 | 70 | Sync Comp | 400 | B-4-2b | 2025 | Addition
ECCLES | ECCL4B | 1 | 150 | 70 | Sync Comp | 400 | B-4-2b | 2025 | Addition

## TEC Register
Project Name | Customer Name | Connection Site | Stage | MW Connected | MW Increase / Decrease | Cumulative Total Capacity (MW) | MW Effective From | Project Status | Agreement Type | HOST TO | Plant Type | Project ID | Project Number | Node_Name | MW_Capacity | ETYS_Node
17 Acres and BESS | AEUK BATTERY PROJECT II LTD | Tealing 275/33kV Substation |  | 0 | 95.76 | 95.76 | 2032-06-30 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000012ezRAAQ | PRO-004392 | TEAL3 | 0 | TEAL3W
50MW BESS Connagill | Cerulisia Ltd | Connagill 132kV Substation |  | 0 | 50 | 50 | 2031-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0lJ9000000blmDIAQ | PRO-004938 |  | 0
A'Chruach Wind Farm | A'CHRUACH WIND FARM LIMITED | A'Chruach Wind Farm 275kV Substation |  | 43 | 0 | 43 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005itEQAQ | PRO-000005 | CRAS3 | 43 | CRAS3-
AGS Calderside Battery Energy Storage System | Advance Grid Solutions Limited | Calderside 275kV Substation | 2 | 0 | 200 | 500 | 2033-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000010wexAAA | PRO-002752-2 | STHA2 | 0 | STHA2A
AGS Calderside Battery Energy Storage System | Advance Grid Solutions Limited | Calderside 275kV Substation | 1 | 0 | 300 | 300 | 2029-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000010wexAAA | PRO-002752-1 | STHA2 | 300 | STHA2A
AGS Harestonhill BESS | AGS Harestonhill Ltd | AGS Harestonhill BESS 400kV Substation |  | 0 | 500 | 500 | 2030-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000ewOTAAY | PRO-003656 | WISH4 | 500 | WISH4-
AIKENGALL II WIND FARM | AIK2A SUSTAINABLE ENERGY LTD | Wester Dod 132kV |  | 81.2 | 0 | 81.2 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005iphQAA | PRO-000559 | WESE1 | 81.2 | WESE1-
AMP Eccles BESS | Eccles Grid Stability Limited | Eccles 400/132kV |  | 0 | 49.9 | 49.9 | 2029-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000f4AmAAI | PRO-003836 | ECCL1 | 49.9 | ECCL1-
ARVEN OFFSHORE WIND FARM | ARVEN OFFSHORE WIND FARM LIMITED | Arven 400/66kV Offshore Substation |  | 0 | 1800 | 1800 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l8e000000TPOFAA4 | PRO-003288 | DOUN2 | 0 | DOUN2-
Aberarder Extension Wind Farm | Renewable Energy Systems Limited | Tomatin 275/132 kV Substation |  | 0 | 138 | 138 | 2031-04-30 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l8e0000010wQ0AAI | PRO-002589 | TOMT1 | 0 | TOMT1J
Aberarder Wind Farm | ABERARDER WIND FARM LLP | Aberarder Wind Farm 132/33kV Substation |  | 0 | 49.99 | 49.99 | 2026-08-31 | Consents Approved | Direct Connection | SHET | Wind Onshore | a0l4L0000005ilHQAQ | PRO-000368 | ABED1 | 49.99 | ABED1-
Aberdeen Offshore Wind Farm | ABERDEEN OFFSHORE WIND FARM LIMITED | Aberdeen Bay 132kV Substation |  | 95.5 | 0 | 95.5 |  | Built | Direct Connection | SHET | Wind Offshore | a0l4L0000005itBQAQ | PRO-000002 | ABBA1 | 95.5 | ABBA1-
Aberthaw (Tertiary) | Aberthaw Green Limited | Aberthaw 275kV Substation |  | 0 | 57 | 57 | 2029-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ixjQAA | PRO-000376 | ABTH2 | 57 | ABTH21
Aberthaw BESS | REWE 7 LIMITED | Aberthaw B 275/132kV Substation |  | 0 | 240 | 240 | 2037-10-15 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f65FAAQ | PRO-003954 | ABTH2 | 0 | ABTH21
Aberthaw Energy | ABERTHAW ENERGY LIMITED | Aberthaw 275kV Substation |  | 0 | 249 | 249 | 2028-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ietQAA | PRO-001697 | ABTH2 | 249 | ABTH21
Aberthaw PV & BESS Generation | CYP SOLAR LIMITED | Aberthaw 275kV Substation |  | 0 | 200 | 200 | 2029-06-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ikSQAQ | PRO-001815 | ABTH2 | 200 | ABTH21
Abhainn Dubh Wind Farm | E Power Limited | Abhainn Dubh Wind Farm 132kV Substation |  | 0 | 75 | 75 | 2029-05-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005ivFQAQ | PRO-002272 | FYRI1 | 75 | FYRI1J
Achany Extension Wind Farm | SSE Generation Limited | Shin GSP |  | 0 | 105 | 105 | 2028-03-30 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005iiYQAQ | PRO-001555 | SHIN | 105 | SHIN5-
Acheilidh Wind Farm | ENERGYFARM UK ACHEILIDH LTD | Lairg II Wind Farm 132/33kV Substation |  | 0 | 84.2 | 84.2 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0lJ9000000PDsuIAG | PRO-005042 |  | 0
Achrugan Wind Farm | Statkraft Windco 1 Limited | Achrugan 132kV Substation |  | 0 | 149 | 149 | 2029-07-31 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l4L0000005ivEQAQ | PRO-002267 | CONN1 | 149 | CONN1J
Afon Ddaw | LIGHTSOURCE SPV 214 LIMITED | Aberthaw 275kV Substation |  | 0 | 249 | 249 | 2028-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ikYQAQ | PRO-001775 | ABTH2 | 249 | ABTH21
Afton Wind Farm | AFTON WIND FARM LIMITED | Blackhill 132/33kV |  | 50 | 0 | 50 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005ipiQAA | PRO-000558 | BLAH3 | 50 | BLAH3A
Aigas (part of the Beauly Cascade) | SSE Generation Limited | Aigas Hydro 132kV Substation |  | 20 | 0 | 20 |  | Built | Direct Connection | SHET | Hydro | a0l4L0000005itFQAQ | PRO-000006 | AIGN1 | 20 | AIGN1-
Aikengall II Windfarm | AIKENGALL II COMMUNITY WIND COMPANY LIMITED | Wester Dod 132kV |  | 63.8 | 0 | 63.8 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005itGQAQ | PRO-000007 | WESE1 | 63.8 | WESE1-
Airtnoch BESS | TURBINE MARKETING SPV LIMITED | Whitelee Extension 275/33kV |  | 0 | 89 | 89 | 2027-09-29 | Scoping | Direct Connection | SPT | PV Array (Photo Voltaic/solar) | a0l4L0000005igoQAA | PRO-001107 | WLEX3 | 89 | WLEX3A
Aitkenhead Farm BESS | BOOM DEVELOPMENTS LTD | Clyde's Mill 400kV Substation |  | 0 | 300 | 300 | 2028-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000010wPWAAY | PRO-002585 | CLYM4 | 300 | CLYM4-
Akku Tealing Battery Storage | Akku Tealing Limited | Tealing 275/33kV Substation |  | 0 | 500 | 500 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000010xi1AAA | PRO-003092 | TEAL2 | 0 | TEAL2A
Al Boum Photo (Norton) | AL BOUM PHOTO LTD | Norton 400kV Substation |  | 0 | 275 | 275 | 2031-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005ixrQAA | PRO-001651 | NORT4 | 0 | NORT41
Alcemi Ridham Docks BESF | Alcemi Storage Developments 23 Ltd | North Kent Connection Node A 400kV Substation |  | 0 | 280 | 280 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TPEFAA4 | PRO-003211 | KEMS41 | 0 | KEMS41
Alcemi Armadale BESS | ALCEMI STORAGE DEVELOPMENTS 8 LTD | Bathgate 400kV |  | 0 | 280 | 280 | 2030-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000f7gRAAQ | PRO-004011 | BAGA3 | 280 | BAGA3-
Alcemi Bramford Battery Energy Storage Facility | ALCEMI STORAGE DEVELOPMENTS 1 LIMITED | Bramford 400kV Substation |  | 0 | 500 | 500 | 2030-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iaqQAA | PRO-001416 | BRFO41 | 500 | BRFO41
Alcemi Bramford Battery Energy Storage Facility Phase 2 | ALCEMI STORAGE DEVELOPMENTS 1 LIMITED | South Anglia Connection Node A 400kV Substation |  | 0 | 1000 | 1000 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TPHYAA4 | PRO-003235 |  | 0
Alcemi Coalburn Battery Energy Storage Facility | ALCEMI STORAGE DEVELOPMENTS 4 LIMITED | Coalburn 400kV GIS Substation |  | 0 | 500 | 500 | 2025-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005id4QAA | PRO-001459 | COAL4 | 500 | COAL4-
Alcemi Devilla Battery Energy Storage Facility | ALCEMI STORAGE DEVELOPMENTS 3 LIMITED | Longannet 275kV |  | 0 | 500 | 500 | 2027-10-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005icyQAA | PRO-001453 | LOAN2 | 500 | LOAN2-
Alcemi Midmill BESF | ALCEMI STORAGE DEVELOPMENTS 2 LIMITED | Kintore 275kV |  | 0 | 300 | 300 | 2029-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l4L0000005iaAQAQ | PRO-002014 | KINT2 | 300 | KINT2J
Alcemi Score 2 Battery Energy Storage Facility | ALCEMI STORAGE DEVELOPMENTS 5 LIMITED | Alcemi Score Battery 400kV Substation |  | 0 | 500 | 500 | 2029-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005ikEQAQ | PRO-001790 | PEHE | 500 | PEHE4J
Alcemi Score Battery Energy Storage Facility | ALCEMI STORAGE DEVELOPMENTS LIMITED | Alcemi Score Battery 400kV Substation |  | 0 | 500 | 500 | 2029-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l4L0000005izQQAQ | PRO-001575 | BAGA3 | 500 | BAGA3-
Alderton PV & BESS Station | BNRG ALBION LIMITED | East Claydon 400kV Substation |  | 0 | 450 | 450 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wg5AAA | PRO-002764 | ECLA4 | 0 | ECLA41
Alverdiscott | XLINKS 1 LTD | Alverdiscott 400kV Substation |  | 0 | 1800 | 1800 | 2030-08-30 | Scoping | Direct Connection | NGET | Interconnector | a0l4L0000005iwaQAA | PRO-001344 | ALVE4A | 1800 | ALVE4A
Alverdiscott | PIVOTED POWER LLP | Alverdiscott 400kV Substation | 1 | 0 | 49.9 | 49.9 | 2029-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ieSQAQ | PRO-001136-1 | ALVE4A | 49.9 | ALVE4A
Alverdiscott | PIVOTED POWER LLP | Alverdiscott 400kV Substation | 2 | 0 | 50.1 | 100 | 2036-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ieSQAQ | PRO-001136-2 | ALVE4A | 0 | ALVE4A
Alverdiscott 2 | XLINKS 1 LTD | Alverdiscott 400kV Substation |  | 0 | 1800 | 1800 | 2032-08-30 | Scoping | Direct Connection | NGET | Interconnector | a0l4L0000005iwbQAA | PRO-001345 | ALVE4A | 0 | ALVE4A
Alverdiscott Farm | Alverdiscott 10 Renewables Ltd | Alverdiscott 400kV Substation |  | 0 | 1000 | 1000 | 2037-04-24 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L000002yQZtQAM | PRO-002554 | ALVE4A | 0 | ALVE4A
Alyth | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | 1 | 0 | 450 | 450 | 2029-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iZLQAY | PRO-001978-1 | ALYT4 | 450 | ALYT4J
Alyth | ECODEV (ALYTH) LTD | Alyth Solar and Battery 400/132kV | 2 | 0 | 450 | 900 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iZLQAY | PRO-001978-2 | ALYT4 | 0 | ALYT4J
Alyth BESS Station | IGP INTERNATIONAL PROSPECTING LIMITED | Alyth 400kV Substation |  | 0 | 500 | 500 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l4L0000005j14QAA | PRO-002466 | ALYT4 | 0 | ALYT4J
Amersham | ENSO GREEN HOLDINGS Z LIMITED | Amersham Main 132kV Substation |  | 0 | 120 | 120 | 2029-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iiwQAA | PRO-001770 | AMEM1 | 120 | AMEM11
Amersham BESS & Substation | O&G Solar (SPV 31) Limited | Amersham Main 400kV Substation |  | 0 | 249.9 | 249.9 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iyBQAQ | PRO-002354 | AMEM4 | 0 | AMEM4A
Amersham Main | Amersham 10 Renewables Limited | London North West Connection Node A 400kV Substation |  | 0 | 1000 | 1000 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000TPQWAA4 | PRO-003404 |  | 0
An Suidhe Wind Farm - Argyll (SRO) | AN SUIDHE WIND FARM LIMITED | Eredine GSP |  | 19.3 | 0 | 19.3 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005itHQAQ | PRO-000009 | ERED | 19.3 | ERED3-
Apley Head Farm | Queequeg Renewables Ltd | Trent Valley South Connection Node B 400kV Substation. |  | 0 | 240 | 240 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f6EdAAI | PRO-003968 |  | 0
Appin Wind Farm | Appin Wind Farm Limited | Glenglass 132kV Substation |  | 0 | 66 | 66 | 2031-10-31 | Scoping | Direct Connection | SPT | Wind Onshore | a0l8e0000010wXBAAY | PRO-002661 |  | 0
Ardleigh Solar & BESS | Nembus BESS Limited | Hadleigh 400kV Substation |  | 0 | 600 | 600 | 2032-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wVFAAY | PRO-002644 |  | 0
Ardonald Wind Farm | Ardonald Renewables Limited | New North East 275kV Substation |  | 0 | 200 | 200 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e0000011xxpAAA | PRO-003491 |  | 0
Arecleoch | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Arecleoch 132/33kV | 2 | 0 | 216 | 330 | 2032-06-15 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005itIQAQ | PRO-000012-2 | AREC1 | 0 | AREC1-
Arecleoch | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Arecleoch 132/33kV | 1 | 114 | 0 | 114 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005itIQAQ | PRO-000012-1 | AREC3 | 114 | AREC3-
Arecleoch Windfarm Extension | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Arecleoch 132/33kV |  | 0 | 72.8 | 72.8 | 2026-08-31 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005ixHQAQ | PRO-001111 | AREC3 | 72.8 | AREC3-
Arkwright | ARLINGTON (GROUP SERVICES) LIMITED | Chesterfield 400kV Substation (Not yet constructed) |  | 0 | 57 | 57 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TPIbAAO | PRO-003248 | CHTE4 | 0 | CHTE41
Armadale Wind Farm | WIND DEVELOPMENT HOLDINGS LIMITED | Armadale 400kv Substation |  | 0 | 99 | 99 | 2027-08-01 | Awaiting Consents | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l4L0000005ipjQAA | PRO-000557 | ARMA1 | 99 | ARMA1-
Arresgill Energy Storage 1 | Arresgill Energy Storage 1 Limited | Arresgill 132kV Substation |  | 0 | 49 | 49 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000TPIRAA4 | PRO-003246 | ELVA4 | 0 | ELVA4-
Arresgill Wind Farm | ARRESGILL ENERGY LIMITED | Arresgill 132kV Substation |  | 0 | 150 | 150 | 2031-10-31 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005ikZQAQ | PRO-002409 | ELVA4 | 0 | ELVA4-
Artfield Forest Wind Farm | ARTFIELD FOREST WIND FARM LTD | Artfield Forest Wind Farm 132kV Substation |  | 0 | 85.8 | 85.8 | 2030-06-28 | Scoping | Direct Connection | SPT | Wind Onshore | a0l8e0000011zPNAAY | PRO-003578 | NECU1 | 85.8 | NECU1-
Arven South Offshore Wind Farm | ARVEN SOUTH LIMITED | Arven South 275kV Offshore Substation |  | 0 | 500 | 500 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l8e000001HxQ5AAK | PRO-004242 | DOUN2 | 0 | DOUN2-
Ashbrook Lane BESS | Downing Renewable Developments LLP | Wymondley GSP |  | 0 | 249.9 | 249.9 | 2031-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000011yd6AAA | PRO-003534 | WYMO4 | 0 | WYMO41
Assel Valley Extension Wind Farm | Renantis UK Limited | Maybole GSP | 2 | 0 | 87 | 175 | 2037-10-30 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l8e0000010wU7AAI | PRO-002632-2 | MAYB | 0 | MAYB3-
Assel Valley Extension Wind Farm | Renantis UK Limited | Maybole GSP | 1 | 0 | 88 | 88 | 2032-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l8e0000010wU7AAI | PRO-002632-1 | MAYB | 0 | MAYB3-
Astwood Solar Farm GEC | ASTWOOD GREEN ENERGY LTD | West Anglia Connection Node G 400kV Substation |  | 0 | 520 | 520 | 2034-10-31 | Scoping | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0lJ9000000blKHIAY | PRO-004799 |  | 0
Auchentiber Farm | GPC 700 Ltd | Auchentiber Farm BESS 400kV Substation |  | 0 | 700 | 700 | 2029-10-17 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000011zs9AAA | PRO-003601 | NEIL4 | 700 | NEIL4Q
Auldhouse 200MW BESS | Apatura Battery Ltd | Strathaven 275/33kV |  | 0 | 200 | 200 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000f41dAAA | PRO-003825 |  | 0
Aultmore Wind Farm (2023) | VATTENFALL WIND POWER LTD | Aultmore Wind Farm 132/33kV Substation |  | 0 | 105 | 105 | 2030-09-30 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l8e000000f6JjAAI | PRO-003975 | BLHI1 | 105 | BLHI1J
Aurora Offshore Windfarm | AURORA FLOATING OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation |  | 0 | 1000 | 1000 | 2031-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005ij0QAA | PRO-001774 | ALVE4A | 0 | ALVE4A
Awel Y Mor | AWEL Y MOR OFFSHORE WIND FARM LIMITED | Bodelwyddan 400kV Substation | 1 | 0 | 574 | 574 | 2027-04-01 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005ipBQAQ | PRO-000529-1 | BODE4 | 574 | BODE41
Awel Y Mor | AWEL Y MOR OFFSHORE WIND FARM LIMITED | Bodelwyddan 400kV Substation | 2 | 0 | 526 | 1100 | 2028-04-01 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005ipBQAQ | PRO-000529-2 | BODE4 | 526 | BODE41
Axminster | CSE25 LIMITED | Axminster 400kV Substation |  | 0 | 150 | 150 | 2028-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ixiQAA | PRO-001740 | AXMI4 | 150 | AXMI41
Axminster | HB825AXM LTD | Axminster 400kV Substation |  | 0 | 120 | 120 | 2024-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005ixvQAA | PRO-001017 | AXMI4 | 120 | AXMI41
Axminster | PIVOTED POWER LLP | Axminster 400kV Substation |  | 0 | 49.9 | 49.9 | 2027-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iufQAA | PRO-001143 | AXMI4 | 49.9 | AXMI41
Axminster - New Connection | ENSO GREEN HOLDINGS B LIMITED | Axminster 132kV Substation |  | 0 | 120 | 120 | 2029-06-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ixwQAA | PRO-001356 | AXMI1 | 120 | AXMI11
Ayr Energy Storage | KXP ALPHA I LIMITED | Ayr 275/33kV |  | 0 | 150 | 150 | 2027-04-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000f3zIAAQ | PRO-003801 | AYR-3 | 150 | AYR-3-
Ayr Farm | NEW ENERGY PARTNERSHIP LIMITED | Ayr 275/33kV |  | 0 | 500 | 500 | 2028-05-26 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000011zmYAAQ | PRO-003596 | AYR-2 | 500 | AYR-2Q
Ayre (ex Cluaran Ear - Thuath) Offshore Wind Farm | AYRE OFFSHORE WIND FARM LIMITED | Banniskirk 400kV Substation |  | 0 | 1008 | 1008 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l4L0000005ix0QAA | PRO-002100 | BANN4 | 0 | BANN4J
Ayrshire Grid Services Facility | FLEXIBLEGRIDPOWER LTD | Hunterston East 400kV substation |  | 0 | 0 | 0 | 2025-09-03 | Scoping | Direct Connection | SPT | Reactive Compensation | a0l4L0000005ibcQAA | PRO-001090 | HUNE4 | 0 | HUNE4-
BESS Cilfynydd | REWE 2 LIMITED | Cilfynydd 400kV Substation |  | 0 | 200 | 200 | 2029-07-12 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iz1QAA | PRO-002008 | CILF4 | 200 | CILF41
BESS Harker | REWE 4 LIMITED | Harker 400kV Substation |  | 0 | 200 | 200 | 2031-05-30 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005ia7QAA | PRO-002010 | HARG4 | 0 | HARG41
BESS North Farm | REWE 5 LIMITED | Chickerell 400kV Substation |  | 0 | 150 | 150 | 2031-11-01 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ic6QAA | PRO-002060 | CHIC4A | 0 | CHIC4A
BESS Swan | REWE 3 LIMITED | Swansea North 400kV Substation |  | 0 | 200 | 200 | 2028-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ia6QAA | PRO-002009 | SWAN41 | 200 | SWAN41
BF88 Oakley | BLUEFIELD RENEWABLE DEVELOPMENTS LIMITED | Chiltern Connection Node C 400kV Substation |  | 0 | 1000 | 1000 | 2038-11-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001Hy11AAC | PRO-004319 | ECLA4 | 0 | ECLA41
BLUE PLANET SOLAR | BLUE PLANET SOLAR LIMITED | Dungeness 400kV Substation |  | 0 | 500 | 500 | 2031-08-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ig5QAA | PRO-001703 | DUNG4 | 0 | DUNG41
BOOM Power Llanbabo Generation | Carrog Storage Facility Limited | Wylfa 400kV Substation |  | 0 | 300 | 300 | 2028-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005ihHQAQ | PRO-001540 | WYLF4 | 300 | WYLF41
Bad a Cheo Wind Farm | RWE RENEWABLES UK SWINDON LIMITED | Mybster 3 33kV Substation |  | 26.65 | 0 | 26.65 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005ilUQAQ | PRO-000018 | MYBS3 | 26.65 | MYBS3J
Baglan BESS IPC | IPC GRID CONNECTION TWO LIMITED | South Wales West Connection Node B 400kV Substation |  | 0 | 500 | 500 | 2036-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0lJ9000000blLjIAI | PRO-004816 | BAGB2 | 0 | BAGB21
Baillie Greener Grid Park | STATKRAFT UK LTD | Baillie 275KV Substation |  | 0 | 48 | 48 | 2030-09-30 | Scoping | Direct Connection | SHET | Energy Storage System;Reactive Compensation | a0l4L0000005ig3QAA | PRO-001701 | BAGP2 | 48 | BAGP2-
Balinoe Wind Farm | RWE RENEWABLES UK ONSHORE WIND LIMITED | A'Chruach Wind Farm 275kV Substation |  | 0 | 160.6 | 160.6 | 2034-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l8e0000012kqNAAQ | PRO-004776 | CRAS3 | 0 | CRAS3-
Ballach | ENERGYFARM UK BALLACH LTD | Ballach 132kV substation |  | 0 | 149 | 149 | 2037-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0lJ9000000PNJcIAO | PRO-005977 |  | 0
Balliemeanoch PSH | ILI (Borders PSH) Ltd | Balliemeanoch 275kV Substation |  | 0 | 900 | 900 | 2034-10-31 | Scoping | Direct Connection | SHET | Pump Storage | a0l4L0000005iROQAY | PRO-001901 | TAYN3 | 0 | TAYN3-
Ballygroggan Wind Farm | DALRIADA RENEWABLES LIMITED | Tangy IV 132KV Substation |  | 0 | 96 | 96 | 2034-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l8e000000exU0AAI | PRO-003733 | TNGF1 | 0 | TNGF1-
Balrobert Farm BESS | ELGIN ENERGY ES CO LIMITED | Knocknagael 132kV Substation |  | 0 | 150 | 150 | 2032-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e000001HpUOAA0 | PRO-004118 | KNOC1 | 0 | KNOC1J
Balvedavist 162 Battery Storage | Sun4net Ltd | Spittal 132kV Substation |  | 0 | 162 | 162 | 2027-07-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l4L0000005iaJQAQ | PRO-002024 | SPIT1 | 162 | SPIT1J
Banc y Celyn Energy Park | Wind 2 Project 2 Limited | Future Swansea North 132kV |  | 0 | 165 | 165 | 2033-07-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l4L0000005ia8QAA | PRO-002011 | SWAN1 | 0 | SWAN11
Bankend Rig III Wind Farm | WILSON RENEWABLES III LLP | Bankend Rig III Windfarm 132/33kV Substation |  | 0 | 78 | 78 | 2030-04-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l8e000000TPcZAAW | PRO-003451 | REDS1 | 78 | REDS1A
Bankhead BESS | Apatura Battery Ltd | Eccles 132/33kV |  | 0 | 500 | 500 | 2036-10-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000TPHdAAO | PRO-003236 | ECCL1 | 0 | ECCL1-
Barking BESS | O&G Solar (SPV 52) Limited | Barking 275kV Substation |  | 0 | 99.9 | 99.9 | 2028-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000011yTTAAY | PRO-003518 | BARK2 | 99.9 | BARK21
Barnby Solar Farm | KS SPV 75 LIMITED | Wymondley 400kV Substation |  | 0 | 249.9 | 249.9 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001201CAAQ | PRO-003607 | WYMO4 | 0 | WYMO41
Barrow Offshore Wind Farm | BARROW OFFSHORE WIND LIMITED | Barrow 132/33kV Offshore Substation |  | 90 | 0 | 90 |  | Built | Direct Connection | OFTO | Wind Offshore | a0l4L0000005ilXQAQ | PRO-000022 | HARG1 | 90 | HARG11
Beanacre BESS | Grenergy Renewables UK Limited | Melksham 132kV Substation |  | 0 | 200 | 200 | 2037-10-15 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iwoQAA | PRO-002452 | MELK1 | 0 | MELK11
Bearsden BESS | BEARSDEN BESS LTD | Windyhill 275kV Substation | 2 | 0 | 140 | 240 | 2033-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000012gHBAAY | PRO-004404-2 | WIYH1 | 0 | WIYH1-
Bearsden BESS | BEARSDEN BESS LTD | Windyhill 275kV Substation | 1 | 0 | 100 | 100 | 2029-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000012gHBAAY | PRO-004404-1 | WIYH1 | 100 | WIYH1-
Beatrice Sync Comp | TINZ PROGRAMME 1 PROJECTCO 3 LIMITED | Beatrice 400kV Substation |  | 0 | 0 | 0 | 2024-05-31 | Scoping | Direct Connection | SHET | Reactive Compensation | a0l4L0000005ihiQAA | PRO-001757 | BEAT4 | 0 | BEAT4-
Beatrice Wind Farm | BEATRICE OFFSHORE WINDFARM LIMITED | Beatrice 400kV Substation |  | 588 | 0 | 588 |  | Built | Direct Connection | SHET | Wind Offshore | a0l4L0000005ilYQAQ | PRO-000025 | BEAT4 | 588 | BEAT4-
Beauly 02 BESS | Virmati Energy Ltd | Beauly GSP |  | 0 | 100 | 100 | 2028-12-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e000000exTqAAI | PRO-003731 | BEAU | 100 | BEAU3U
Beaw Field Wind Farm | BEAW FIELD SHETLAND LIMITED | Beaw Field 132/33kV Substation |  | 0 | 102 | 102 | 2032-10-29 | Consents Approved | Direct Connection | SHET | Wind Onshore | a0l4L0000005iyaQAA | PRO-000026 | BEWF3 | 0 | BEWF3-
Beechgreen Energyfarm | BEECHGREEN ENERGYFARM LIMITED | Burwell Main 400kV Substation |  | 49.9 | 0 | 49.9 |  | Built | Direct Connection | NGET | PV Array (Photo Voltaic/solar) | a0l4L0000005ixnQAA | PRO-001018 | BURW4 | 49.9 | BURW41
Beinn Tharsuinn Repower | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Beinn Tharsuinn Repower 132/33kV Substation |  | 0 | 84 | 84 | 2029-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005iaNQAQ | PRO-001035 | FYRI1 | 84 | FYRI1J
Beinn an Tuirc 1 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Carradale 1 GSP |  | 0 | 95.2 | 95.2 | 2034-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l8e000000f5BiAAI | PRO-003918 | CAAD | 0 | CAAD3J
Beinneun Wind Farm | BEINNEUN WIND FARM LTD | Beinneun 132kV Substation |  | 109 | 0 | 109 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005ilZQAQ | PRO-000031 | BEIN1 | 109 | BEIN11
Bellbroughton Energy Park | ELGIN ENERGY ES CO LIMITED | Warwickshire Connection Node A 400kV Substation |  | 0 | 500 | 500 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wloAAA | PRO-002826 |  | 0
Bellrock Offshore Wind Farm | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Lyra 320/66kV Offshore Substation |  | 0 | 1200 | 1200 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l4L0000005izEQAQ | PRO-001496 |  | 0
Benbrack Wind Farm | Benbrack Wind Farm Limited | Benbrack Wind Farm 132/33kV Substation |  | 0 | 72 | 72 | 2025-01-30 | Awaiting Consents | Direct Connection | SPT | Wind Onshore | a0l4L0000005ilaQAA | PRO-000032 | BENB3 | 72 | BENB3-
Bendle Farm | Balance Power Projects Limited | Gretna 400/132kV |  | 0 | 228 | 228 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005ikkQAA | PRO-002243 | GRNA1 | 0 | GRNA1-
Bendle Farm 2.0 | Balance Power Projects Limited | Bendle Farm 132kV Substation |  | 0 | 228 | 228 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000010waRAAQ | PRO-002700 | GRNA1 | 0 | GRNA1-
Bendsmoor BESS | Apatura Battery Ltd | Bendsmoor BESS 400Kv Substation |  | 0 | 500 | 500 | 2032-06-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000011zPmAAI | PRO-003582 | GRNA1 | 0 | GRNA1-
Berkswell (Tertiary) | ENSO GREEN HOLDINGS LIMITED | Berkswell 275kV Substation | 1 | 0 | 49.9 | 49.9 | 2025-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iy3QAA | PRO-000516-1 | BESW2 | 49.9 | BESW21
Berkswell (Tertiary) | ENSO GREEN HOLDINGS LIMITED | Berkswell 275kV Substation | 2 | 0 | 7.1 | 57 | 2027-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iy3QAA | PRO-000516-2 | BESW2 | 7.1 | BESW21
Berkswell BESS | BERKSWELL ENERGY PARK LIMITED | Berkswell B 275kV Substation |  | 0 | 249.9 | 249.9 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f4n0AAA | PRO-003868 | BESW2 | 0 | BESW21
Berkswell Energy Storage | BW ESS DEVELOPMENT UK LIMITED | Berkswell 275kV Substation |  | 0 | 200 | 200 | 2026-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005ixbQAA | PRO-001788 | BESW2 | 200 | BESW21
Bernicia Energy Park | BAYWA R.E. UK LIMITED | Stella West 400kV Substation |  | 0 | 350 | 350 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012hphAAA | PRO-004541 | STEW4 | 0 | STEW41
Berwick Bank Offshore Wind Farm A | BERWICK BANK A LIMITED | Berwick Bank A 275/66kV Offshore Substation |  | 0 | 1150 | 1150 | 2028-10-31 | Scoping | Direct Connection | SPT | Wind Offshore | a0l8e0000010wTnAAI | PRO-002627 | BERW1 | 1150 | BERW1Q
Berwick Bank Offshore Wind Farm B | Berwick Bank B Limited | Berwick Bank B 275/66kV Offshore Substation | 2 | 0 | 900 | 1150 | 2029-10-31 | Scoping | Direct Connection | SPT | Wind Offshore | a0l8e000000snsQAAQ | PRO-002628-2 | BERW1 | 900 | BERW1Q
Berwick Bank Offshore Wind Farm B | Berwick Bank B Limited | Berwick Bank B 275/66kV Offshore Substation | 1 | 0 | 250 | 250 | 2029-10-31 | Scoping | Direct Connection | SPT | Wind Offshore | a0l8e000000snsQAAQ | PRO-002628-1 | BERW2 | 250 | BERW3-
Berwick Bank Offshore Wind Farm C | BERWICK BANK C LIMITED | Blyth 400kV Substation |  | 0 | 1800 | 1800 | 2029-11-30 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005io7QAA | PRO-000513 | BLYT4 | 1800 | BLYT41
Berwick Solar Wind and Battery Storage | BERWICK RENEWABLES TX LIMITED | Berwick 132/33kV |  | 0 | 100 | 100 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e0000011xxoAAA | PRO-003490 | BERW3 | 0 | BERW3-
Bewley BESS | Apatura Battery Ltd | Wearside Connection Node C 400kV Substation |  | 0 | 249 | 249 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f6uBAAQ | PRO-003993 |  | 0
Bexley GEC - Hurst Grid Park 2 | BEXLEY GREEN ENERGY CENTRE LTD | Hurst 275kV Substation |  | 0 | 228 | 228 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012hq6AAA | PRO-004546 | HURS2 | 0 | HURS21
Bhlaraidh Extension Wind Farm | SSE Generation Limited | Bhlaraidh 132/33kV Substation |  | 0 | 100.8 | 100.8 | 2026-04-01 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005ilnQAA | PRO-000383 | BLEX3 | 100.8 | BLEX3-
Bhlaraidh Wind Farm | SSE Generation Limited | Bhlaraidh 132/33kV Substation |  | 108 | 0 | 108 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005ilbQAA | PRO-000034 | BLEX3 | 108 | BLEX3-
Bicker Drove | REWE 1 LIMITED | Navenby 400kV Substation |  | 0 | 400 | 400 | 2034-05-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f4nZAAQ | PRO-003874 | BICF4 | 0 | BICF41
Bicker Fen | IB VOGT UK LTD | Trent Valley South Connection Node C 400kV Substation |  | 0 | 400 | 400 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001HxlxAAC | PRO-004295 |  | 0
Bicker Fen 1 Solar | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 1 | 0 | 49.995 | 49.995 | 2025-05-30 | Awaiting Consents | Direct Connection | NGET | PV Array (Photo Voltaic/solar) | a0l4L0000005iaOQAQ | PRO-001034-1 | BICF4 | 49.995 | BICF41
Bicker Fen 1 Solar | AGR SOLAR 2 LIMITED | Bicker Fen 400kV Substation | 2 | 0 | 7.005 | 57 | 2035-04-01 | Scoping | Direct Connection | NGET | PV Array (Photo Voltaic/solar) | a0l4L0000005iaOQAQ | PRO-001034-2 | BICF4 | 0 | BICF41
Bicker Fen 2 Solar | AGR SOLAR 3 LIMITED | Bicker Fen 400kV Substation | 2 | 0 | 7.005 | 57 | 2033-04-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005itRQAQ | PRO-001046-2 | BICF4 | 0 | BICF41
Bicker Fen 2 Solar | AGR SOLAR 3 LIMITED | Bicker Fen 400kV Substation | 1 | 0 | 49.995 | 49.995 | 2026-07-27 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005itRQAQ | PRO-001046-1 | BICF4 | 49.995 | BICF41
Bicker Fen PV & BESS Sub | O&G Solar (SPV 40) Limited | Bicker Fen 400kV Substation |  | 0 | 249.9 | 249.9 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wOiAAI | PRO-002575 | BICF4 | 0 | BICF41
Bicker Fenn Energy Park | BEACON FEN ENERGY PARK LIMITED | Bicker Fen 400kV Substation |  | 0 | 600 | 600 | 2029-06-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iZPQAY | PRO-001984 | BICF4 | 600 | BICF41
Biggleswade | Biggleswade 10 Renewables Limited | Biggleswade 400kV Substation |  | 0 | 1000 | 1000 | 2034-10-31 | Scoping | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000TPRKAA4 | PRO-003415 | BIGG4 | 0 | BIGG41
Biggleswade BESS | Central Bedfordshire Council | Biggleswade 400kV Substation |  | 0 | 57 | 57 | 2029-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iyjQAA | PRO-002165 | BIGG4 | 57 | BIGG41
Biggleswade BESS | HARMONY BW LTD | Biggleswade 400kV Substation |  | 0 | 200 | 200 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001HxbqAAC | PRO-004279 | BIGG4 | 0 | BIGG41
Biggleswade High Impact Green Energy Hub | TELIS ENERGY UK LIMITED | Biggleswade 400kV Substation |  | 0 | 1000 | 1000 | 2034-10-31 | Scoping | Direct Connection | NGET | Demand;Energy Storage System;Nuclear;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e0000012gscAAA | PRO-004477 | BIGG4 | 0 | BIGG41
Biggleswade PV | CSE38 LIMITED | Biggleswade 400kV Substation |  | 0 | 49.9 | 49.9 | 2031-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005itqQAA | PRO-002226 | BIGG4 | 0 | BIGG41
Bishops Dal Energy Park | Renewable Energy Systems Limited | Bishop Dal 132kV Substation |  | 0 | 150 | 150 | 2030-07-31 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iyJQAQ | PRO-002361 | ECCL1 | 150 | ECCL1-
BlackDyke BESS | ANESCO LIMITED | Leeds North Connection Node D 400kV Substation |  | 0 | 250 | 250 | 2035-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000012jPIAAY | PRO-004671 |  | 0
Blackcraig Wind Farm | BLACKCRAIG WIND FARM (SCOTLAND) LIMITED | Blackcraig 132/33kV |  | 52.9 | 0 | 52.9 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005ilcQAA | PRO-000035 | BLCW3 | 52.9 | BLCW3-
Blackhillock Battery | BLACKHILLOCK FLEXPOWER LTD | Blackhillock 400kV Substation |  | 0 | 349 | 349 | 2026-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l4L0000005iZ0QAI | PRO-001970 | BLHI4 | 349 | BLHI4-
Blacklaw | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Blacklaw 132/33kV | 1 | 118 | 0 | 118 |  | Built | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l4L0000005ildQAA | PRO-000036-1 | BLKL3 | 118 | BLKL3A
Blacklaw | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Blacklaw 132/33kV | 2 | 0 | 222 | 340 | 2032-10-08 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l4L0000005ildQAA | PRO-000036-2 | BLKL1 | 0 | BLKL1-
Blacklaw Extension | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Blacklaw Extension 132/33kV |  | 60 | 0 | 60 |  | Built | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l4L0000005ilzQAA | PRO-000037 | BLLX3 | 60 | BLLX3-
Blair Hill Wind Farm | Renewable Energy Systems Limited | Glenlee 132/11kV |  | 0 | 99 | 99 | 2036-10-31 | Scoping | Direct Connection | SPT | Wind Onshore | a0lJ9000000PDkoIAG | PRO-004994 |  | 0
Blairgowrie BESS | BLAIRGOWRIE BESS LTD | Coupar Angus GSP |  | 0 | 200 | 200 | 2030-05-30 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000011xxAAAQ | PRO-003482 | COUA | 200 | COUA3-
Blanket’s Farm | Noventum Power Solar 9 Limited | Warley 275kV Substation |  | 0 | 200 | 200 | 2038-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000012gs3AAA | PRO-004469 | WARL2 | 0 | WARL21
Blarghour Wind | BLARGHOUR WIND FARM LIMITED | Blarghour Substation |  | 0 | 73.1 | 73.1 | 2027-10-31 | Consents Approved | Direct Connection | SHET | Wind Onshore | a0l4L0000005itaQAA | PRO-000398 | BLGH | 73.1 | BLGH1-
Bloch Energy Park | Renewable Energy Systems Limited | Bloch Energy Park 132kV Substation |  | 0 | 126 | 126 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l4L0000005ivPQAQ | PRO-002447 |  | 0
Blyth BESS | SSE RENEWABLES SOLAR & BATTERY HOLDINGS LIMITED | Blyth 275kV Substation |  | 0 | 450 | 450 | 2036-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000010wl0AAA | PRO-002817 | BLYT2 | 0 | BLYT21
Bodelwyddan BESS and PV | Bodelwyddan Solar & Energy Storage Limited | Bodelwyddan 400kV Substation |  | 0 | 110 | 110 | 2029-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iPCQAY | PRO-001657 | BODE4 | 110 | BODE41
Bodinglee Wind Farm | Banks Renewables (Bodinglee Wind Farm) Limited | Bodinglee Wind Farm 132kV |  | 0 | 280 | 280 | 2029-04-30 | Awaiting Consents | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l4L0000005iZQQAY | PRO-001985 | REDS1 | 280 | REDS1A
Bolney | PIVOTED POWER LLP | Bolney 400kV Substation |  | 0 | 49.9 | 49.9 | 2027-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iaRQAQ | PRO-001031 | BOLN4 | 49.9 | BOLN41
Bolney (tertiary) | BOLNEY GREEN LIMITED | Bolney 400kV Substation | 1 | 0 | 49.9 | 49.9 | 2024-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ilrQAA | PRO-000380-1 | BOLN4 | 49.9 | BOLN41
Bolney (tertiary) | BOLNEY GREEN LIMITED | Bolney 400kV Substation | 2 | 0 | 7.1 | 57 | 2025-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ilrQAA | PRO-000380-2 | BOLN4 | 7.1 | BOLN41
Bolney BESS | CSE45 LIMITED | Bolney 400kV Substation |  | 0 | 49.9 | 49.9 | 2037-09-11 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f8NWAAY | PRO-004026 | BOLN4 | 0 | BOLN41
Bolney Farm | Dragon Green 2 Renewables Ltd | Bolney 400kV Substation |  | 0 | 200 | 200 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wYEAAY | PRO-002674 | BOLN4 | 0 | BOLN41
Bolney Farm 2 | DRAGON GREEN 7 RENEWABLES LTD | Bolney 400kV Substation |  | 0 | 700 | 700 | 2037-11-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wdQAAQ | PRO-002733 | BOLN4 | 0 | BOLN41
Bolney Grid Stability Services | WP GRID SERVICES 13 LIMITED | Bolney 400kV Substation |  | 0 | 0 | 0 | 2031-10-31 | Scoping | Direct Connection | NGET | Reactive Compensation | a0l8e000000f6ALAAY | PRO-003966 | BOLN4 | 0 | BOLN41
Boom Power Feckenham Generation Hub | BOOM POWER LTD | Feckenham 400kV Substation |  | 0 | 400 | 400 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iv8QAA | PRO-002312 | FECK4 | 0 | FECK41
Boom Power Seaton Hill Generation HUB | BOOM DEVELOPMENTS LTD | Cockenzie 400/275kV |  | 0 | 300 | 300 | 2033-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000f650AAA | PRO-003951 | COCK4 | 0 | COCK4Q
Borders Solar | BUCCLEUCH ESTATES LTD (THE) | Wyseby Hill GSP |  | 0 | 228 | 228 | 2036-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012gtGAAQ | PRO-004484 |  | 0
Borders Wind Farm | EDF ENERGY RENEWABLES LIMITED | Borders Windfarm 132kV |  | 0 | 400 | 400 | 2033-05-30 | Scoping | Direct Connection | NGET | Wind Onshore | a0l4L0000005iZKQAY | PRO-001977 |  | 0
Botley GEC (Ethos Green) | BOTLEY GREEN ENERGY CENTRE LTD | Botley 400kV Substation |  | 0 | 800 | 800 | 2033-10-31 | Awaiting Consents | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l8e0000010wP7AAI | PRO-002580 | COWL4 | 0 | COWL41
Botley West - Cote Solar Power Station | SOLARFIVE LTD | Botley West 400kV Substation |  | 0 | 840 | 840 | 2026-10-30 | Scoping | Direct Connection | NGET | PV Array (Photo Voltaic/solar) | a0l4L0000005ijzQAA | PRO-001587 | COWL4 | 840 | COWL41
Bowdun (ex Cluaran Deas Ear) Offshore Wind Farm | BOWDUN OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation |  | 0 | 1008 | 1008 | 2035-12-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l4L0000005idoQAA | PRO-002091 | NEDE4 | 0 | NEDE4J
Bowsheil Solar and Battery | VOLTALIA UK LTD | Bowsheils 132kV Substation |  | 0 | 166.61 | 166.61 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wXGAAY | PRO-002662 |  | 0
Bradenham - Thetford (Necton) GEC (Ethos Green) | NECTON GREEN ENERGY CENTRE LTD | Necton 400kV Substation |  | 0 | 850 | 850 | 2033-10-01 | Scoping | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l8e000000ViFJAA0 | PRO-004346 | NECT4 | 0 | NECT41
Bradford Solar Farm | SolarFour Ltd | Staffordshire Connection Node A 400kV Substation |  | 0 | 960 | 960 | 2033-10-31 | Scoping | Direct Connection | NGET | PV Array (Photo Voltaic/solar) | a0l8e0000011yCAAAY | PRO-003511 |  | 0
Bradford West 100MW | 24 POWER LTD | Bradford West 275kV Substation |  | 0 | 100 | 100 | 2026-05-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iQLQAY | PRO-001874 | BRAW2 | 100 | BRAW21
Bradford West BESS Substation | O&G Solar (SPV 36) Limited | Bradford West 275kV Substation |  | 0 | 249 | 249 | 2036-10-26 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L000002yQWuQAM | PRO-002544 | BRAW2 | 0 | BRAW21
Bradwell Energy Park | LOW CARBON SOLAR PARK 28 LIMITED | Rayleigh 400kV Substation | 1 | 0 | 499 | 499 | 2032-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e000000f7CIAAY | PRO-004004-1 | RAYL4 | 0 | RAYL41
Bradwell Energy Park | LOW CARBON SOLAR PARK 28 LIMITED | Rayleigh 400kV Substation | 2 | 0 | 551 | 1050 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e000000f7CIAAY | PRO-004004-2 | RAYL4 | 0 | RAYL41
Brae House Farm | QAIR RENEWABLES UK LIMITED | Dounreay |  | 0 | 500 | 500 | 2032-07-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e000001HxliAAC | PRO-004292 | DOUN | 0 | DOUN3-
Braegrundie Farm | AEUK BATTERY PROJECT III LTD | Beauly GSP |  | 0 | 95 | 95 | 2030-06-30 | Awaiting Consents | Direct Connection | SHET | Energy Storage System | a0l8e0000012jPXAAY | PRO-004674 | BEAU | 95 | BEAU3U
Braidfield Battery Storage | BRAIDFIELD BATTERY STORAGE LIMITED | Braidfield Battery Storage 132kV Substation |  | 0 | 100 | 100 | 2027-09-27 | Scoping | Direct Connection | SPT | Demand;Energy Storage System | a0l4L0000005iyFQAQ | PRO-002357 | WIYH1 | 100 | WIYH1-
Braintree | Braintree 10 Renewables Limited | Braintree 400kV Substation |  | 0 | 1000 | 1000 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000TPQgAAO | PRO-003406 | BRAI4 | 0 | BRAI4A
Braintree | PIVOTED POWER LLP | Braintree 400kV Substation | 1 | 0 | 49.9 | 49.9 | 2024-10-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005iZfQAI | PRO-001042-1 | BRAI4A | 49.9 | BRAI4A
Braintree | PIVOTED POWER LLP | Braintree 400kV Substation | 2 | 0 | 7.1 | 57 | 2026-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iZfQAI | PRO-001042-2 | BRAI4 | 7.1 | BRAI4A
Braintree (Tertiary) | CSE22 LIMITED | Braintree 400kV Substation |  | 0 | 49.9 | 49.9 | 2026-10-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iZeQAI | PRO-001043 | BRAI4B | 49.9 | BRAI4B
Bramford (Tertiary) | DAMSONGREEN ENERGYFARM LIMITED | Bramford 400kV Substation |  | 57 | 0 | 57 |  | Built | Direct Connection | NGET | Energy Storage System | a0l4L0000005iy5QAA | PRO-001016 | BRFO41 | 57 | BRFO41
Bramford 2 GEC (Ethos Green) | BRAMFORD 2 GREEN ENERGY CENTRE LTD | Bramford 400kV Substation |  | 0 | 57 | 57 | 2032-07-01 | Awaiting Consents | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l8e0000010wO9AAI | PRO-002568 | BRFO41 | 0 | BRFO41
Bramford BESS | CSE33 LIMITED | Bramford 400kV Substation |  | 0 | 400 | 400 | 2029-11-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005icDQAQ | PRO-002071 | BRFO41 | 400 | BRFO41
Bramford GEC (Ethos Green) | BRAMFORD GREEN ENERGY CENTRE LTD | Bramford 400kV Substation |  | 0 | 650 | 650 | 2033-10-30 | Awaiting Consents | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l8e000000f8NgAAI | PRO-004027 | BRFO42 | 0 | BRFO41
Bramford Tertiary | BRAMFORD GREEN LIMITED | Bramford 400kV Substation |  | 0 | 57 | 57 | 2026-05-16 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ilNQAQ | PRO-000397 | BRFO42 | 57 | BRFO41
Bramley (tertiary) | BRAMLEY SOLAR LIMITED | Bramley 400kV Substation |  | 0 | 57 | 57 | 2026-08-15 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ilOQAQ | PRO-000396 | BRLE4 | 57 | BRLE41
Bramley BESS | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 1 | 0 | 49.995 | 49.995 | 2025-09-29 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005igrQAA | PRO-001104-1 | BRLE4 | 49.995 | BRLE41
Bramley BESS | BRAMLEY BESS LIMITED | Bramley 400kV Substation | 2 | 0 | 7.005 | 57 | 2037-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005igrQAA | PRO-001104-2 | BRLE4 | 0 | BRLE41
Bramley Farm | BRAMLEY 2 RENEWABLES LTD | Basingstoke East 400kV Substation |  | 0 | 200 | 200 | 2038-03-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wYJAAY | PRO-002675 | BRLE4 | 0 | BRLE41
Bramley Farm 2 | BRAMLEY 7 RENEWABLES LTD | Basingstoke East 400kV Substation |  | 0 | 700 | 700 | 2038-05-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wdaAAA | PRO-002735 | BRLE4 | 0 | BRLE41
Branxton Energy Storage Facility | EastCoastGridServices Ltd | Branxton 400/132kV |  | 0 | 750 | 750 | 2029-05-13 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005idaQAA | PRO-002076 | BRNX4 | 750 | BRNX4-
Branxton PV & BESS Station | ISLAND GREEN POWER UK LIMITED | Branxton 400/132kV |  | 0 | 1000 | 1000 | 2028-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005itPQAQ | PRO-002122 | BRNX4 | 1000 | BRNX4-
Braxbess Branxton BESS | BRAXBESS LTD | Branxton 400/132KV Substation |  | 0 | 480 | 480 | 2028-04-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005iuuQAA | PRO-002208 | BRNX4 | 480 | BRNX4-
Braybrooke | SSE DE SOLAR HOLDCO LIMITED | Market Harborough 400kV Substation |  | 0 | 600 | 600 | 2032-07-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TPSSAA4 | PRO-003429 | MARH42 | 0 | MARH42
Braybrooke Solar and Battery Connection | Irena BESS LIMITED | Braybrooke (Network Rail) GSP |  | 0 | 500 | 500 | 2031-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005itZQAQ | PRO-002207 | BRAY4 | 0
Breach Solar Farm | Burwell 11 Solar Limited | Burwell 400kV Substation |  | 0 | 49.995 | 49.995 | 2024-04-25 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ixlQAA | PRO-001019 | BURW4 | 49.995 | BURW41
Breackerie wind farm | ENERGYFARM UK BREACKERIE LTD | Breackerie 132kV Substation |  | 90.8 | 0 | 90.8 | 2037-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0lJ9000000PN5RIAW | PRO-005965 |  | 0
Breakish Windfarm | ARISE AB | Breakish 132/33kV | 1 | 0 | 50 | 50 | 2029-05-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005ikhQAA | PRO-002170-1 | BROA1 | 50 | BROA1-
Breakish Windfarm | ARISE AB | Breakish 132/33kV | 2 | 0 | 49.8 | 99.8 | 2034-04-30 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005ikhQAA | PRO-002170-2 | BROA1 | 0 | BROA1-
Bredbury | PIVOTED POWER LLP | Bredbury 275kV Substation |  | 0 | 49.9 | 49.9 | 2024-09-14 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iZgQAI | PRO-001041 | BRED2 | 49.9 | BRED21
Breezy Hill Wind Farm | BROCKWELL ENERGY LIMITED | New Cumnock 275/132kV |  | 0 | 80 | 80 | 2028-04-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005intQAA | PRO-000475 | NECU1 | 80 | NECU1-
Bridge BESS | Apatura Battery Ltd | Torness 400/132kV |  | 0 | 150 | 150 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000f41iAAA | PRO-003826 | TORN1 | 0 | TORN1-
Bridgwater (tertiary) | ENSO GREEN HOLDINGS H LIMITED | Bridgwater 400/132kV Substation |  | 0 | 57 | 57 | 2026-11-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ilPQAQ | PRO-000375 | BRWA42 | 57 | BRWA42
Bridgwater 2 (tertiary) - New Conn | BRIDGWATER GREEN LIMITED | Bridgewater 400kV Substation |  | 0 | 57 | 57 | 2029-08-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iYjQAI | PRO-001347 | BRWA41 | 57 | BRWA41
Bridgwater Energy Park | EXAGEN GROUP LIMITED | Bridgwater GSP |  | 0 | 249.99 | 249.99 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001HrhnAAC | PRO-004215 | BRWA4A | 0 | BRWA4A
Brinsworth | SSE RENEWABLES SOLAR & BATTERY HOLDINGS LIMITED | Brinsworth 400kV Substation |  | 0 | 600 | 600 | 2032-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f41JAAQ | PRO-003821 | BRIN4 | 0 | BRIN41
Broadford BESS | FIELD DEVCO LTD | Broadford GSP |  | 0 | 200 | 200 | 2034-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000012kjsAAA | PRO-004756 | BROA | 0 | BROA3-
Broadshore Offshore Wind Farm | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | New Deer 2 400kV Substation |  | 0 | 900 | 900 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l4L0000005itdQAA | PRO-002171 | NEDE4 | 0 | NEDE4J
Broken Cross Windfarm | BROKEN CROSS WIND FARM LIMITED | Broken Cross 132/33kV |  | 43.2 | 4.8 | 48 | 2026-04-01 | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005ilQQAQ | PRO-000395 | BROC1 | 48 | BROC1-
Brown Rig Wind Farm | SSE RENEWABLES SERVICES (UK) LIMITED | Hawick 132kV Substation |  | 0 | 114 | 114 | 2033-10-31 | Scoping | Direct Connection | SPT | Wind Onshore | a0l8e000001HoYjAAK | PRO-004083 | HAWI1 | 0 | HAWI1-
Bryn Tilti | RHIWLAS ENERGY PARK LIMITED | Chirk GSP |  | 0 | 106 | 106 | 2027-02-04 | Scoping | Direct Connection | NGET | Wind Onshore | a0l4L0000005iXXQAY | PRO-001586 | IRON4 | 106 | IRON41
Buchan 01 Offshore Wind Farm | BUCHAN OFFSHORE WIND LIMITED | Buchan 01 275/66kV Substation |  | 0 | 932 | 932 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l4L0000005izLQAQ | PRO-001528 | BUCH4 | 0
Buckland Marsh Solar Park | Arise Renewable Energy UK Limited | Botley West 400kV Substation |  | 0 | 280 | 280 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000ewwxAAA | PRO-003695 | COWL4 | 0 | COWL41
Builth Wells | ABEREDW ENERGY PARK LIMITED | Pont Abraham GSP |  | 0 | 133 | 133 | 2026-10-31 | Scoping | Direct Connection | NGET | Wind Onshore | a0l4L0000005iUHQAY | PRO-001564 | POAB4 | 133 | POAB41
Bulls Lodge Farm | 548 UK INVESTMENT HOLDINGS LIMITED | Braintree 400kV Substation |  | 0 | 200 | 200 | 2033-04-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wYOAAY | PRO-002676 | BULL4 | 0 | BULL41
Bulls Lodge Farm 2 | 548 UK INVESTMENT HOLDINGS LIMITED | Braintree 400kV Substation |  | 0 | 700 | 700 | 2033-03-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wdkAAA | PRO-002737 | BULL4 | 0 | BULL41
Buntington GEC (Ethos Green) | BUNTINGTON GREEN ENERGY CENTRE LTD | Cottered 400kV Substation |  | 0 | 850 | 850 | 2032-07-01 | Awaiting Consents | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l8e0000010wOnAAI | PRO-002576 | PELH4 | 0 | PELH41
Burbo Bank Extension Offshore Wind Farm | BURBO EXTENSION LTD | BURBO BANK EXTENSION OFFSHORE Substation |  | 258 | 0 | 258 |  | Built | Direct Connection | NGET | Wind Offshore | a0l4L0000005ilRQAQ | PRO-000394 | BODE4 | 258 | BODE41
Burwell (Tertiary) | PIVOTED POWER LLP | Burwell Main 400kV Substation |  | 0 | 57 | 57 | 2029-06-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005ixmQAA | PRO-001109 | BURW4 | 57 | BURW41
Burwell BESS | O&G Solar (SPV 38) Limited | Burwell Main 400kV Substation |  | 0 | 249.9 | 249.9 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f4n5AAA | PRO-003869 | BURW4 | 0 | BURW41
Burwell GEC (Ethos Green) | BURWELL GREEN ENERGY CENTRE LTD | Burwell 400kV Substation |  | 0 | 480 | 480 | 2032-10-31 | Scoping | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l8e000000f5cWAAQ | PRO-003937 | BURW4 | 0 | BURW41
Bushbury | Bushbury 10 Renewables Limited | Staffordshire Connection Node A 400kV Substation |  | 0 | 1000 | 1000 | 2037-10-30 | Scoping | Direct Connection | NGET | Demand;PV Array (Photo Voltaic/solar) | a0l8e000000TPQvAAO | PRO-003409 | BUSH2 | 0 | BUSH21
Bushbury Green Energy Centre | INNOVA RENEWABLES LIMITED | Bushbury GSP |  | 0 | 480 | 480 | 2028-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iRTQAY | PRO-001907 | BUSH2 | 480 | BUSH21
Bustleholme | PIVOTED POWER LLP | Bustleholm GSP |  | 57 | 0 | 57 |  | Built | Direct Connection | NGET | Energy Storage System | a0l4L0000005iZiQAI | PRO-001039 | BUST2 | 57 | BUST21
Bute Hydrogen Project 1 | Bute Hydrogen Project 1 Limited | Keadby GSP |  | 0 | 4800 | 4800 | 2035-10-31 | Scoping | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l8e000001HpdKAAS | PRO-004124 | KEAD4 | 0 | KEAD41
Bute Hydrogen Project 2 | Bute Hydrogen Project 2 Limited | Creyke Beck 400kV Substation |  | 0 | 3600 | 3600 | 2035-10-31 | Scoping | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine);Demand;Energy Storage System | a0l8e000001HpdPAAS | PRO-004125 | CREB4 | 0 | CREB41
Bute Hydrogen Project 3 | BUTE HYDROGEN PROJECT 3 LIMITED | Grimsby West 400kV Substation |  | 0 | 3600 | 3600 | 2035-10-31 | Scoping | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine);Demand;Energy Storage System | a0l8e000001HpdUAAS | PRO-004126 | GRIW4 | 0 | GRIW41
Bute Hydrogen Project 4 | BUTE HYDROGEN PROJECT 4 LIMITED | Norton 400kV Substation |  | 0 | 2400 | 2400 | 2035-10-31 | Scoping | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine);Demand;Energy Storage System | a0l8e000001HpdZAAS | PRO-004127 | NORT4 | 0 | NORT41
Bute Hydrogen Project 5 | BUTE HYDROGEN PROJECT 5 LIMITED | Lackenby 400kV Substation |  | 0 | 3600 | 3600 | 2035-10-31 | Scoping | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine);Demand;Energy Storage System | a0l8e000001HpdeAAC | PRO-004128 | LACK4 | 0 | LACK41
Bute Hydrogen Project 6 | Bute Hydrogen Project 6 Limited | Connah's Quay 400kV Substation |  | 0 | 3600 | 3600 | 2037-10-31 | Scoping | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l8e000001HpdjAAC | PRO-004129 | CONQ4 | 0 | CONQ41
Bute Hydrogen Project 7.1 | Bute Hydrogen Project 7 Limited | Solent Connection Node C 400kV |  | 0 | 2400 | 2400 | 2038-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000012jKlAAI | PRO-004666 |  | 0
Butlers Energy Project | IG RENEWABLES SPV 1 LTD | Butlers Wood 400kV Substation |  | 0 | 480 | 480 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f64WAAQ | PRO-003946 | TWIN4A | 0 | TWIN4A
Butlers Wood Green Energy Centre | INNOVA RENEWABLES LIMITED | Butlers Wood 400kV Substation |  | 0 | 1025 | 1025 | 2031-10-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ixpQAA | PRO-002416 | TWIN4B | 0 | TWIN4B
Butlers Wood PV & BESS Station | IB VOGT UK LTD | South Anglia Connection Node B 400kV Substation |  | 0 | 240 | 240 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012grtAAA | PRO-004467 |  | 0
CDCL | UNIPER UK LIMITED | Cottam 400kV Substation |  | 445 | 0 | 445 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005inBQAQ | PRO-000093 | COTT4 | 445 | COTT41
CENOS | FLOTATION ENERGY LIMITED | Lackenby GSP |  | 0 | 1500 | 1500 | 2033-10-30 | Scoping | Direct Connection | NGET | Demand;Wind Offshore | a0l4L0000005iPEQAY | PRO-001847 | LACK4 | 0 | LACK41
CODDINGTON BESS | SHAW-ENERGI LTD | Coddington 400kV Substation |  | 0 | 300 | 300 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000ewXhAAI | PRO-003666 | EASO4 | 0 | EASO41
CREYKE BECK | CLEAN AIR RENEWABLES LIMITED | Creyke Beck 400kV Substation |  | 0 | 500 | 500 | 2033-05-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iZ2QAI | PRO-001972 | CREB4 | 0 | CREB41
Caegarw Farm | Downing Renewable Developments LLP | Pyle 275kV Substation |  | 0 | 350 | 350 | 2037-05-10 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wRwAAI | PRO-002605 | PYLE2 | 0 | PYLE21
Caithness Energy Storage | BAYWA R.E. UK LIMITED | Spittal 400kV |  | 0 | 456 | 456 | 2034-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0lJ9000000blibIAA | PRO-004933 |  | 0
Calderdale Wind Farm 312MW | CALDERDALE WIND FARM LTD | Calderdale Wind Farm 275kV Substation |  | 0 | 312 | 312 | 2035-10-30 | Scoping | Direct Connection | NGET | Wind Onshore | a0l8e0000012kcnAAA | PRO-004714 | ROCH2 | 0 | ROCH21
Caldwell Road | TAGENERGY DEVELOPMENT UK LIMITED | Drakelow 400kV Substation |  | 0 | 249 | 249 | 2028-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000010wbKAAQ | PRO-002710 | DRAK4 | 249 | DRAK41
Callisterhall Wind Farm | E Power Limited | Callisterhall 132kV |  | 0 | 45.5 | 45.5 | 2029-04-27 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005iYxQAI | PRO-001965 | GRNA1 | 45.5 | GRNA1-
Calon y Gwynt | Wind 2 Project 3 Limited | Mid Wales Connection Node A |  | 0 | 72 | 72 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0lJ9000000bla3IAA | PRO-004896 |  | 0
Camp Farm | CHINT SOLAR UK MANAGEMENT LTD | Coventry 275kV Substation |  | 0 | 249.9 | 249.9 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0lJ900000000XVIAY | PRO-004990 | COVE2 | 0 | COVE21
Canterbury North | Canterbury North 10 Renewables Limited | East Kent Connection Node B 400kV Substation |  | 0 | 1000 | 1000 | 2030-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000TPRFAA4 | PRO-003414 | CANT4 | 1000 | CANT41
Canterbury Tertiary | ENSO GREEN HOLDINGS LIMITED | Canterbury 400kV Substation | 1 | 0 | 49.9 | 49.9 | 2025-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iaTQAQ | PRO-001029-1 | CANT4 | 49.9 | CANT41
Canterbury Tertiary | ENSO GREEN HOLDINGS LIMITED | Canterbury 400kV Substation | 2 | 0 | 7.1 | 57 | 2026-09-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iaTQAQ | PRO-001029-2 | CANT4 | 7.1 | CANT41
Caorach | Invenergy Development UK Ltd | Caorach 132 KV Substation |  | 0 | 81 | 81 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0lJ9000000PDqZIAW | PRO-005026 |  | 0
Capenhurst | ENSO GREEN HOLDINGS LIMITED | Capenhurst 275kV Substation |  | 0 | 400 | 400 | 2033-09-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ioiQAA | PRO-000540 | CAPE2 | 0 | CAPE21
Capenhurst 275KV Substation | ZENOBE CAPENHURST LIMITED | Capenhurst 275kV Substation |  | 100 | 0 | 100 |  | Built | Direct Connection | NGET | Energy Storage System | a0l4L0000005iwGQAQ | PRO-001349 | CAPE2 | 100 | CAPE21
Capenhurst GSP | SP MANWEB PLC | Capenhurst GSP |  | 0 | 199.6 | 199.6 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000010wu7AAA | PRO-002949 | CAPE4 | 0 | CAPE4A
Capenhurst Tertiary | ENSO GREEN HOLDINGS LIMITED | Capenhurst 400kV Substation | 1 | 0 | 49.9 | 49.9 | 2025-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ikTQAQ | PRO-002162-1 | CAPE4 | 49.9 | CAPE4A
Capenhurst Tertiary | ENSO GREEN HOLDINGS LIMITED | Capenhurst 400kV Substation | 2 | 0 | 7.1 | 57 | 2027-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ikTQAQ | PRO-002162-2 | CAPE4 | 7.1 | CAPE4A
Capenhurst Tertiary Connection | HD888CAP LIMITED | Capenhurst 275kV Substation |  | 0 | 57 | 57 | 2023-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005iaUQAQ | PRO-001028 | CAPE2 | 57 | CAPE21
Car Duibh Wind Farm | CAR DUIBH WIND FARM LIMITED | Car Duibh 275kV Substation |  | 0 | 99 | 99 | 2034-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005iMQQAY | PRO-002342 | ANSN2 | 0 | ANSN2-
Carberry BESS (was Smeaton BESS) | HARMONY CBR LTD | Dalkeith 400kV Substation |  | 0 | 200 | 200 | 2031-06-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000010xIgAAI | PRO-003053 | SMEA4 | 0 | SMEA4Q
Carbon Free 2030 | CARBON FREE 2030 ENERGY LIMITED | Grimsby West 400kV Substation |  | 0 | 500 | 500 | 2034-06-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010x1NAAQ | PRO-003047 | GRIW4 | 0 | GRIW41
Carn Fearna Wind Farm | STATKRAFT UK LTD | Carn Fearna Wind Farm 132/33kV Substation |  | 0 | 85 | 85 | 2030-06-30 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005ivTQAQ | PRO-002231 | CORI3 | 85 | CORI3-
Carraig Gheal Wind Farm | GREENPOWER (CARRAIG GHEAL) LIMITED | Carraig Gheal 132/33kV Substation |  | 46 | 0 | 46 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005inAQAQ | PRO-000091 | FERO3 | 46 | FERO3-
Carrick Wind Farm | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Carrick Wind Farm Substation |  | 0 | 84 | 84 | 2030-04-01 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005iaWQAQ | PRO-001026 | MAHI | 84 | MAHI3U
Carrington | Carrington Storage Limited | Carrington 400KV Substation | 1 | 0 | 1040 | 1040 | 2025-10-30 | Consents Approved | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005iziQAA | PRO-000276-1 | CARR41 | 1040 | CARR41
Carrington | Carrington Storage Limited | Carrington 400KV Substation | 2 | 0 | 1040 | 2080 | 2036-10-30 | Scoping | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005iziQAA | PRO-000276-2 | CARR41 | 0 | CARR41
Carrington | PIVOTED POWER LLP | Carrington 275kV Substation |  | 0 | 57 | 57 | 2028-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005iaXQAQ | PRO-001025 | CARR2 | 57 | CARR21
Carrington Lane BESS | Apatura Battery Ltd | Daines 400kV Substation |  | 0 | 1800 | 1800 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TPEeAAO | PRO-003215 | DAIN4 | 0 | DAIN41
Carrington Power Station | CARRINGTON POWER LIMITED | Carrington GSP (SP Manweb) |  | 910 | 0 | 910 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005ivuQAA | PRO-000092 | CARR41 | 910 | CARR41
Castlemilk 1 | Queequeg Renewables Ltd | Castlemilk 400kV Substation |  | 0 | 300 | 300 | 2036-10-31 | Scoping | Direct Connection | SPT | PV Array (Photo Voltaic/solar) | a0l8e000000f5XxAAI | PRO-003932 |  | 0
Ceislein Wind Farm | RWE RENEWABLES UK ONSHORE WIND LIMITED | Ceislien Wind Farm |  | 0 | 85.8 | 85.8 | 2031-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l8e000000TPK3AAO | PRO-003256 | SHIN | 0 | SHIN5-
Cellarhead | ENSO GREEN HOLDINGS LIMITED | Cellarhead 400kV Substation |  | 0 | 400 | 400 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ikWQAQ | PRO-002161 | CELL4 | 0 | CELL41
Cellarhead 400kV Energy Storage | C & S ENERGY LIMITED | Cellarhead 400kV Substation |  | 0 | 300 | 300 | 2026-06-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005iemQAA | PRO-001685 | CELL4 | 300 | CELL41
Cellarhead Green Energy Centre | CELLARHEAD GREEN NG LIMITED | Cellarhead 400kV Substation |  | 0 | 400 | 400 | 2028-10-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ihjQAA | PRO-001758 | CELL4 | 400 | CELL41
Cellarhead PV & BESS Station | IB VOGT UK LTD | Manchester South Connection Node B 400kV Substation |  | 0 | 400 | 400 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000TPHxAAO | PRO-003240 |  | 0
Celtic 2 Offshore Wind Farm | RWE RENEWABLES UK LIMITED | Alverdiscott 400kV Substation |  | 0 | 1000 | 1000 | 2031-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005ia5QAA | PRO-002007 | ALVE4A | 0 | ALVE4A
Celtic Offshore Wind Farm | RWE RENEWABLES UK LIMITED | Alverdiscott 400kV Substation |  | 0 | 400 | 400 | 2031-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005ihkQAA | PRO-001760 | ALVE4A | 0 | ALVE4A
Celtic Sea Offshore Wind Farm (ESB) | ESB ASSET DEVELOPMENT UK LIMITED | Alverdiscott 400kV Substation |  | 0 | 1000 | 1000 | 2031-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005iurQAA | PRO-002219 | ALVE4A | 0 | ALVE4A
Cerulean Winds INTOG 1 | CERULEAN WINDS LIMITED | Peterhead 400kV Substation |  | 0 | 600 | 600 | 2033-10-31 | Awaiting Consents | Direct Connection | SHET | Demand;Wind Offshore | a0l8e000001I31aAAC | PRO-004330 | PEHE4 | 0 | PEHE4J
Chalmerston Windfarm | BROCKWELL ENERGY LIMITED | New Cumnock 275/132kV Substation |  | 0 | 75 | 75 | 2033-10-31 | Scoping | Direct Connection | SPT | Wind Onshore | a0l8e000001Ho2yAAC | PRO-004057 | NECU1 | 0 | NECU1-
Chapel Rush Solar | RWE RENEWABLES UK SOLAR AND STORAGE LIMITED | Thornton 400kV Substation |  | 0 | 600 | 600 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012hpXAAQ | PRO-004538 | THTO41 | 0 | THTO41
Chapelcross Solar PV and Storage | EEB68 LIMITED | Chapelcross 132/33kV |  | 0 | 150.88 | 150.88 | 2027-10-29 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ib6QAA | PRO-002031 | CHAP3 | 150.88 | CHAP3-
Chesterfield | SSE RENEWABLES SOLAR & BATTERY HOLDINGS LIMITED | Chesterfield 400kV Substation (Not yet constructed) |  | 0 | 600 | 600 | 2032-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f4iJAAQ | PRO-003861 | CHTE4 | 0 | CHTE41
Chesters | Queequeg Renewables Ltd | Teviot 400/132kV Substation |  | 0 | 80 | 80 | 2033-10-29 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0lJ9000000blKlIAI | PRO-004805 | TEVI1 | 0
Chickerell | ENSO GREEN HOLDINGS LIMITED | Chickerell 400kV Substation | 3 | 0 | 100 | 400 | 2038-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ikqQAA | PRO-002186-3 | CHIC41 | 0 | CHIC41
Chickerell | ENSO GREEN HOLDINGS LIMITED | Chickerell 400kV Substation | 1 | 0 | 200 | 200 | 2036-12-06 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ikqQAA | PRO-002186-1 | CHIC4A | 0 | CHIC4A
Chickerell | ENSO GREEN HOLDINGS LIMITED | Chickerell 400kV Substation | 2 | 0 | 100 | 300 | 2037-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ikqQAA | PRO-002186-2 | CHIC41 | 0 | CHIC41
Chickerell Solar PV & BESS | CHICKERELL SOLAR LIMITED | Chickerell 400kV Substation |  | 0 | 400 | 400 | 2027-10-01 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iw2QAA | PRO-001598 | CHIC41 | 400 | CHIC41
Chirmorie Wind Farm | CHIRMORIE WIND FARM LIMITED | Chirmorie 132/33kV Substation |  | 0 | 80 | 80 | 2026-04-30 | Consents Approved | Direct Connection | SPT | Wind Onshore | a0l4L0000005inCQAQ | PRO-000094 | CHMO1 | 80 | CHMO1-
Chleansaid Wind Farm | ESB ASSET DEVELOPMENT UK LIMITED | Chleansaid Wind Farm 132kV Substation |  | 0 | 96 | 96 | 2027-07-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005iY6QAI | PRO-001608 | CHLS1 | 96 | CHLS1-
Cilfynydd | ENSO GREEN HOLDINGS LIMITED | Cilfynydd 400kV Substation |  | 0 | 400 | 400 | 2030-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l4L0000005idlQAA | PRO-002088 | CILF4 | 400 | CILF41
Cilfynydd 2 | REWE 8 LIMITED | Cilfynydd 400kV Substation |  | 0 | 240 | 240 | 2037-10-15 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f6A1AAI | PRO-003962 | CILF4 | 0 | CILF41
Cilfynydd BESS | Cilfynydd BESS Limited | Cilfynydd 400kV Substation |  | 0 | 349.9 | 349.9 | 2037-10-15 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000010wfHAAQ | PRO-002756 | CILF4 | 0 | CILF41
Cilfynydd Green Energy Centre | CILFYNYDD NG LIMITED | Cilfynydd 400kV Substation | 1 | 0 | 400 | 400 | 2028-10-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005idMQAQ | PRO-001663-1 | CILF4 | 400 | CILF41
Cilfynydd Green Energy Centre | CILFYNYDD NG LIMITED | Cilfynydd 400kV Substation | 2 | 0 | 625 | 1025 | 2033-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005idMQAQ | PRO-001663-2 | CILF4 | 0 | CILF41
Cilfynydd Grid Stability Services | CILFYNYDD GRID SERVICES LIMITED | Cilfynydd 400kV Substation |  | 0 | 0 | 0 | 2025-07-31 | Consents Approved | Direct Connection | NGET | Reactive Compensation | a0l4L000002yQWWQA2 | PRO-002540 | CILF4 | 0 | CILF41
Clash Gour | EDF ENERGY RENEWABLES LIMITED | Clash Gour Wind Farm 132kV Substation |  | 0 | 210 | 210 | 2027-10-30 | Awaiting Consents | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l4L0000005iaaQAA | PRO-001022 | CLGO1 | 210 | CLGO1-
Clashindarroch Windfarm Extension | CLASHINDARROCH WINDFARM EXTENSION LIMITED | Clashindarroch Windfarm Extension 132kV Substation |  | 0 | 145.2 | 145.2 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l8e0000012kkvAAA | PRO-004769 | CAIN3 | 0 | CAIN3J
Clauchrie Windfarm | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Clauchrie 132kV Substation |  | 0 | 108 | 108 | 2027-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l4L0000005iabQAA | PRO-001021 | CLAU3 | 108 | CLAU3-
Clean Planet Solar | Clean Planet Solar Farm Limited | Frodsham 400kV Substation |  | 0 | 500 | 500 | 2037-11-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l8e0000011yXgAAI | PRO-003519 | FROD4 | 0 | FROD41
Cleve Hill Solar Park | CLEVE HILL SOLAR PARK LIMITED | Cleve Hill 400kV Substation |  | 350 | 0 | 350 |  | Built | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iwHQAQ | PRO-001097 | CLEH4 | 350 | CLEH41
Cliff Hill Energy Farm | Renewable Energy Systems Limited | Navenby 400kV Substation |  | 0 | 800 | 800 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f4xRAAQ | PRO-003896 | BICF4 | 0 | BICF41
Cliffhope | Invenergy Development UK Ltd | Hawick 132kV Substation |  | 0 | 205 | 205 | 2034-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0lJ9000000POVrIAO | PRO-006052 |  | 0
Cloich Forest Wind Farm | EDF ENERGY RENEWABLES LIMITED | Cloiche 132kV Substation |  | 0 | 67.2 | 67.2 | 2029-07-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005iZoQAI | PRO-001387 | CLOI1 | 67.2 | CLOI1-
Cloiche Wind Farm | SSE Generation Limited | Cloiche 132kV Substation |  | 0 | 200 | 200 | 2027-07-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005ilxQAA | PRO-000425 | CLOI1 | 200 | CLOI1-
Cloud Hill Windfarm | Cloud Hill Windfarm Limited | Glenglass 132/33kV | 2 | 0 | 10 | 60 | 2036-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005iYOQAY | PRO-001938-2 |  | 0
Cloud Hill Windfarm | Cloud Hill Windfarm Limited | Glenglass 132/33kV | 1 | 0 | 50 | 50 | 2030-05-31 | Awaiting Consents | Direct Connection | SPT | Energy Storage System | a0l4L0000005iYOQAY | PRO-001938-1 |  | 50
Cloverhill Farm BESS | Apatura Battery Ltd | Ayr 275/33kV |  | 0 | 200 | 200 | 2030-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000TPRtAAO | PRO-003421 | AYR-2 | 200 | AYR-2Q
Clune Wind Farm | Renewable Energy Systems Limited | Clune 132/33 kV Substation |  | 0 | 187.2 | 187.2 | 2030-04-30 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l8e0000012j2rAAA | PRO-004620 | TOMT1 | 187.2 | TOMT1J
Clunie (part of the Clunie Cascade) | SSE Generation Limited | Clunie GSP |  | 61.2 | 0 | 61.2 |  | Built | Direct Connection | SHET | Hydro | a0l4L0000005imgQAA | PRO-000072 | CLUN | 61.2 | CLUN5J
Clyde North | CLYDE WINDFARM (SCOTLAND) LIMITED | Clyde North 275/33kV |  | 374.5 | 0 | 374.5 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005inDQAQ | PRO-000095 | CLYN2 | 374.5 | CLYN2Q
Clyde South | CLYDE WINDFARM (SCOTLAND) LIMITED | Clyde South 275/33kV |  | 128.8 | 0 | 128.8 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005inEQAQ | PRO-000096 | CLYS3 | 128.8 | CLYS3A
Cnoc Buidhe Wind Farm | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | 1 | 0 | 150 | 150 | 2029-04-30 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l4L0000005idTQAQ | PRO-001672-1 | CRSS2 | 150 | CRSS2A
Cnoc Buidhe Wind Farm | CNOC BUIDHE WIND ENERGY HUB LIMITED | Cnoc Buidhe 132kV/33kV Substation | 2 | 0 | 70 | 220 | 2034-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l4L0000005idTQAQ | PRO-001672-2 | CRSS2 | 0 | CRSS2A
Coachford 400MW BESS | Field Devco Ltd | Blackhillock 2 400/33kV GSP Substation |  | 0 | 400 | 400 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0lJ9000000PDxzIAG | PRO-005097 |  | 0
Cockenzie BESS | COCKENZIE STORAGE B LTD | Cockenzie 400/132kV |  | 0 | 102 | 102 | 2026-07-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001Hrm5AAC | PRO-004217 | COCK4 | 102 | COCK4Q
Coddington | STARLIGHT ENERGY UK LIMITED | Eaton Socon 400kV Substation |  | 0 | 240 | 240 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000ey6vAAA | PRO-003750 | EASO41 | 0 | EASO41
Codham Hall BESS | Pulse Clean Energy Limited | Warley 400kV Substation |  | 0 | 249 | 249 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f6JAAAY | PRO-003972 | WARL2 | 0 | WARL21
Coire Glas Pumped Storage | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | 1 | 0 | 612 | 612 | 2029-10-31 | Consents Approved | Direct Connection | SHET | Pump Storage | a0l4L0000005imhQAA | PRO-000073-1 | COGL | 612 | COGL4J
Coire Glas Pumped Storage | COIRE GLAS HYDRO PUMPED STORAGE LIMITED | Coire Glas GSP | 2 | 0 | 684 | 1296 | 2029-10-31 | Scoping | Direct Connection | SHET | Pump Storage | a0l4L0000005imhQAA | PRO-000073-2 | COGL | 684 | COGL4J
Cold Norton | BSR APPLICATIONS LIMITED | South Anglia Connection Node C 400kV Substation |  | 0 | 1250 | 1250 | 2036-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e0000011yYUAAY | PRO-003528 |  | 0
Coldstream BESS | IGP ENERGY STORAGE 4 LIMITED | Eccles 400/132kV |  | 0 | 50 | 50 | 2030-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000011zGTAAY | PRO-003572 | ECCL1 | 50 | ECCL1-
Colmealie Wind - Solar - BESS Farm | Galileo 21 Limited | Fetteresso 132kV substation |  | 0 | 112 | 112 | 2037-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0lJ9000000POtpIAG | PRO-006136 |  | 0
Conexus North BESS Facility | Pulse Clean Energy Limited | Coalburn 400kV Substation |  | 0 | 200 | 200 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000011xUTAAY | PRO-003460 | COAL4 | 0 | COAL4-
Connah's Quay | UNIPER UK LIMITED | Connah's Quay 400kV Substation |  | 1380 | 0 | 1380 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005imCQAQ | PRO-000058 | CONQ4 | 1380 | CONQ41
Copper Nose BESS | Copper Nose Energy Ltd | Fawley 132kV Substation |  | 0 | 150 | 150 | 2036-10-24 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iyCQAQ | PRO-002356 | FAWL1 | 0 | FAWL11
Cormoran Offshore Wind Farm | South West Wind Holdco Limited | Alverdiscott 400kV Substation |  | 0 | 1008 | 1008 | 2036-12-06 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005iyQQAQ | PRO-002390 | ALVE4A | 0 | ALVE4A
Cornharrow Wind Farm | ENERGYFARM UK CORNHARROW LLP | Quantans Hill 132kV |  | 0 | 50 | 50 | 2027-10-31 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005if2QAA | PRO-001741 | QUAN1 | 50 | QUAN1-
Cornwall Energy Park | GREEN ENERGY MAB LTD | Tideford 400kV Substation |  | 0 | 500 | 500 | 2036-12-06 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iyVQAQ | PRO-002379 | LAND4 | 0 | LAND41
Corriegarth | CORRIEGARTH WIND ENERGY LIMITED | Corriegarth 132/33kV substation |  | 69 | 0 | 69 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005inHQAQ | PRO-000101 | COGA3 | 69 | COGA3-
Corriegarth 2 Wind Farm | CORRIEGARTH 2 WIND FARM LIMITED | Corriegarth 132/33kV substation |  | 0 | 70 | 70 | 2027-07-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005imGQAQ | PRO-000420 | COGA3 | 70 | COGA3-
Corriemoillie BESS | FIELD CORRIEMOILLIE LTD | Corriemoillie 132kV Substation |  | 0 | 200 | 200 | 2029-09-30 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e000000f6u6AAA | PRO-003992 | CORI3 | 200 | CORI3-
Corriemoillie Wind Farm | ROWAN ONSHORE WINDFARMS LIMITED | Corriemoillie 132/33kV Substation |  | 47.5 | 0 | 47.5 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005inIQAQ | PRO-000102 | CORI3 | 47.5 | CORI3-
Coryton | CORYTON ENERGY COMPANY LTD | Coryton South 400kV Substation |  | 800 | 0 | 800 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005inJQAQ | PRO-000103 | COSO4 | 800 | COSO41
Coryton | Coryton 10 Renewables Limited | Coryton South 400kV Substation |  | 0 | 1000 | 1000 | 2034-10-31 | Scoping | Direct Connection | NGET | Demand;PV Array (Photo Voltaic/solar) | a0l8e000000TPQlAAO | PRO-003407 | COSO4 | 0 | COSO41
Cottam | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 1 | 0 | 250 | 250 | 2029-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ielQAA | PRO-001502-1 | COTT4 | 250 | COTT41
Cottam | GATE BURTON ENERGY PARK LIMITED | Cottam 400kV Substation | 2 | 0 | 250 | 500 | 2030-07-30 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ielQAA | PRO-001502-2 | COTT4 | 250 | COTT41
Cottam PV & BESS Sub | O&G Solar (SPV 44) Limited | Cottam 400kV Substation |  | 0 | 500 | 500 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L000002yQWpQAM | PRO-002543 | COTT4 | 0 | COTT41
Cottam Solar PV + BESS | COTTAM SOLAR PROJECT LIMITED | Cottam 400kV Substation |  | 0 | 600 | 600 | 2029-09-01 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iz0QAA | PRO-001401 | COTT4 | 600 | COTT41
Cottam-Ryhall Solar & BESS | TYLER HILL RENEWABLES LIMITED | Trent Valley South Connection Node B 400kV Substation. |  | 0 | 400 | 400 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001HozEAAS | PRO-004100 |  | 0
Cottered | SSE UTILITY SOLUTIONS LIMITED | Cottered 400kV Substation |  | 0 | 600 | 600 | 2030-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ivhQAA | PRO-002173 | PELH4 | 600 | PELH41
Cottered - PVDP | SolarNine Ltd | West Anglia Connection Node D 400kV Substation |  | 0 | 520 | 520 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f7BjAAI | PRO-003999 |  | 0
Cour Wind Farm | COUR WIND FARM (SCOTLAND ) LIMITED | Crossaig 132kV Substation |  | 20.5 | 0 | 20.5 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005infQAA | PRO-000106 | CRSS1 | 20.5 | CRSS1J
Coventry | PIVOTED POWER LLP | Coventry 275kV Substation |  | 49.9 | 0 | 49.9 |  | Built | Direct Connection | NGET | Energy Storage System | a0l4L0000005iadQAA | PRO-001005 | COVE2 | 49.9 | COVE21
Cowley | PIVOTED POWER LLP | Cowley 400kV Substation |  | 49.9 | 0 | 49.9 |  | Built | Direct Connection | NGET | Energy Storage System | a0l4L0000005ibMQAQ | PRO-001015 | COWL4 | 49.9 | COWL41
Cowley (Tertiary) | COWLEY BALDON GREEN LIMITED | Cowley 400kV Substation |  | 0 | 57 | 57 | 2025-07-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ixTQAQ | PRO-000407 | COWL4 | 57 | COWL41
Cowley Energy Storage | BW ESS DEVELOPMENT UK LIMITED | Cowley 400kV Substation |  | 0 | 200 | 200 | 2028-10-25 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ic8QAA | PRO-002066 | COWL4 | 200 | COWL41
Cowley Farm | COWLEY 2 RENEWABLES LTD | Cowley 400kV Substation |  | 0 | 200 | 200 | 2038-10-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wYTAAY | PRO-002677 | COWL4 | 0 | COWL41
Cowley Farm 2 | COWLEY 7 RENEWABLES LTD | Cowley 400kV Substation |  | 0 | 700 | 700 | 2038-11-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wdpAAA | PRO-002738 | COWL4 | 0 | COWL41
Coylton 275kV Greener Grid Park | COYLTON ENERGY LIMITED | Coylton 275/33kV Substation |  | 0 | 150 | 150 | 2025-05-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005ihQQAQ | PRO-001551 | COYL3 | 150 | COYL3-
Coylton Farm | NEW ENERGY PARTNERSHIP LIMITED | Coylton 275/33kV Substation |  | 0 | 300 | 300 | 2037-10-30 | Awaiting Consents | Direct Connection | SPT | Energy Storage System | a0l8e000001HwvEAAS | PRO-004230 | COYL2 | 0 | COYL2-
Craig Moss Farm | QAIR RENEWABLES UK LIMITED | Craig Moss Farm 132kV Substation |  | 0 | 300 | 300 | 2036-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000011y2hAAA | PRO-003498 | DUMF4 | 0 | DUMF3A
Craig Watch Wind Farm | Craig Watch Wind Farm Limited | Craig Watch Substation |  | 0 | 72.6 | 72.6 | 2029-06-30 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005iyhQAA | PRO-001877 | BLHI | 72.6 | BLHI1J
Craighead Wind Farm | GALILEO 02 LIMITED | Westfield 132/33kV |  | 0 | 77 | 77 | 2032-10-29 | Scoping | Direct Connection | SPT | Wind Onshore | a0l8e0000010wlKAAQ | PRO-002821 |  | 0
Craiginmoddie Wind Farm | ENERGYFARM UK CRAIGINMODDIE LLP | Maybole 132/33kV |  | 0 | 92.4 | 92.4 | 2031-09-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l8e000000f41xAAA | PRO-003829 | MAYB3 | 0 | MAYB3-
Craigneuk 250MW BESS | Apatura Battery Ltd | Newarthill Energy Park 275kV Substation |  | 0 | 250 | 250 | 2028-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000011zPXAAY | PRO-003579 | NEAR2 | 250 | NEAR2Q
Cranwell Solar & BESS Farm | TRIO POWER LIMITED | Navenby 400kV Substation |  | 0 | 300 | 300 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0lJ9000000blnVIAQ | PRO-004952 | BICF4 | 0 | BICF41
Crathorne Estate BESS and Solar Farm | Exagen Development Limited | Lackenby 400kV Substation |  | 0 | 600 | 600 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f427AAA | PRO-003831 | LACK4 | 0 | LACK41
Creachan Wind Farm | RWE RENEWABLES UK ONSHORE WIND LIMITED | Creachan Wind Farm 132/33kV Substation |  | 0 | 79.2 | 79.2 | 2030-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l8e000000f4yFAAQ | PRO-003906 | DALL2 | 79.2 | DALL2-
Creag Dhubh Windfarm | Invenergy Development UK Ltd | Creag Dhubh Wind Farm and BESS 132kV Substation |  | 0 | 171 | 171 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0lJ9000000PDmkIAG | PRO-005014 |  | 0
Creag Riabhach Wind Farm | CREAG RIABHACH WIND FARM LTD | Creag Riabhach 132/33kV Substation | 2 | 0 | 12.6 | 105 | 2027-07-31 | Consents Approved | Direct Connection | SHET | Wind Onshore | a0l4L0000005ingQAA | PRO-000109-2 | CREA3 | 12.6 | CREA3-
Creag Riabhach Wind Farm | CREAG RIABHACH WIND FARM LTD | Creag Riabhach 132/33kV Substation | 1 | 92.4 | 0 | 92.4 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005ingQAA | PRO-000109-1 | CREA3 | 92.4 | CREA3-
Creyke Beck Battery 2 | CBB SPV LIMITED | Creyke Beck 400kV Substation |  | 0 | 28.5 | 28.5 | 2028-06-30 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l8e000001Ho7SAAS | PRO-004060 | CREB4 | 28.5 | CREB41
Creyke Beck PV & BESS Sub | BEFERLEAH ENERGY PARK LIMITED | Creyke Beck 400kV Substation |  | 0 | 249.9 | 249.9 | 2035-05-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wY4AAI | PRO-002672 | CREB4 | 0 | CREB41
Crossdykes | CROSSDYKES WF LIMITED | Crossdykes 33kV |  | 46 | 0 | 46 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005injQAA | PRO-000112 | CRDY3 | 46 | CRDY3A
Crossgatehall BESS | DE 001 LIMITED | Smeaton 400/275kV |  | 0 | 300 | 300 | 2033-10-28 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000012jKvAAI | PRO-004668 |  | 0
Cruach Bhreac Wind Farm | STATKRAFT UK LTD | Craig Murrail GSP |  | 0 | 100.8 | 100.8 | 2034-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l8e000000f4w9AAA | PRO-003879 | CRMU | 0 | CRMU3-
Cruachan | DRAX PUMPED STORAGE LIMITED | Cruachan 275kV Substation | 1 | 440 | 0 | 440 |  | Built | Direct Connection | SPT | Pump Storage | a0l4L0000005inkQAA | PRO-000113-1 | CRUA2 | 440 | CRUA2Q
Cruachan | DRAX PUMPED STORAGE LIMITED | Cruachan 275kV Substation | 2 | 0 | 40 | 480 | 2027-06-01 | Scoping | Direct Connection | SPT | Pump Storage | a0l4L0000005inkQAA | PRO-000113-2 | CRUA2 | 40 | CRUA2Q
Cruachan Expansion | Drax Cruachan Expansion Limited | Cruachan 275kV Substation |  | 0 | 600 | 600 | 2030-10-31 | Scoping | Direct Connection | SPT | Pump Storage | a0l4L0000005iQWQAY | PRO-001889 | CRUA2 | 600 | CRUA2Q
Cryogenic Battery System (Synchronous) | CRYOBATTERY ONE LIMITED | Carrington 400KV Substation |  | 0 | 49.9 | 49.9 | 2024-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System;Reactive Compensation | a0l4L0000005iprQAA | PRO-000549 | CARR41 | 49.9 | CARR41
Crystal Rig II Wind Farm | CRYSTAL RIG II LIMITED | Crystal Rig 132/33kV |  | 138 | 0 | 138 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005imMQAQ | PRO-000414 | CRYR3 | 138 | CRYR31
Crystal Rig III Wind Farm | CRYSTAL RIG III LIMITED | Crystal Rig 132/33kV |  | 13.8 | 0 | 13.8 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005ifVQAQ | PRO-001127 | CRYR3 | 13.8 | CRYR31
Crystal Rig IV Wind Farm | CRYSTAL RIG IV LIMITED | Crystal Rig 132/33kV |  | 0 | 48.2 | 48.2 | 2024-06-30 | Under Construction/Commissioning | Direct Connection | SPT | Wind Onshore | a0l4L0000005ipMQAQ | PRO-000520 | CRYR3 | 48.2 | CRYR31
Culham Storage | CULHAM STORAGE LIMITED | Culham Jet 400kV Substation |  | 0 | 500 | 500 | 2027-10-29 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iwLQAQ | PRO-001946 | CULJ4 | 500 | CULJ4A
Culligran (part of the Beauly Cascade) | SSE Generation Limited | Culligran GSP |  | 19.1 | 0 | 19.1 |  | Built | Direct Connection | SHET | Hydro | a0l4L0000005imiQAA | PRO-000074 | CULL | 19.1 | CULL5-
Cumberhead | CUMBERHEAD WIND ENERGY LIMITED | Cumberhead 33kV |  | 50 | 0 | 50 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005inlQAA | PRO-000114 | CUMH3 | 50 | CUMH3-
Cumberhead West Wind Farm | CUMBERHEAD WEST WIND FARM LTD. | Cumberhead 33kV |  | 0 | 114 | 114 | 2025-07-31 | Awaiting Consents | Direct Connection | SPT | Wind Onshore | a0l4L0000005ix7QAA | PRO-000423 | CUMW3 | 114 | CUMW3-
DRAGON GREEN BESS | SHAW-ENERGI LTD | Bolney 400kV Substation |  | 0 | 300 | 300 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TPHiAAO | PRO-003237 | BOLN4 | 0 | BOLN41
Daer Wind Farm | RWE RENEWABLES UK ONSHORE WIND LIMITED | Daer Windfarm 132/33kV |  | 0 | 96 | 96 | 2027-07-14 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005iqVQAQ | PRO-000565 | DAER3 | 96 | DAER3-
Daines BESS | DAINES ENERGY PARK LIMITED | Daines 400kV Substation |  | 0 | 249.9 | 249.9 | 2037-11-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000010wSkAAI | PRO-002614 | DAIN4 | 0 | DAIN41
Daines BESS | SSE DAINES BESS LIMITED | Daines 400kV Substation |  | 0 | 600 | 600 | 2028-10-27 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ibyQAA | PRO-002050 | DAIN4 | 600 | DAIN41
Daines Green Energy Centre | INNOVA RENEWABLES LIMITED | Daines 400kV Substation |  | 0 | 480 | 480 | 2028-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iRPQAY | PRO-001902 | DAIN4 | 480 | DAIN41
Daines NP BESS | NORIKER POWER LTD | Manchester South connection node A 400kv |  | 0 | 500 | 500 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TPCdAAO | PRO-003194 |  | 0
Dalchork Farm | QAIR RENEWABLES UK LIMITED | Dalchork 132kV Substation |  | 0 | 200 | 200 | 2032-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000010wk2AAA | PRO-002807 | DLCH1 | 0 | DLCH1A
Dalmarnock Storage BESS | VIRIDISIA LTD | Dalmarnock 132/33kV |  | 0 | 42 | 42 | 2030-04-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000exgsAAA | PRO-003737 | DALM3 | 42 | DALM3-
Dalquhandy Wind Farm | DALQUHANDY WIND FARM LIMITED | Cumberhead Collector 132/33kV |  | 42 | 0 | 42 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005inmQAA | PRO-000117 | CCSS3 | 42 | CCSS3-
Damhead Creek | VPI POWER LIMITED | Kingsnorth GSP |  | 812 | 0 | 812 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005innQAA | PRO-000119 | DAMC4 | 812 | DAMC41
Damhead Creek 2 | VPI POWER LIMITED | Kingsnorth 400kV Substation |  | 0 | 1800 | 1800 | 2025-08-31 | Consents Approved | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine);Energy Storage System;OCGT (Open Cycle Gas Turbine) | a0l4L0000005ieKQAQ | PRO-001056 | KINO4 | 1800 | KINO41
Daventry High Impact Green Energy Hub (HIGEH) 1 | TELIS ENERGY UK LIMITED | New Patford Bridge 400kV Substation |  | 0 | 1000 | 1000 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;Nuclear;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e000000ewvzAAA | PRO-003686 | PAFB4 | 0 | PAFB4A
Daviot Windfarm | CUBICO UK DEVELOPMENT LIMITED | Daviot 132/33kV Substation |  | 0 | 45 | 45 | 2031-03-31 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l8e000001HoGbAAK | PRO-004069 |  | 0
Dealanach WLC WF | DEALANACH LIMITED | Hopsrig Collector 132/33kV Substation |  | 0 | 12 | 12 | 2026-12-15 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005igLQAQ | PRO-001722 | HORI3 | 12 | HORI3A
Deanie (part of the Beauly Cascade) | SSE Generation Limited | Deanie GSP |  | 38 | 0 | 38 |  | Built | Direct Connection | SHET | Hydro | a0l4L0000005imjQAA | PRO-000075 | DEAW | 38 | DEAW5-
Deeside Power Station | DEESIDE POWER (UK) LIMITED | Connah's Quay 400kV Substation |  | 1 | 189 | 190 | 2026-10-25 | Consents Approved | Direct Connection | NGET | Energy Storage System;Gas Reciprocating | a0l4L0000005ieEQAQ | PRO-001062 | CONQ4 | 190 | CONQ41
Dell Wind Farm | DELL WIND FARM LIMITED | Dell 132kV Substation |  | 0 | 49.8 | 49.8 | 2030-04-01 | Consents Approved | Direct Connection | SHET | Wind Onshore | a0l4L0000005ibPQAQ | PRO-001012 | DELL1 | 49.8 | DELL1-
Denny BESS | IGP ENERGY STORAGE 3 LIMITED | Denny North |  | 0 | 350 | 350 | 2030-10-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000011zGOAAY | PRO-003571 | DENN | 350 | DENN4-
Dersalloch Wind Farm | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Dersalloch 132/33kV |  | 69 | 11 | 80 | 2027-10-31 | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005imEQAQ | PRO-000060 | DESA3 | 80 | DESA3-
Derwent Solar PV Array | ANESCO LIMITED | Thornton 400kV Substation |  | 0 | 160 | 160 | 2032-05-31 | Scoping | Direct Connection | NGET | PV Array (Photo Voltaic/solar) | a0l4L0000005iOsQAI | PRO-001648 | THTO42 | 0 | THTO42
Deucheran Hill 2 Wind Farm | RWE RENEWABLES UK ONSHORE WIND LIMITED | Deucheran Hill 2 Wind Farm Substation |  | 0 | 165 | 165 | 2034-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l8e000001HrYyAAK | PRO-004208 | CAAD | 0 | CAAD3J
Devol Moor Battery & Solar Project | RELAY HOLDCO LIMITED | Devol Moor 400/132kV |  | 0 | 400 | 400 | 2029-10-17 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000001HoYoAAK | PRO-004084 | DEVM4 | 400 | DEVM4-
Devonhill | CBS ENERGY STORAGE ASSETS UK LIMITED | Strathaven 400/275kV |  | 0 | 500 | 500 | 2033-10-28 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000012gtzAAA | PRO-004492 | STHA4 | 0 | STHA4A
Devonside BESS | CARLTON POWER LIMITED | Devonside 132/33kV |  | 0 | 49.5 | 49.5 | 2028-08-18 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005iaBQAQ | PRO-002015 | DEVO3 | 49.5 | DEVO3-
Didcot B | RWE Generation UK Plc | Didcot 400kV Substation |  | 1475 | 230 | 1705 | 2037-10-31 | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005inoQAA | PRO-000122 | DIDC4 | 1475 | DIDC41
Didcot BESS 1 | Downing Renewable Developments LLP | Didcot 400kV Substation |  | 0 | 750 | 750 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TPcAAAW | PRO-003446 | DIDC4 | 0 | DIDC41
Didcot BESS 2 | Downing Renewable Developments LLP | Didcot GSP |  | 0 | 99.9 | 99.9 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TPcFAAW | PRO-003447 | DIDC4 | 0 | DIDC41
Didcot Battery | DIDCOT BATTERY LIMITED | Didcot 400kV Substation |  | 0 | 100 | 100 | 2025-10-31 | Scoping | Direct Connection | NGET | Demand;Energy Storage System | a0l4L0000005idCQAQ | PRO-001468 | DIDC4 | 100 | DIDC41
Didcot Energy Park | BROCKWELL STORAGE & SOLAR LIMITED | Didcot 400kV Substation |  | 0 | 300 | 300 | 2027-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005ivKQAQ | PRO-002382 | DIDC4 | 300 | DIDC41
Didcot Farm | APPLEFORD 2 RENEWABLES LTD | Appleford 400kV |  | 0 | 200 | 200 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wYxAAI | PRO-002683 | DIDC4 | 0 | DIDC41
Didcot Farm 2 | Appleford 7 Renewables Limited | Didcot 400kV Substation |  | 0 | 700 | 700 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000exN3AAI | PRO-003709 | DIDC4 | 0 | DIDC41
Didcot High Impact Green Energy Hub (HIGEH) 1 | TELIS ENERGY UK LIMITED | Didcot 400kV Substation |  | 0 | 1000 | 1000 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;Nuclear;PV Array (Photo Voltaic/solar);Reactive Compensation;Wind Onshore | a0l8e0000010wVoAAI | PRO-002649 | DIDC4 | 0 | DIDC41
Didcot Road | TBC 001 Limited | Didcot 400kV Substation |  | 0 | 300 | 300 | 2027-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iMPQAY | PRO-002336 | DIDC4 | 300 | DIDC41
Dinorwig | First Hydro Company | Dinorwig 400kV Substation |  | 1644 | 0 | 1644 |  | Built | Direct Connection | NGET | Pump Storage | a0l4L0000005im8QAA | PRO-000054 | DINO4 | 1644 | DINO41
Divot Hill Wind Farm | ENERGYFARM DIVOT HILL LTD | Divot Hill 132/33 kV Substation |  | 0 | 63 | 63 | 2036-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l8e0000012jKWAAY | PRO-004664 |  | 0
Dog Trap Lane | HB411MIN Limited | Minety 400kV Substation |  | 0 | 47.5 | 47.5 | 2028-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005ixxQAA | PRO-001626 | MITY4 | 47.5 | MITY41
Dogger Bank Project 4 (Dogger Bank B) | DOGGERBANK OFFSHORE WIND FARM PROJECT 2 PROJCO LIMITED | Dogger Bank 220kV Offshores |  | 1200 | 0 | 1200 |  | Built | Direct Connection | NGET | Wind Offshore | a0l4L0000005imQQAQ | PRO-000410 | CREB41 | 1200 | CREB41
Dogger Bank Project A | DOGGERBANK OFFSHORE WIND FARM PROJECT 1 PROJCO LIMITED | Dogger Bank 220kV Offshores |  | 1200 | 0 | 1200 |  | Built | Direct Connection | NGET | Wind Offshore | a0l4L0000005imPQAQ | PRO-000411 | CREB42 | 1200 | CREB42
Dogger Bank Project C | DOGGERBANK OFFSHORE WIND FARM PROJECT 3 PROJCO LIMITED | Lackenby GSP |  | 0 | 1200 | 1200 | 2025-04-01 | Consents Approved | Direct Connection | NGET | Wind Offshore | a0l4L0000005imRQAQ | PRO-000409 | LACK4 | 1200 | LACK41
Dogger Bank South East | RWE Renewables UK Dogger Bank South (East) Limited | RWE North Sea Offshore Substation | 1 | 0 | 400 | 400 | 2030-10-30 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005iZFQAY | PRO-001375-1 | CRBB4 | 400
Dogger Bank South East | RWE Renewables UK Dogger Bank South (East) Limited | RWE North Sea Offshore Substation | 2 | 0 | 1050 | 1450 | 2031-11-30 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005iZFQAY | PRO-001375-2 | CRBB4 | 0
Dogger Bank South West | RWE RENEWABLES UK LIMITED | Wylfa 400kV Substation | 1 | 0 | 400 | 400 | 2030-10-30 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005iZnQAI | PRO-001386-1 | WYLF4 | 400 | WYLF41
Dogger Bank South West | RWE RENEWABLES UK LIMITED | Wylfa 400kV Substation | 2 | 0 | 1050 | 1450 | 2031-11-30 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005iZnQAI | PRO-001386-2 | WYLF4 | 0 | WYLF41
Don Cossack | Don Cossack Ltd | Tynemouth 275kV Substation |  | 0 | 70 | 70 | 2034-06-15 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f4neAAA | PRO-003875 | TYNE21 | 0 | TYNE21
Dorenell Battery | DORENELL WINDFARM EXTENSION LIMITED | Dorenell BESS 132KV substation |  | 0 | 37.5 | 37.5 | 2023-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005ilvQAA | PRO-000427 | DORE1 | 37.5 | DORE11
Dorenell Windfarm | DORENELL WINDFARM LIMITED | Dorenell 132/33kV Substation |  | 177 | 0 | 177 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005ipKQAQ | PRO-000522 | DORE1 | 177 | DORE11
Dorenell Windfarm Extension | DORENELL WINDFARM EXTENSION LIMITED | Blackhillock 400kV Substation |  | 0 | 610 | 610 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005iuPQAQ | PRO-002415 | BLHI4 | 0 | BLHI4-
Douglas West | DOUGLAS WEST WIND FARM LTD | Coalburn 400/132kV |  | 45 | 0 | 45 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005inrQAA | PRO-000128 | COAL1 | 45 | COAL1-
Douglas West Extension | DOUGLAS WEST EXTENSION LTD | Douglas West Extension Windfarm |  | 0 | 60 | 60 | 2025-06-30 | Consents Approved | Direct Connection | SPT | Wind Onshore | a0l4L0000005ixIQAQ | PRO-000422 | DWEX | 60 | DWEX3-
Dounreay BESS | FIELD DEVCO LTD | New Dounreay 400kV substation |  | 0 | 200 | 200 | 2034-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000012kjJAAQ | PRO-004749 | DOUN4 | 0 | DOUN3-
Dove Solar | RWE RENEWABLES UK SOLAR AND STORAGE LIMITED | North Anglia Connection Node E 400kV Substation |  | 0 | 500 | 500 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001Hq1lAAC | PRO-004166 |  | 0
Downiebrae BESS | DOWNIEBRAE BESS LTD | Dalmarnock 132/33kV |  | 0 | 150 | 150 | 2028-04-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000TPE0AAO | PRO-003208 | DALM3 | 150 | DALM3-
Drakelow | ENSO GREEN HOLDINGS V LIMITED | Drakelow 132kV Substation |  | 0 | 120 | 120 | 2027-12-01 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iwyQAA | PRO-000428 | DRAK1 | 120 | DRAK11
Drakelow BESS | HARMONY DL LTD | Drakelow 132kV Substation |  | 0 | 200 | 200 | 2028-06-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ib8QAA | PRO-002033 | DRAK1 | 200 | DRAK11
Drakelow Green Energy Centre | DRAKELOW GREEN ENERGY LIMITED | Drakelow 400kV Substation | 1 | 0 | 400 | 400 | 2026-10-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ieqQAA | PRO-001693-1 | DRAK4 | 400 | DRAK41
Drakelow Green Energy Centre | DRAKELOW GREEN ENERGY LIMITED | Drakelow 400kV Substation | 2 | 0 | 625 | 1025 | 2029-10-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ieqQAA | PRO-001693-2 | DRAK4 | 625 | DRAK41
Drakelow PV & BESS Station | IB VOGT UK LTD | Drakelow 400kV Substation |  | 0 | 400 | 400 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000TPHnAAO | PRO-003238 | DRAK4 | 0 | DRAK41
Drax | ENSO GREEN HOLDINGS D LIMITED | Drax 132kV Substation |  | 0 | 190 | 190 | 2029-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ixOQAQ | PRO-001355 | DRAX1 | 190 | DRAX11
Drax Power Station | DRAX POWER LIMITED | Drax 400kV Substation |  | 3906 | 0 | 3906 |  | Built | Direct Connection | NGET | Biomass | a0l4L0000005ixUQAQ | PRO-000129 | DRAX4 | 3906 | DRAX41
Drinkstone Hybrid | BUCCLEUCH ESTATES LTD (THE) | Hawick 132kV Substation |  | 0 | 55 | 55 | 2035-07-01 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e0000012hpDAAQ | PRO-004534 | HAWI1 | 0 | HAWI1-
Drongan Battery Storage | Drongan Battery Storage Ltd | Coylton 275/132kV |  | 0 | 100 | 100 | 2026-10-20 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005ikaQAA | PRO-002287 | COYL1 | 100 | COYL1-
Drum of Clunas Wind and Solar Park | BROADHAVEN DISTRIBUTION LIMITED | Drum of Clunas 275kV |  | 0 | 150 | 150 | 2031-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f6J0AAI | PRO-003970 |  | 0
Dudgeon Offshore Wind Farm | DUDGEON OFFSHORE WIND LIMITED | Necton 400kV Substation |  | 400 | 0 | 400 |  | Built | Direct Connection | NGET | Wind Offshore | a0l4L0000005ioFQAQ | PRO-000132 | NECT4 | 400 | NECT41
Dunach Wind Farm | GALILEO 04 LIMITED | Taynuilt GSP |  | 0 | 100.8 | 100.8 | 2034-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l8e0000010wf7AAA | PRO-002754 | TAYN | 0 | TAYN3-
Dunan Hill | ORSTED ONSHORE UK LIMITED | Dunan Hill 400kV substation |  | 0 | 249.9 | 249.9 | 2036-11-11 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l8e0000012gbZAAQ | PRO-004433 |  | 0
Dunclent Battery Storage | Firma Vogt Solar Ltd | Warwickshire Connection Node A 400kV Substation |  | 0 | 400 | 400 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000010wltAAA | PRO-002827 |  | 0
Dungeness B | EDF ENERGY NUCLEAR GENERATION LIMITED | Dungeness 275kV Substation |  | 0 | 0 | 0 |  | Built | Direct Connection | NGET | Nuclear | a0l4L0000005ioGQAQ | PRO-000133 | DUNG2 | 0 | DUNG21
Dungeness Energy Park | SOUTH KENT ENERGY PARK LIMITED | East Kent connection node A 400kV Substation |  | 0 | 500 | 500 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iZRQAY | PRO-001986 | DUNG4 | 0 | DUNG41
Dungeness Energy Park (Dungeness 400kV) | SOUTH KENT ENERGY PARK LIMITED | Dungeness 400kV Substation |  | 0 | 500 | 500 | 2030-12-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0lJ9000000PDq5IAG | PRO-005021 | DUNG4 | 500 | DUNG41
Dunlaw Extension | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Dunlaw Extension 132/33kV |  | 29.75 | 126.25 | 156 | 2032-04-01 | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005imYQAQ | PRO-000061 | DUNE3 | 29.75 | DUNE3-
Dunmaglass Wind Farm | DUNMAGLASS WIND FARM LIMITED | Dunmaglass 132kV Substation |  | 94 | 0 | 94 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005imkQAA | PRO-000076 | DUNM1 | 94 | DUNM1-
Dunstable | Connectid 9 Limited | West Anglia Connection Node A 400kV Substation |  | 0 | 600 | 600 | 2034-10-30 | Scoping | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l8e000000TPReAAO | PRO-003418 |  | 0
ELMYA REDNAL | ELMYA RPC UK REDNAL LIMITED | Ironbridge 400kV Substation |  | 0 | 300 | 300 | 2034-10-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005j9YQAQ | PRO-002526 | IRON4 | 0 | IRON41
EMERGE Centre | UNIPER UK LIMITED | Ratcliffe-On-Soar 132kV Substation |  | 0 | 49.9 | 49.9 | 2024-07-01 | Awaiting Consents | Direct Connection | NGET | Waste | a0l4L0000005iutQAA | PRO-001462 | RATS1 | 49.9 | RATS11
EOLFI Offshore | Shell New Energies UK Ltd | Eolfi Offshore Substation |  | 0 | 3000 | 3000 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l4L0000005ihFQAQ | PRO-001538 | TEAL | 0 | TEAL3W
EPL Hampshire | EPL NEWCO7 LIMITED | Nursling 400kV Substation |  | 0 | 480 | 480 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012hp8AAA | PRO-004533 | NURS41 | 0 | NURS41
EPL Somerset | EPL NEWCO8 LIMITED | West Country Connection Node E 400kV Substation |  | 0 | 480 | 480 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f4yAAAQ | PRO-003905 | TAUN41 | 0 | TAUN41
EPL Suffolk | EPL NEWCO9 LIMITED | North Anglia Connection Node E 400kV Substation |  | 0 | 480 | 480 | 2032-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f5BYAAY | PRO-003916 |  | 0
ER BBR Energy | ER PROJECT DEVELOPMENT CO LIMITED | Er Bbr Energy 132kV Substation |  | 0 | 50 | 50 | 2029-10-30 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000011yBvAAI | PRO-003508 |  | 50
ER BR Energy | ER PROJECT DEVELOPMENT CO LIMITED | Tween Bridge 400kV |  | 0 | 1000 | 1000 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e000000exSTAAY | PRO-003724 |  | 0
ER BRF 2 Energy | ER PROJECT DEVELOPMENT CO LIMITED | Bramford 400kV Substation |  | 0 | 249 | 249 | 2033-07-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000exSYAAY | PRO-003725 | BRFO42 | 0 | BRFO41
ER BUR Energy | ER PROJECT DEVELOPMENT CO LIMITED | Burwell South 400kV Substation |  | 0 | 57 | 57 | 2033-10-28 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000exSEAAY | PRO-003721 | BURW4 | 0 | BURW41
ER HTP Energy | ER PROJECT DEVELOPMENT CO LIMITED | Hawthorn Pit 400kV Substation |  | 0 | 57 | 57 | 2034-06-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000exSJAAY | PRO-003722 | HAWP41 | 0 | HAWP41
ER LBR Energy | ER PROJECT DEVELOPMENT CO LIMITED | Littlebrook 400kV Substation |  | 0 | 57 | 57 | 2029-10-17 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000exSOAAY | PRO-003723 | LITT4 | 57 | LITT41
ER LIL Energy | ER PROJECT DEVELOPMENT CO LIMITED | Hope 400kV Substation |  | 0 | 1000 | 1000 | 2036-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000exRzAAI | PRO-003718 |  | 0
ER MKH Energy | ER PROJECT DEVELOPMENT CO LIMITED | Market Harborough 400kV Substation |  | 0 | 400 | 400 | 2033-10-28 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l8e0000010wTJAAY | PRO-002621 | MARH41 | 0 | MARH41
ER MSM Energy | ER PROJECT DEVELOPMENT CO LIMITED | Er Msm Energy 132kV Substation |  | 0 | 200 | 200 | 2030-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e0000011xwRAAQ | PRO-003480 |  | 200
ER TWD Energy | ER PROJECT DEVELOPMENT CO LIMITED | Llanteg 400kV Substation |  | 0 | 700 | 700 | 2037-09-15 | Scoping | Direct Connection | NGET | Energy Storage System;Wind Onshore | a0l8e000000exS4AAI | PRO-003719 |  | 0
Earba PSH | EARBA LIMITED | Earba PSH Powerhouse Substation | 2 | 0 | 1200 | 1800 | 2035-10-31 | Consents Approved | Direct Connection | SHET | Pump Storage | a0l8e000000f8OKAAY | PRO-004030-2 | BEAU | 0 | BEAU3U
Earba PSH | EARBA LIMITED | Earba PSH Powerhouse Substation | 1 | 0 | 600 | 600 | 2032-12-31 | Consents Approved | Direct Connection | SHET | Pump Storage | a0l8e000000f8OKAAY | PRO-004030-1 | BEAU | 0 | BEAU3U
Earl Shilton BESS | Exagen Development Limited | Earl Shilton 275kV |  | 0 | 500 | 500 | 2029-10-26 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iYVQAY | PRO-001950 | ENDE4 | 500 | ENDE41
Earraghail Renewable Energy Development (formerly Skipness & Corranbuie) | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Earraghail 275/33KV Substation |  | 0 | 105 | 105 | 2031-04-01 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005iePQAQ | PRO-001139 | EARR3 | 0 | EARR3-
East Anglia One | EAST ANGLIA ONE LIMITED | Platform EA One 220/66kV Offshore Substation |  | 680 | 0 | 680 |  | Built | Direct Connection | NGET | Wind Offshore | a0l4L0000005irMQAQ | PRO-000268 | FRIS41 | 680 | FRIS41
East Anglia One North | EAST ANGLIA ONE LIMITED | EA1N 275/66kV Offshore Platform |  | 0 | 860 | 860 | 2028-03-31 | Awaiting Consents | Direct Connection | NGET | Wind Offshore | a0l4L0000005irNQAQ | PRO-000269 | BRFO42 | 860 | BRFO41
East Anglia Three | EAST ANGLIA THREE LIMITED | East Anglia Project Three Offshore Platform | 2 | 0 | 100 | 1300 | 2028-12-31 | Consents Approved | Direct Connection | NGET | Wind Offshore | a0l4L0000005irOQAQ | PRO-000270-2 | BRFO42 | 100 | BRFO41
East Anglia Three | EAST ANGLIA THREE LIMITED | East Anglia Project Three Offshore Platform | 1 | 0 | 1200 | 1200 | 2026-01-31 | Consents Approved | Direct Connection | NGET | Wind Offshore | a0l4L0000005irOQAQ | PRO-000270-1 | BRFO41 | 1200 | BRFO41
East Anglia Two | EAST ANGLIA TWO LIMITED | EA2A and EA2B 275/66kV Offshore Platform | 2 | 0 | 20 | 880 | 2030-12-31 | Awaiting Consents | Direct Connection | NGET | Wind Offshore | a0l4L0000005ioHQAQ | PRO-000134-2 | FRIS4 | 20 | FRIS41
East Anglia Two | EAST ANGLIA TWO LIMITED | EA2A and EA2B 275/66kV Offshore Platform | 1 | 0 | 860 | 860 | 2028-03-31 | Awaiting Consents | Direct Connection | NGET | Wind Offshore | a0l4L0000005ioHQAQ | PRO-000134-1 | FRIS4 | 860 | FRIS41
East Claydon Green Energy Centre | INNOVA RENEWABLES LIMITED | East Claydon 400kV Substation |  | 0 | 1025 | 1025 | 2034-10-01 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ivLQAQ | PRO-002383 | ECLA4 | 0 | ECLA41
East Claydon Greener Grid Park | STATKRAFT UK LTD | East Claydon 400kV Substation |  | 0 | 650 | 650 | 2036-11-01 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iwgQAA | PRO-002314 | ECLA4 | 0 | ECLA41
East Claydon High Impact Green Energy Hub (HIGEH) 1 | TELIS ENERGY UK LIMITED | East Claydon 400kV Substation |  | 0 | 1000 | 1000 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;Nuclear;PV Array (Photo Voltaic/solar);Reactive Compensation;Wind Onshore | a0l8e0000010wW3AAI | PRO-002652 | ECLA4 | 0 | ECLA41
East Claydon Solar PV | STATERA ENERGY LIMITED | East Claydon 400kV Substation |  | 0 | 500 | 500 | 2026-10-01 | Scoping | Direct Connection | NGET | PV Array (Photo Voltaic/solar) | a0l4L0000005ivtQAA | PRO-001573 | ECLA4 | 500 | ECLA41
East Lincolnshire Solar | STATKRAFT UK LTD | Lincolnshire Coastal Node B 400kV Substation |  | 0 | 800 | 800 | 2035-05-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012khcAAA | PRO-004737 | LCNB4 | 0
East Pit | CS UK HOLDINGS III LIMITED | Rhigos 400kV Substation |  | 0 | 750 | 750 | 2037-10-15 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wdfAAA | PRO-002736 | RHIG4 | 0 | RHIG41
Eaton Socon High Impact Green Energy Hub (HIGEH) 1 | TELIS ENERGY UK LIMITED | Eaton Socon 400kV Substation |  | 0 | 1000 | 1000 | 2033-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;Nuclear;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e0000010wWNAAY | PRO-002656 | EASO41 | 0 | EASO41
Eaton Socon PV Storage | CSE37 Limited | Eaton Socon 400kV Substation |  | 0 | 49.9 | 49.9 | 2029-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ivcQAA | PRO-002218 | EASO41 | 49.9 | EASO41
Eaton Socon Solar | BROCKWELL STORAGE & SOLAR LIMITED | Eaton Socon 400kV Substation |  | 0 | 500 | 500 | 2028-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ifsQAA | PRO-001513 | EASO41 | 500 | EASO41
Eccles BESS | Weaver Power Limited | Eccles 132/33kV |  | 0 | 500 | 500 | 2026-04-12 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005idEQAQ | PRO-001470 | ECCL1 | 500 | ECCL1-
EcoGrainWest | Econergy International Limited | Grain West 400kV Substation |  | 0 | 249 | 249 | 2029-12-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iuGQAQ | PRO-002223 | WALE4 | 249 | WALE41
EcoGrimsbyWest | Econergy International Limited | Grimsby West 400kV Substation |  | 0 | 249 | 249 | 2031-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iv5QAA | PRO-002251 | GRIW4 | 0 | GRIW41
EcoKilwinning | Econergy International Limited | Kilwinning 132/33kV |  | 0 | 100 | 100 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000011yxHAAQ | PRO-003559 | KILW3 | 0 | KILW3-
EcoKincardine | Econergy International Limited | Kincardine North 400kV Substation |  | 0 | 249 | 249 | 2028-07-31 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000011yxGAAQ | PRO-003557 | KINN4 | 249 | KINN4-
EcoLovedean | Econergy International Limited | Lovedean 400kV Substation |  | 0 | 249 | 249 | 2031-03-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iu2QAA | PRO-002230 | LOVE4 | 0 | LOVE41
EcoMablethorpe | Econergy International Limited | Mablethorpe 400kV Substation |  | 0 | 249 | 249 | 2034-08-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wPHAAY | PRO-002583 | MABL4 | 0
EcoMossmorran | Econergy International Limited | Mossmorran 132/33kV |  | 0 | 249 | 249 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000011xZRAAY | PRO-003469 | MOSM1 | 0 | MOSM1A
EcoStocksbridge | Econergy International Limited | Stocksbridge 400kV Substation |  | 0 | 249 | 249 | 2036-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000ez6uAAA | PRO-003789 | STSB4 | 0 | STSB4A
EcoUskmouth | Econergy International Limited | Uskmouth 275kV Substation |  | 0 | 249 | 249 | 2029-06-14 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ic0QAA | PRO-002052 | USKM21 | 249 | USKM21
EcoWymondley | Econergy International Limited | Wymondley 2 400kV Substation |  | 0 | 249 | 249 | 2033-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005j9sQAA | PRO-002529 | WYMO4 | 0 | WYMO41
EcoYaxley1 | Econergy International Limited | Yaxley 400kV Substation |  | 0 | 249 | 249 | 2030-12-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ic1QAA | PRO-002053 | YAXL4 | 249 | YAXL41
Edinbane Windfarm | VATTENFALL WIND POWER LTD | Edinbane 132/33kV Substation | 1 | 41.4 | 0 | 41.4 |  | Built | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l4L0000005ioIQAQ | PRO-000135-1 | EDIN3 | 41.4 | EDIN3-
Edinbane Windfarm | VATTENFALL WIND POWER LTD | Edinbane 132/33kV Substation | 2 | 0 | 48.6 | 90 | 2033-04-30 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l4L0000005ioIQAQ | PRO-000135-2 | EDIN3 | 0 | EDIN3-
Edrom Green Energy Park | NP SPV 45 Limited | Kelloe Mains 400kV Substation |  | 0 | 400 | 400 | 2033-10-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0lJ9000000PEnkIAG | PRO-005818 |  | 0
Eggborough | SSE EGGBOROUGH LIMITED | Eggborough 400kV Substation |  | 0 | 550 | 550 | 2032-06-16 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ibxQAA | PRO-002049 | EGGB42 | 0 | EGGB42
Eggborough BESS | Fig Power Limited | Eggborough 400kV Substation |  | 0 | 200 | 200 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0lJ9000000PDl3IAG | PRO-004997 | EGGB42 | 0 | EGGB42
Eggborough CCGT - OCGT - BESS | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 2 | 0 | 451 | 2450 | 2027-10-01 | Awaiting Consents | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine);Energy Storage System;OCGT (Open Cycle Gas Turbine) | a0l4L0000005iktQAA | PRO-000136-2 | EGGB42 | 451 | EGGB42
Eggborough CCGT - OCGT - BESS | EGGBOROUGH POWER LIMITED | Eggborough 400kV Substation | 1 | 0 | 1999 | 1999 | 2026-10-01 | Awaiting Consents | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine);Energy Storage System;OCGT (Open Cycle Gas Turbine) | a0l4L0000005iktQAA | PRO-000136-1 | EGGB41 | 1999 | EGGB41
Eggborough PV & BESS Sub | O&G Solar (SPV 47) Limited | Eggborough 400kV Substation |  | 0 | 249.9 | 249.9 | 2033-10-28 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wQtAAI | PRO-002597 | EGGB41 | 0 | EGGB41
Elchies Wind Farm | ELCHIES WIND LIMITED | Elchies 132/33kV Substation | 2 | 0 | 71 | 170 | 2028-11-30 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005ixhQAA | PRO-000151-2 | ELCH3 | 71 | ELCH3-
Elchies Wind Farm | ELCHIES WIND LIMITED | Elchies 132/33kV Substation | 1 | 0 | 99 | 99 | 2028-11-30 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005ixhQAA | PRO-000151-1 | ELCH3 | 99 | ELCH3-
Elland BESS | Pulse Clean Energy Limited | Leeds North Connection Node E |  | 0 | 249 | 249 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000011xZ7AAI | PRO-003465 |  | 0
Elland BESS | O&G Solar (SPV 39) Limited | Elland 132kV Substation |  | 0 | 99.9 | 99.9 | 2036-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f4nAAAQ | PRO-003870 | ELLA1 | 0 | ELLA11
Elmya Bathgate BESS | RPC ELMYA CARNATION DEVCO LIMITED | Armadale 400kv Substation |  | 0 | 300 | 300 | 2031-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000012gYpAAI | PRO-004416 | ARMA1 | 0 | ARMA1-
Elmya Braybrooke BESS | ELMYA RPC UK BRAYBROOKE LIMITED | Braybrooke 400kV Substation |  | 0 | 252 | 252 | 2031-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005ikbQAA | PRO-002427 | BRAY4 | 0
Elmya Dalry BESS & PV | ELMYA ENERGY UK 17 LIMITED | Hunterston 400/132kV |  | 0 | 800 | 800 | 2033-10-25 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000exYIAAY | PRO-003735 | HUER4 | 0 | HUER4-
Elmya Dunbar BESS | ELMYA ENERGY UK 1 LIMITED | Thorntonloch 400kV Substation |  | 0 | 400 | 400 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005iwdQAA | PRO-002290 |  | 0
Elmya Foxdale BESS | RPC ELMYA CARNATION FOXDALE LIMITED | Trent Valley South Connection Node C 400kV Substation |  | 0 | 800 | 800 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0lJ9000000bligIAA | PRO-004934 |  | 0
Elmya Gissing BESS & PV | RPC ELMYA CARNATION GISSING LIMITED | North Anglia Connection Node A 400kV |  | 0 | 900 | 900 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012jJxAAI | PRO-004657 |  | 0
Elmya Grange Road | ELMYA RPC UK GRANGE ROAD LIMITED | Elmya Grange 400kV |  | 0 | 300 | 300 | 2031-10-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005il8QAA | PRO-002340 |  | 0
Elmya Hunterston | ELMYA RPC UK HUNTERSTON LIMITED | Hunterston 400/132kV |  | 0 | 400 | 400 | 2030-10-25 | Awaiting Consents | Direct Connection | SPT | Energy Storage System | a0l8e000000TPBVAA4 | PRO-003182 | HUER4 | 400 | HUER4-
Elmya Kilworth BESS & PV | RPC ELMYA CARNATION KILWORTH LIMITED | Derbyshire Connection Node H 400kV Substation |  | 0 | 850 | 850 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012khrAAA | PRO-004739 |  | 0
Elmya Melbourne BESS | ELMYA RPC UK MELBOURNE LIMITED | Thornton 400kV Substation |  | 0 | 300 | 300 | 2033-10-28 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005iylQAA | PRO-002424 | THTO43 | 0 | THTO43
Elmya Morningside BESS & PV | ELMYA RPC UK MORNINGSIDE LIMITED | Elmya Morningside 400kV Substation |  | 0 | 400 | 400 | 2033-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012fGMAAY | PRO-004396 |  | 0
Elmya Towcester BESS | RPC ELMYA CARNATION TOWCASTER LIMITED | Derbyshire Connection Node I 400kV Substation |  | 0 | 550 | 550 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0lJ9000000blLAIAY | PRO-004809 |  | 0
Elstree (tertiary) | ELSTREE GREEN LIMITED | Elstree 275kV Substation |  | 0 | 57 | 57 | 2030-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iMTQAY | PRO-000400 | ELST22 | 57 | ELST22
Elstree BESS NP | NORIKER POWER LTD | Elstree 400kV Substation |  | 0 | 500 | 500 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000010wh8AAA | PRO-002776 | ELST41 | 0 | ELST41
Elstree Energy Storage | BW ESS DEVELOPMENT UK LIMITED | Elstree 132kV Substation |  | 0 | 170 | 170 | 2029-10-01 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TPDlAAO | PRO-003205 | ELST1 | 170 | ELST11
Elvanfoot (25MW) Energy Storage | ELVANFOOT ENERGY STORAGE LIMITED | Elvanfoot 275/132/33kV |  | 0 | 25 | 25 | 2029-10-26 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000TPNHAA4 | PRO-003278 | ELVA3 | 25 | ELVA3A
Elvanfoot (50MW) Energy Storage | ELVANFOOT ENERGY STORAGE LIMITED | Elvanfoot 275/132/33kV |  | 0 | 50 | 50 | 2029-10-26 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000TPNMAA4 | PRO-003279 | ELVA3 | 50 | ELVA3A
Elvanfoot (9.8 MW) Energy Storage | ELVANFOOT ENERGY STORAGE LIMITED | Elvanfoot 400/275/33kV |  | 0 | 9.8 | 9.8 | 2027-04-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005igKQAQ | PRO-001721 | ELVA3 | 9.8 | ELVA3A
Enderby (Akira) | ENDERBY BATTERY STORAGE LIMITED | Enderby 400kV Substation |  | 0 | 57 | 57 | 2024-12-09 | Built | Direct Connection | NGET | Energy Storage System | a0l4L0000005ilwQAA | PRO-000426 | ENDE4 | 57 | ENDE41
Enderby BESS | EARL SHILTON ENERGY PARK LIMITED | Earl Shilton 400kV Substation |  | 0 | 249.9 | 249.9 | 2033-11-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f4nKAAQ | PRO-003872 | ENDE4 | 0 | ENDE41
Enderby Farm | 548 UK INVESTMENT HOLDINGS LIMITED | Earl Shilton 400kV Substation |  | 0 | 200 | 200 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wYsAAI | PRO-002682 | ENDE4 | 0 | ENDE41
Enderby Farm 2 | 548 UK INVESTMENT HOLDINGS LIMITED | Earl Shilton 400kV Substation |  | 0 | 700 | 700 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010weEAAQ | PRO-002743 | ENDE4 | 0 | ENDE41
Enderby Green Energy Centre | ENDERBY GREEN NG LIMITED | Enderby 400kV Substation |  | 0 | 1025 | 1025 | 2028-10-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005itgQAA | PRO-002177 | ENDE4 | 1025 | ENDE41
Enderby Solar & BESS | GREENTECH PROJECTS HOLDING UK LIMITED | Enderby 400kV Substation |  | 0 | 500 | 500 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012hpcAAA | PRO-004540 | ENDE4 | 0 | ENDE41
Enderby Tertiary | CLUMP FARM SOLAR LIMITED | Enderby 400kV Substation |  | 0 | 57 | 57 | 2027-08-01 | Scoping | Direct Connection | NGET | PV Array (Photo Voltaic/solar) | a0l4L0000005izzQAA | PRO-000430 | ENDE4 | 57 | ENDE41
Energy Isles | ENERGY ISLES SHETLAND LIMITED | Energy Isles 132kV Substation |  | 0 | 120.3 | 120.3 | 2032-10-30 | Awaiting Consents | Direct Connection | SHET | Wind Onshore | a0l4L0000005imtQAA | PRO-000447 | ENEI1 | 0 | ENEI1-
Enfield | UNIPER UK LIMITED | Brimsdown 132kV Substation |  | 442 | 0 | 442 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005ioSQAQ | PRO-000147 | BRIM1 | 442 | BRIM11
Enoch Hill | RWE RENEWABLES UK ONSHORE WIND LIMITED | Enoch Hill 132/33kV Substation |  | 0 | 69 | 69 | 2025-05-30 | Consents Approved | Direct Connection | SPT | Wind Onshore | a0l4L0000005iomQAA | PRO-000152 | ENHI3 | 69 | ENHI3-
Enoch Hill 2 Wind Farm | RWE RENEWABLES UK ONSHORE WIND LIMITED | Enoch Hill 2 Wind Farm 132kV/33kV |  | 0 | 10 | 10 | 2027-04-30 | Awaiting Consents | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l4L0000005indQAA | PRO-000478 | MONQ3 | 10 | MONQ3-
Epworth PV & BESS Station | IB VOGT UK LTD | Keadby 400kV Substation |  | 0 | 150 | 150 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000ew2TAAQ | PRO-003644 | KEAD4 | 0 | KEAD41
Equinor Celtic Sea 1 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation |  | 0 | 1000 | 1000 | 2036-12-06 | Scoping | Direct Connection | NGET | Energy Storage System;Wind Offshore | a0l8e000000f8QCAAY | PRO-004037 | ALVE4A | 0 | ALVE4A
Equinor Celtic Sea 2 | EQUINOR NEW ENERGY LIMITED | Alverdiscott 400kV Substation |  | 0 | 1000 | 1000 | 2036-12-06 | Scoping | Direct Connection | NGET | Energy Storage System;Wind Offshore | a0l8e000000f8QHAAY | PRO-004038 | ALVE4A | 0 | ALVE4A
Erebus | Blue Gem Wind Limited | Pembroke 132kV Substation |  | 0 | 95.25 | 95.25 | 2028-07-26 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005inxQAA | PRO-000471 | PEMB1 | 95.25 | PEMB11
Eredine Wind Farm | RWE RENEWABLES UK ONSHORE WIND LIMITED | An Suidhe 275/33kV |  | 0 | 105 | 105 | 2029-11-01 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005ia2QAA | PRO-002005 | ANSN3 | 105 | ANSN3-
Errochty | SSE Generation Limited | Errochty 132kV Substation |  | 75 | 0 | 75 |  | Built | Direct Connection | SHET | Hydro | a0l4L0000005ihIQAQ | PRO-001541 | ERRO1 | 75 | ERRO1A
Eskrigg End BESS | Energi Generation 6 Ltd | Hutton 400kV Substation |  | 0 | 249 | 249 | 2037-11-01 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000010wjnAAA | PRO-002804 | HUTT4 | 0 | HUTT41
Essendine | MALLARD PASS SOLAR FARM LIMITED | Ryhall 400kV Substation |  | 0 | 240 | 240 | 2028-01-01 | Consents Approved | Direct Connection | NGET | PV Array (Photo Voltaic/solar) | a0l4L0000005iNfQAI | PRO-001643 | RYHA42 | 240 | RYHA4A
Euchanhead Wind Farm | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Euchanhead 132kV Substation |  | 0 | 112 | 112 | 2029-10-29 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005ibQQAQ | PRO-001011 | EUCH1 | 112 | EUCH1-
Ewe Hill | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Ewehill 132/33kV |  | 39 | 0 | 39 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005iZAQAY | PRO-001368 | EWEH3 | 39 | EWEH3-
Ewerby | SSE EWERBY SOLAR LIMITED | Navenby 400kV Substation |  | 0 | 500 | 500 | 2029-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iaDQAQ | PRO-002017 | BICF4 | 500 | BICF41
Exeter (Tertiary) | PIVOTED POWER LLP | Exeter 400kV Substation | 1 | 0 | 49.9 | 49.9 | 2028-06-16 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iz7QAA | PRO-001047-1 | EXET4 | 49.9 | EXET41
Exeter (Tertiary) | PIVOTED POWER LLP | Exeter 400kV Substation | 2 | 0 | 7.1 | 57 | 2036-12-06 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iz7QAA | PRO-001047-2 | EXET4 | 0 | EXET41
Exeter BESS | Exeter Storage Limited | Exeter 400kV Substation |  | 0 | 290 | 290 | 2027-08-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ivyQAA | PRO-001666 | EXET4 | 290 | EXET41
Exeter BESS and PV (Post-Interactivity Revised Offer) | Broadclyst Energy Storage Limited | Exeter Main 400kV Substation |  | 0 | 249 | 249 | 2029-12-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iNpQAI | PRO-001827 | EXET4 | 249 | EXET41
Exeter Main | ENSO GREEN HOLDINGS LIMITED | Exeter 400kV Substation |  | 0 | 400 | 400 | 2033-10-28 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005idfQAA | PRO-002082 | EXET4 | 0 | EXET41
Exeter Main Tertiary | EXETER MAIN BATTERY LIMITED | Exeter 400kV Substation |  | 0 | 57 | 57 | 2024-05-01 | Scoping | Direct Connection | NGET | Thermal | a0l4L0000005izUQAQ | PRO-000452 | EXET4 | 57 | EXET41
Eye Grid Services Facility | CONRAD (EYE) LIMITED | Yaxley 400kV Substation |  | 0 | 0 | 0 | 2024-10-31 | Consents Approved | Direct Connection | NGET | Reactive Compensation | a0l8e000000eww9AAA | PRO-003688 | YAXL4 | 0 | YAXL41
FCC Thurcroft BESS | Downing Renewable Developments LLP | Thorpe Marsh GSP |  | 0 | 750 | 750 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TPMJAA4 | PRO-003268 | THOM42 | 0 | THOM42
Fairburn Extension Wind Farm | SSE RENEWABLES SERVICES (UK) LIMITED | Fairburn Extension 132/33kV Substation |  | 0 | 90 | 90 | 2031-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l8e000000f7klAAA | PRO-004012 | ORRI3 | 0 | ORRI3-
Fairholme BESS | HB411MIN Limited | Minety 400kV Substation |  | 0 | 47.5 | 47.5 | 2025-02-28 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005ixgQAA | PRO-001625 | MITY4 | 47.5 | MITY41
Fairmead and Yewtree Farm | QAIR RENEWABLES UK LIMITED | East Kent connection node A 400kV Substation |  | 0 | 240 | 240 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001HxldAAC | PRO-004291 | CANT4 | 0 | CANT41
Fallago Rig 2 | EDF ENERGY RENEWABLES LIMITED | Fallago 400/33kV |  | 0 | 100 | 100 | 2029-04-30 | Awaiting Consents | Direct Connection | SPT | Wind Onshore | a0l4L0000005ipGQAQ | PRO-000526 | FALL3 | 100 | FALL3A
Fallago Rig Wind Farm | FALLAGO RIG WINDFARM LIMITED | Fallago 400/33kV |  | 144 | 0 | 144 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005iooQAA | PRO-000155 | FALL3 | 144 | FALL3A
Fancott | SSE FANCOTT BESS LTD | Sundon 400kV Substation |  | 0 | 600 | 600 | 2031-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iu4QAA | PRO-002174 | SUND42 | 0 | SUND42
Farm 100MW BESS | Apatura Battery Ltd | Thurso South 275kV Substation’ |  | 0 | 100 | 100 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e000000f6J5AAI | PRO-003971 | THUS2 | 0 | THUS2J
Farr Wind Farm - Tomatin | FARR WINDFARM LIMITED | Beauly GSP |  | 92 | 0 | 92 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005iopQAA | PRO-000156 | BEAU | 92 | BEAU3U
Farr WindFarm | FARR WINDFARM LIMITED | Tomatin 275kV Substation |  | 0 | 144.8 | 144.8 | 2030-01-30 | Scoping | Direct Connection | SHET | Wind Onshore | a0l8e0000012eoeAAA | PRO-004381 | TOMT2 | 144.8 | TOMT2J
Fasnakyle G1 & G2 | SSE Generation Limited | Fasnakyle GSP |  | 46 | 0 | 46 |  | Built | Direct Connection | SHET | Hydro | a0l4L0000005imlQAA | PRO-000077 | FASN | 46 | FASN3-
Fasque Windfarm | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Fasque Wind Farm 132kV Substation |  | 0 | 90 | 90 | 2031-10-31 | Scoping | Direct Connection | SHET | PV Array (Photo Voltaic/solar);Wind Onshore | a0l4L0000005ibSQAQ | PRO-001009 | FASQ3 | 0 | FASQ3-
Faw Side Community Wind Farm | CWP Energy Limited | Faw Side Community Wind Farm Substation |  | 0 | 250 | 250 | 2028-04-27 | Awaiting Consents | Direct Connection | SPT | Wind Onshore | a0l4L0000005isGQAQ | PRO-000297 | FASI | 250 | FASI1-
Fearna PSH | FEARNA PSH LIMITED | Loch Fearna Pumped Storage 275kV |  | 0 | 1495 | 1495 | 2036-11-11 | Scoping | Direct Connection | SHET | Pump Storage | a0l8e0000012ezMAAQ | PRO-004391 |  | 0
Feckenham | ENSO GREEN HOLDINGS LIMITED | Feckenham 400kV Substation |  | 0 | 400 | 400 | 2036-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ikrQAA | PRO-002189 | FECK4 | 0 | FECK41
Feckenham | IGP SOLAR 14 LIMITED | Feckenham 400kV Substation |  | 0 | 500 | 500 | 2029-07-21 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iOwQAI | PRO-001600 | FECK4 | 500 | FECK41
Feckenham Energy Park | GREEN ENERGY MAB LTD | Feckenham 400kV Substation |  | 0 | 500 | 500 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iM7QAI | PRO-002378 | FECK4 | 0 | FECK41
Feckenham Green Energy Centre | FECKENHAM GREEN NG LIMITED | Feckenham 400kV Substation |  | 0 | 1025 | 1025 | 2032-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iitQAA | PRO-001767 | FECK4 | 0 | FECK41
Feckenham Greener Grid Park | STATKRAFT UK LTD | Feckenham 400kV Substation | 1 | 0 | 12 | 12 | 2028-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ibTQAQ | PRO-001008-1 | FECK4 | 12 | FECK41
Feckenham Greener Grid Park | STATKRAFT UK LTD | Feckenham 400kV Substation | 2 | 0 | 138 | 150 | 2032-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ibTQAQ | PRO-001008-2 | FECK4 | 0 | FECK41
Feckenham PV & BESS Station | IB VOGT UK LTD | Feckenham 400kV Substation |  | 0 | 400 | 400 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000TPHOAA4 | PRO-003233 | FECK4 | 0 | FECK41
Fell Wind Farm | ENERGYFARM UK FELL LLP | SPT Margree collector substation |  | 0 | 50 | 50 | 2029-10-31 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005izPQAQ | PRO-001755 | FELL3 | 50 | FELL3-
Fenwick Solar Project | STARK ENERGY LIMITED | Thorpe Marsh 400kV Substation |  | 0 | 237.5 | 237.5 | 2032-04-16 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ix1QAA | PRO-001915 | THOM42 | 0 | THOM42
Ferrybridge B BESS & Solar Substation | O&G Solar (SPV 19) Limited | Ferrybridge B 132kV Substation |  | 0 | 99.9 | 99.9 | 2035-10-24 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005j8VQAQ | PRO-002521 | FERR1 | 0 | FERR11
Ferrybridge C PV & BESS Substation | O&G Solar (SPV 19) Limited | Ferrybridge C 275kV Substation |  | 0 | 249.9 | 249.9 | 2035-10-24 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000evg6AAA | PRO-003632 | FERR21 | 0 | FERR21
Ferrybridge D | KEADBY GENERATION LIMITED | Ferrybridge C 275kV Substation | 1 | 0 | 310 | 310 | 2028-10-06 | Scoping | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine);Demand;Energy Storage System;OCGT (Open Cycle Gas Turbine) | a0l4L0000005iacQAA | PRO-001020-1 | FERR21 | 310 | FERR21
Ferrybridge D | KEADBY GENERATION LIMITED | Ferrybridge C 275kV Substation | 2 | 0 | 910 | 1220 | 2030-10-04 | Awaiting Consents | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine);Demand;Energy Storage System;OCGT (Open Cycle Gas Turbine) | a0l4L0000005iacQAA | PRO-001020-2 | FERR22 | 910 | FERR22
Ferrybridge D | KEADBY GENERATION LIMITED | Ferrybridge C 275kV Substation | 3 | 0 | 600 | 1820 | 2034-06-01 | Awaiting Consents | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine);Demand;Energy Storage System;OCGT (Open Cycle Gas Turbine) | a0l4L0000005iacQAA | PRO-001020-3 | FERR23 | 0 | FERR23
Fferm Solar Pentir | LIGHTSOURCE SPV 191 LIMITED | Pentir 400kV Substation |  | 0 | 57 | 57 | 2027-05-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ixKQAQ | PRO-001049 | PENT4 | 57 | PENT41
Ffestiniog | First Hydro Company | Ffestiniog 275kV Substation |  | 360 | 0 | 360 |  | Built | Direct Connection | NGET | Pump Storage | a0l4L0000005im9QAA | PRO-000055 | FFES21 | 360 | FFES21
Fiddlers Ferry BESS | FIDDLERS FERRY LTD | Fiddlers Ferry 275kV Substation |  | 0 | 900 | 900 | 2037-11-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f4xWAAQ | PRO-003897 | FIDF2 | 0 | FIDF21
Field Farm | Net Zero One Limited | Staythorpe 400kv |  | 0 | 249.9 | 249.9 | 2030-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iRcQAI | PRO-001924 | STAY41 | 249.9 | STAY41
Field Glenniston BESS | FIELD DEVCO LTD | Glenniston GSP |  | 0 | 200 | 200 | 2032-10-29 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000012kjiAAA | PRO-004754 | GLNI | 0 | GLNI3-
Field Kinardochy BESS | Field Devco Ltd | Kinardochy Substation. 400/275kV |  | 0 | 400 | 400 | 2035-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0lJ9000000PDyYIAW | PRO-005104 |  | 0
Fife 2 BESS | CARLTON POWER LIMITED | Westfield 132/33kV |  | 0 | 49.9 | 49.9 | 2028-06-14 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005iw1QAA | PRO-002184 | WFIE3 | 49.9 | WFIE3-
Fife Battery Storage | CARLTON POWER LIMITED | Westfield 132/33kV |  | 0 | 200 | 200 | 2031-10-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005iQVQAY | PRO-001888 | WFIE3 | 0 | WFIE3-
Fife Energy Centre | CAMBRIDGE POWER LIMITED | Fife Energy Centre 132kV substation |  | 0 | 100 | 100 | 2028-04-28 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005iPYQAY | PRO-001868 | FIGS2 | 100 | FIGS2-
Fife Grid Services | BLUEGRIDPOWER LTD | Fife Grid Services Facility 275kV Substation |  | 0 | 0 | 0 | 2024-04-12 | Scoping | Direct Connection | SPT | Reactive Compensation | a0l4L0000005inRQAQ | PRO-000453 | FIGS2 | 0 | FIGS2-
Finlarig | SSE Generation Limited | Finlarig GSP | 1 | 16.5 | 0 | 16.5 |  | Built | Direct Connection | SHET | Hydro | a0l4L0000005immQAA | PRO-000079-1 | FINL | 16.5 | FINL5-
Finlarig | SSE Generation Limited | Finlarig GSP | 2 | 0 | 18.5 | 35 | 2031-11-30 | Scoping | Direct Connection | SHET | Hydro | a0l4L0000005immQAA | PRO-000079-2 | FINL | 0 | FINL5-
Five Estuaries Offshore Wind Farm | FIVE ESTUARIES OFFSHORE WIND FARM LIMITED | Five Estuaries 220/66 kV Offshore Substation |  | 0 | 1080 | 1080 | 2030-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005izvQAA | PRO-000450 | EACS4 | 1080
Flash Solar Farm | ELEMENTS GREEN TRENT LTD | Staythorpe 400kV Substation | 2 | 0 | 440 | 800 | 2028-05-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iNYQAY | PRO-001634-2 | STAY41 | 440 | STAY41
Flash Solar Farm | ELEMENTS GREEN TRENT LTD | Staythorpe 400kV Substation | 1 | 0 | 360 | 360 | 2026-08-30 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iNYQAY | PRO-001634-1 | STAY41 | 360 | STAY41
Fleet (Tertiary) | CSE23 LIMITED | Fleet 400kV Substation |  | 0 | 47.5 | 47.5 | 2026-10-31 | Consents Approved | Direct Connection | NGET | PV Array (Photo Voltaic/solar) | a0l4L0000005izAQAQ | PRO-001087 | FLEE4 | 47.5 | FLEE41
Fleet EGH (Tertiary) | Fleet Green Limited | Fleet 400kV Substation |  | 0 | 47.5 | 47.5 | 2027-01-13 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ipwQAA | PRO-000544 | FLEE4 | 47.5 | FLEE41
Fleet Farm | BASINGSTOKE EAST 2 RENEWABLES LTD | Fleet 400kV Substation |  | 0 | 200 | 200 | 2038-04-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wYYAAY | PRO-002678 | FLEE4 | 0 | FLEE41
Fleet Farm 2 | Basingstoke East 7 Renewables Ltd | Fleet 400kV Substation |  | 0 | 700 | 700 | 2038-06-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wduAAA | PRO-002739 | FLEE4 | 0 | FLEE41
Fleet Solar PV | FLEET SOLAR LIMITED | Fleet 400kV Substation |  | 0 | 57 | 57 | 2026-12-13 | Awaiting Consents | Direct Connection | NGET | PV Array (Photo Voltaic/solar) | a0l8e0000010wklAAA | PRO-002814 | FLEE4 | 57 | FLEE41
Fleet Tertiary | FLEET SOLAR LIMITED | Fleet 400kV Substation |  | 0 | 47.5 | 47.5 | 2025-11-30 | Scoping | Direct Connection | NGET | Thermal | a0l4L0000005j00QAA | PRO-000429 | FLEE4 | 47.5 | FLEE41
Flemyland Battery Storage | Flemyland Battery Storage Ltd | Kilwinning 132/33kV |  | 0 | 100 | 100 | 2027-10-26 | Scoping | Direct Connection | SPT | Demand;Energy Storage System | a0l4L0000005iyIQAQ | PRO-002360 | KILW3 | 100 | KILW3-
Foel Fach Wind Farm | FOEL FACH WIND FARM LIMITED | North Wales connection Node A 400kV Substation |  | 0 | 79.2 | 79.2 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;Wind Onshore | a0l8e000001Hy9vAAC | PRO-004327 |  | 0
Forsa Energy Denny BESS | FORSA ENERGY GAS HOLDINGS LIMITED | FORSA ENERGY DENNY BESS 132KV GRID SUPPLY POINT SUBSTATION |  | 0 | 99.9 | 99.9 | 2030-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0lJ9000000bltAIAQ | PRO-004971 | DENN1 | 99.9 | DENN1-
Fort Augustus BESS | FIELD DEVCO LTD | Fort Augustus GSP |  | 0 | 200 | 200 | 2035-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000012i3dAAA | PRO-004599 | FAUG | 0 | FAUG3X
Foyers | SSE Generation Limited | Foyers 275kV Substation |  | 300 | 0 | 300 |  | Built | Direct Connection | SHET | Pump Storage | a0l4L0000005imnQAA | PRO-000080 | FOYE2 | 300 | FOYE2-
Freasdail | FREASDAIL ENERGY LIMITED | Crossaig 132kV Substation |  | 22.2 | 0 | 22.2 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005im3QAA | PRO-000046 | CRSS1 | 22.2 | CRSS1J
Fyrish Battery Storage | FIELD DEVCO LTD | Fyrish 132kV Substation |  | 0 | 200 | 200 | 2029-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000012hngAAA | PRO-004515 | FYRI1 | 200 | FYRI1J
GALILEO 12 LIMITED | GALILEO 12 LIMITED | Fetteresso 132kV substation |  | 0 | 150.8 | 150.8 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0lJ9000000blKgIAI | PRO-004804 |  | 0
GALILEO 16 | GALILEO 16 LIMITED | Gala North 400/132kV Substation |  | 0 | 125 | 125 | 2032-10-29 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0lJ9000000PEBCIA4 | PRO-005117 |  | 0
GF Norwich BESS | GF Norwich Energy Ltd | Norwich Main 400kV Substation |  | 0 | 400 | 400 | 2032-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f3zmAAA | PRO-003807 | NORM42 | 0 | NORM41
GF SELLINDGE BESS | GF Sellindge Energy Ltd | East Kent connection node A 400kV Substation |  | 0 | 300 | 300 | 2036-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001HrvJAAS | PRO-004228 | SELL4 | 0 | SELL4A
GF Thornton Energy BESS | GF THORNTON ENERGY LTD | Thornton 400kV Substation |  | 0 | 400 | 400 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TPcPAAW | PRO-003449 | THTO43 | 0 | THTO43
GF Upper Boat | PULSE CLEAN ENERGY SPV FRANKLIN LIMITED | Upper Boat 275kV Substation | 3 | 0 | 200 | 200 | 2028-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;Reactive Compensation | a0l8e0000011zBpAAI | PRO-003568-3 | UPPB22 | 200 | UPPB22
GF Upper Boat | PULSE CLEAN ENERGY SPV FRANKLIN LIMITED | Upper Boat 275kV Substation | 2 | 0 | 0 | 0 | 2025-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;Reactive Compensation | a0l8e0000011zBpAAI | PRO-003568-2 | UPPB22 | 0 | UPPB22
GF Upper Boat | PULSE CLEAN ENERGY SPV FRANKLIN LIMITED | Upper Boat 275kV Substation | 1 | 0 | 0 | 0 | 2025-05-31 | Scoping | Direct Connection | NGET | Energy Storage System;Reactive Compensation | a0l8e0000011zBpAAI | PRO-003568-1 | UPPB21 | 0 | UPPB21
GH DEVCO Gretna Green BESS | Gresham House Devco Pipeline Limited | Gretna Green 132 kV Substation |  | 0 | 56 | 56 | 2032-10-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000010xikAAA | PRO-003096 | GRNA1 | 0 | GRNA1-
GH DEVCO Kincardine BESS | Gresham House Devco Pipeline Limited | Kincardine GSP |  | 0 | 42 | 42 | 2028-12-01 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000TPAmAAO | PRO-003173 | KINC | 42 | KINC2-
GT R4 Wind Farm | GT R4 LIMITED | Weston Marsh 400kV Substation |  | 0 | 1500 | 1500 | 2030-11-30 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005izbQAA | PRO-000563 | WEMA4 | 1500
Gaerwen Wind Farm | RWE RENEWABLES UK ONSHORE WIND LIMITED | Gwyddelwern 400kV Substation |  | 0 | 67 | 67 | 2027-06-01 | Awaiting Consents | Direct Connection | NGET | Wind Onshore | a0l4L0000005ihPQAQ | PRO-001550 | GWYD4 | 67 | GWYD41
Galawhistle Wind Farm | GALAWHISTLE WIND FARM LIMITED | Galawhistle 132/33kV Substation |  | 55.2 | 0 | 55.2 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005iosQAA | PRO-000161 | GAWH3 | 55.2 | GAWH3-
Galileo 05 | GALILEO 05 LIMITED | Lynemore Windfarm 132kV Substation |  | 0 | 84 | 84 | 2031-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l8e000001Hr2cAAC | PRO-004173 |  | 0
Galileo 07 Limited | GALILEO 07 LIMITED | Cassley GSP |  | 0 | 150 | 150 | 2032-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0lJ9000000PDr3IAG | PRO-005029 |  | 0
Galileo 09 | GALILEO 09 LIMITED | Oswestry Substation |  | 0 | 297 | 297 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0lJ9000000blKCIAY | PRO-004798 |  | 0
Galileo 10 | GALILEO 10 LIMITED | Bathgate 132/33kV Substation |  | 0 | 60 | 60 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000f65AAAQ | PRO-003953 | BAGA3 | 0 | BAGA3-
Gallatown Battery Energy Storage Facility | CESA (KIRKCALDY) LIMITED | Redhouse 132/33kV |  | 0 | 80 | 80 | 2029-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000010wfCAAQ | PRO-002755 | REDH3 | 80 | REDH3-
Galloper Wind Farm | GALLOPER WIND FARM LIMITED | Galloper North 132/33kV Substation |  | 348 | 0 | 348 |  | Built | Direct Connection | NGET | Wind Offshore | a0l4L0000005iotQAA | PRO-000162 | LEIS1 | 348 | LEIS11
Gallos | Corio Generation Limited | Alverdiscott 400kV Substation |  | 0 | 2000 | 2000 | 2036-12-06 | Scoping | Direct Connection | NGET | Wind Offshore | a0l8e0000010wdVAAQ | PRO-002734 | ALVE4A | 0 | ALVE4A
Gammidge PV & BESS Park | CS UK HOLDINGS III LIMITED | Grendon 132kV Substation |  | 0 | 40.9 | 40.9 | 2027-10-15 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iOtQAI | PRO-001649 | GREN1 | 40.9 | GREN11
Garn Fach Wind Farm | EDF ENERGY RENEWABLES LIMITED | Garn Fach 132kV Substation |  | 0 | 110 | 110 | 2032-05-01 | Scoping | Direct Connection | NGET | Wind Onshore | a0l4L0000005iv1QAA | PRO-001157 |  | 0
Gartclash Farm BESS | BOOM DEVELOPMENTS LTD | Denny North 275/132kV |  | 0 | 200 | 200 | 2028-10-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000exYNAAY | PRO-003736 | DENN1 | 200 | DENN1-
Garvary Wind Farm | GARVARY WIND FARM LTD | Garvary 132kV Substation |  | 0 | 222 | 222 | 2028-06-30 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005iyqQAA | PRO-001927 | BEAU1 | 222 | BEAU1J
Gastard BESS | SIRIUSECODEV (GASTARD) LTD | Melksham B 132KV Substation |  | 0 | 200 | 200 | 2037-11-15 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000011yrPAAQ | PRO-003552 | MELK1 | 0 | MELK11
Gateway Energy Centre Power Station | GATEWAY ENERGY CENTRE LIMITED | Coryton South 400kV Substation | 2 | 0 | 550 | 1000 | 2029-10-30 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005im2QAA | PRO-000045-2 | COSO4 | 550 | COSO41
Gateway Energy Centre Power Station | GATEWAY ENERGY CENTRE LIMITED | Coryton South 400kV Substation | 1 | 0 | 450 | 450 | 2025-09-30 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005im2QAA | PRO-000045-1 | COSO4 | 450 | COSO41
Gatroben Offshore Wind Farm | GATROBEN OFFSHORE DEVELOPMENTS 2 LIMITED | Gatroben Offshore Substation |  | 0 | 1320 | 1320 | 2031-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005idWQAQ | PRO-001675 |  | 0
Glen App Windfarm | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Glen App 33kV |  | 32.2 | 0 | 32.2 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005imaQAA | PRO-000063 | GLAP3 | 32.2 | GLAP3-
Glen Earrach PSH | GLEN EARRACH ENERGY LIMITED | Glen Earrach PSH 400kV substation |  | 0 | 1800 | 1800 | 2035-10-31 | Scoping | Direct Connection | SHET | Pump Storage | a0lJ9000000blarIAA | PRO-004903 |  | 0
Glen Kyllachy Wind Farm | GLEN KYLLACHY WIND FARM LIMITED | Glen Kyllachy Wind Farm Substation |  | 48.5 | 0 | 48.5 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005iovQAA | PRO-000165 | GLKO | 48.5 | GLKO1-
Glen Lednock | Glen Lednock Wind Farm Limited | Glen Lednock 132kV Substation |  | 0 | 165 | 165 | 2031-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l8e0000012ho5AAA | PRO-004520 |  | 0
Glen Ullinish Extension | GLEN ULLINISH WF 2 LTD | Glen Ullinish Extension 132/33kV Substation |  | 0 | 240 | 240 | 2027-04-01 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005iYiQAI | PRO-001346 | GLUE1 | 240 | GLUE1-
Glen Ullinish Wind Farm | GLEN ULLINISH WF LIMITED | Glen Ullinish 132/33kV Substation |  | 0 | 49.9 | 49.9 | 2026-10-31 | Consents Approved | Direct Connection | SHET | Wind Onshore | a0l4L0000005isHQAQ | PRO-000298 | GLNU3 | 49.9 | GLNU3-
Glendoe | SSE Generation Limited | Fort Augustus GSP |  | 99.9 | 0 | 99.9 |  | Built | Direct Connection | SHET | Hydro | a0l4L0000005imoQAA | PRO-000081 | FAUG | 99.9 | FAUG3X
Glendye Wind Farm | GLENDYE WIND FARM LIMITED | Glendye Wind Farm Substation | 1 | 0 | 124.8 | 124.8 | 2028-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005iyyQAA | PRO-001389-1 |  | 124.8
Glendye Wind Farm | GLENDYE WIND FARM LIMITED | Glendye Wind Farm Substation | 2 | 0 | 42 | 166.8 | 2034-04-30 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005iyyQAA | PRO-001389-2 |  | 0
Glenmore | AEUK WIND PROJECT II LTD | Edinbane 132/33kV Substation |  | 0 | 39.6 | 39.6 | 2034-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l8e0000012ggkAAA | PRO-004445 | EDIN3 | 0 | EDIN3-
Glenmoriston (part of the Moriston Cascade) | SSE Generation Limited | Glenmoriston GSP |  | 40 | 0 | 40 |  | Built | Direct Connection | SHET | Hydro | a0l4L0000005imqQAA | PRO-000083 | GLEN | 40 | GLEN5-
Glenmuckloch Pumped Storage | GLENMUCKLOCH PUMPED STORAGE HYDRO LIMITED | Glenmuckloch 132kV Substation |  | 0 | 210 | 210 | 2029-05-18 | Consents Approved | Direct Connection | SPT | Pump Storage | a0l4L0000005isIQAQ | PRO-000299 | GLMU1 | 210 | GLMU3-
Glenmuckloch Wind Farm | GLENMUCKLOCH RENEWABLE ENERGY LIMITED | Glenmuckloch 132/33kV |  | 0 | 33.6 | 33.6 | 2028-09-29 | Awaiting Consents | Direct Connection | SPT | Wind Onshore | a0l4L0000005iwRQAQ | PRO-000300 | GLMU3 | 33.6 | GLMU3-
Glenmuir Windfarm | BROCKWELL ENERGY LIMITED | Glenmuir Windfarm 132kV Substation |  | 0 | 80 | 80 | 2036-06-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l8e000001Ho33AAC | PRO-004058 |  | 0
Glennifer Road BESS | GPC 1119 Ltd | Neilston 400/275/132kV |  | 0 | 150 | 150 | 2027-10-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000011zs8AAA | PRO-003600 | NEIL1 | 150 | NEIL1-
Glenrothes Hybrid BESS & Solar PV | TAGENERGY DEVELOPMENT UK LIMITED | Conland Substation |  | 0 | 200 | 200 | 2031-10-30 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000TPJUAA4 | PRO-003252 | GLRO | 0 | GLRO3A
Glenshimmeroch Windfarm | ENERGYFARM UK GLENSHIMMEROCH LLP | SPT Margree collector substation |  | 0 | 45 | 45 | 2029-10-31 | Consents Approved | Direct Connection | SPT | Wind Onshore | a0l4L0000005in1QAA | PRO-000440 |  | 45
Glenside Farm BESS | GPC 1211 Ltd | Denny North 275/132kV |  | 0 | 400 | 400 | 2028-05-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000012eVgAAI | PRO-004368 | DENN2 | 400 | DENN2-
Glentaggart 150MW BESS | BROCKWELL ENERGY LIMITED | Redshaw 400kV |  | 0 | 150 | 150 | 2030-10-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000001HpfGAAS | PRO-004145 | REDS4 | 150 | REDS4-
Glentaggart 42MW BESS | GLENTAGGART WIND LIMITED | Glentaggart WF 33kV Substation |  | 0 | 42 | 42 | 2027-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005ik6QAA | PRO-001595 | REDS3 | 42 | REDS3A
Glentarken Wind Farm | SSE RENEWABLES SERVICES (UK) LIMITED | Killin GSP |  | 0 | 104 | 104 | 2031-11-30 | Scoping | Direct Connection | SHET | Wind Onshore | a0l8e00000120NhAAI | PRO-003627 | KIIN | 0 | KIIN3-
Gordonbush Wind Farm | SSE Generation Limited | Gordonbush GSP |  | 108 | 0 | 108 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005ipOQAQ | PRO-000518 | GORW | 108 | GORW3-
Graeme Road Solar & BESS | GREENTECH PROJECTS HOLDING UK LIMITED | Ryhall 400kV Substation |  | 0 | 550 | 550 | 2038-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012eoAAAQ | PRO-004375 | RYHA42 | 0 | RYHA4A
Grain | UNIPER UK LIMITED | Grain 400kV Substation |  | 1517 | 0 | 1517 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine);Reactive Compensation | a0l4L0000005im4QAA | PRO-000049 | GRAI4 | 1517 | GRAI41
Grain North Power Station | GRAIN NORTH POWER LIMITED | Grain North 132kV Substation |  | 0 | 49.99 | 49.99 | 2023-06-30 | Consents Approved | Direct Connection | NGET | Gas Reciprocating | a0l4L0000005j1SQAQ | PRO-001524 | GRAI1 | 49.99 | GRAI11
Grain South Power Station | Grain South Power Limited | Grain South 132kV Substation |  | 0 | 49.99 | 49.99 | 2023-10-30 | Consents Approved | Direct Connection | NGET | Gas Reciprocating | a0l4L0000005ivoQAA | PRO-000449 | GRAI1 | 49.99 | GRAI11
Grangemouth Hybrid BESS & Solar PV | TAGENERGY DEVELOPMENT UK LIMITED | Grangemouth 275/33kV |  | 0 | 300 | 300 | 2032-06-30 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000TPJeAAO | PRO-003254 | GRMO2 | 0 | GRMO2-
Grantham Generation | Aukera Energy Limited | Trent Valley South Connection Node C 400kV Substation |  | 0 | 700 | 700 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000TPFwAAO | PRO-003230 |  | 0
Grantham Solar Farm - RSL | SOUTH GRANTHAM ENERGY CENTRE LIMITED | Grantham 400KV |  | 0 | 810 | 810 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0lJ9000000PDt9IAG | PRO-005045 |  | 0
Great Coates BESS | BRUTON ONE BESS LIMITED | South Humber Bank 400kV Substation |  | 0 | 300 | 300 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f69rAAA | PRO-003960 | SHBA4 | 0 | SHBA41
Greater Gabbard Offshore Wind Farm | GREATER GABBARD OFFSHORE WINDS LIMITED | Gabbard 33/132kV Offshore Substation |  | 500 | 0 | 500 |  | Built | Direct Connection | OFTO | Wind Offshore | a0l4L0000005ioxQAA | PRO-000168 | LEIS1 | 500 | LEIS11
Green Hydrogen Solar Farm | GREEN HYDROGEN SOLAR FARM LIMITED | Sealand 400kV Substation |  | 0 | 500 | 500 | 2037-11-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000ew37AAA | PRO-003652 |  | 0
Green Volt Offshore Windfarm | FLOTATION ENERGY LIMITED | New Deer 400kV Substation | 1 | 0 | 300 | 300 | 2029-03-31 | Scoping | Direct Connection | SHET | Demand;Wind Offshore | a0l4L0000005idDQAQ | PRO-001469-1 |  | 300
Green Volt Offshore Windfarm | FLOTATION ENERGY LIMITED | New Deer 400kV Substation | 2 | 0 | 260 | 560 | 2033-10-31 | Scoping | Direct Connection | SHET | Demand;Wind Offshore | a0l4L0000005idDQAQ | PRO-001469-2 |  | 0
Greenburn Mixed Technology | REG GREENBURN LIMITED | Greenburn Mixed Technology 132kV Substation |  | 0 | 90 | 90 | 2027-10-31 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005ibVQAQ | PRO-001006 |  | 90
Greengage Farm | Renewable Energy Systems Limited | Biggleswade 400kV Substation |  | 0 | 500 | 500 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012jPcAAI | PRO-004675 | BIGG4 | 0 | BIGG41
Greenock Road BESS | Pulse Clean Energy Limited | Greenock Road 275kV Substation |  | 0 | 250 | 250 | 2033-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000012kkHAAQ | PRO-004761 | ERSK3 | 0 | ERSK3-
Grendon High Impact Green Energy Hub (HIGEH) 1 | TELIS ENERGY UK LIMITED | Grendon 400kV Substation |  | 0 | 1000 | 1000 | 2033-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;Nuclear;PV Array (Photo Voltaic/solar);Reactive Compensation;Wind Onshore | a0l8e0000010wVyAAI | PRO-002651 | GREN4 | 0 | GREN41
Grendon Solar & BESS | Green Hill Solar Farm Limited | Grendon 400kV Substation |  | 0 | 500 | 500 | 2029-07-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iihQAA | PRO-001568 | GREN4 | 500 | GREN41
Gresham House Cockenzie BESS | COCKENZIE STORAGE LIMITED | Cockenzie 275/33kV |  | 0 | 240 | 240 | 2026-07-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005iuFQAQ | PRO-002209 | COCK2 | 240 | COCK2-
Gresham House Connagill BESS | Gresham House Devco Pipeline Limited | Connagill 275kV Substation |  | 0 | 240 | 240 | 2030-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e000000TPSrAAO | PRO-003434 | CONN2 | 240 | CONN2J
Gresham House Dalmarnock BESS | Gresham House Devco Pipeline Limited | Dalmarnock 132/33kV |  | 0 | 300 | 300 | 2030-04-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000010wkCAAQ | PRO-002809 | DALM1 | 300 | DALM1-
Gresham House Gretna BESS | ALBUSIA LTD | Gretna 400/132kV |  | 0 | 400 | 400 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005il0QAA | PRO-002367 | GRNA1 | 0 | GRNA1-
Gresham House Kincardine BESS | FLAVUSIA LTD | Kincardine 275/132kV Substation |  | 0 | 300 | 300 | 2029-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005iyMQAQ | PRO-002368 | KINC2 | 300 | KINC2-
Gresham House Mossmoran BESS | Gresham House Devco Pipeline Limited | Mossmorran 132/33kV |  | 0 | 200 | 200 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005ituQAA | PRO-002395 | MOSM3 | 0 | MOSM3Q
Gresham House Rayleigh BESS | Gresham House Asset Management Limited | Rayleigh 400kV Substation |  | 0 | 480 | 480 | 2028-06-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iubQAA | PRO-002115 | RAYL4 | 480 | RAYL41
Greta III | Trent BESS III LIMITED | Drakelow 400kV Substation |  | 0 | 500 | 500 | 2029-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ikMQAQ | PRO-001803 | DRAK4 | 500 | DRAK41
Greta IV (b) | Greta IV Limited | North Anglia Connection Node B 400kV Substation |  | 0 | 500 | 500 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012guYAAQ | PRO-004499 |  | 0
Greta IV (c) | Greta IV Limited | North Anglia Connection Node B 400kV Substation |  | 0 | 500 | 500 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000012gudAAA | PRO-004500 |  | 0
Greta IV (d) | Greta IV Limited | North Anglia Connection Node B 400kV Substation |  | 0 | 500 | 500 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000012guiAAA | PRO-004501 |  | 0
Gretna Synchronous Compensation | GRETNA GRID SERVICES LIMITED | Gretna 400/132kV |  | 0 | 0 | 0 | 2024-09-30 | Consents Approved | Direct Connection | SPT | Reactive Compensation | a0l4L0000005ibsQAA | PRO-001444 | GRNA1 | 0 | GRNA1-
Griffin Wind Farm | GRIFFIN WIND FARM LIMITED | Griffin 132/33kV Substation |  | 188.6 | 0 | 188.6 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005ioyQAA | PRO-000169 | GRIF3 | 188.6 | GRIF36
Grimsby BESS | Shama BESS Limited | Grimsby West 400kV Substation |  | 0 | 500 | 500 | 2035-04-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000010wUCAAY | PRO-002633 | GRIW4 | 0 | GRIW41
Grimshader Wind Farm | RWE RENEWABLES UK ONSHORE WIND LIMITED | Grimshader Wind Farm Substation132 KV |  | 0 | 79.2 | 79.2 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l8e000000TPKNAA4 | PRO-003258 |  | 0
Grindon Grange | STARLIGHT ENERGY UK LIMITED | Norton East 400kV Substation |  | 0 | 240 | 240 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f8NqAAI | PRO-004028 | NORT4 | 0 | NORT41
Gunfleet Sands II Offshore Wind Farm | Gunfleet Sands II Ltd | Gunfleet Sands 33/132kV Offshore |  | 64 | 0 | 64 |  | Built | Direct Connection | NGET | Wind Offshore | a0l4L0000005iqiQAA | PRO-000229 | BRFO1 | 64 | BRFO11
Gunfleet Sands Offshore Wind Farm | GUNFLEET SANDS LIMITED | Gunfleet Sands 33/132kV Offshore |  | 99.9 | 0 | 99.9 |  | Built | Direct Connection | NGET | Wind Offshore | a0l4L0000005iqJQAQ | PRO-000224 | BRFO1 | 99.9 | BRFO11
Gwynt Alwen WF | WIND 2 LIMITED | North Wales connection Node A 400kV Substation |  | 0 | 108 | 108 | 2027-04-30 | Scoping | Direct Connection | NGET | Energy Storage System;Wind Onshore | a0l4L0000005ihMQAQ | PRO-001545 | TRAW1 | 108 | TRAW11
Gwynt Glas Offshore Wind Farm | GWYNT GLAS OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation |  | 0 | 300 | 300 | 2031-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005iiyQAA | PRO-001772 | ALVE4A | 0 | ALVE4A
Gwynt Glas Offshore Wind Farm 2 | GWYNT GLAS OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation |  | 0 | 1000 | 1000 | 2036-12-06 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005j1NQAQ | PRO-002480 | ALVE4A | 0 | ALVE4A
Gwynt Y Mor Offshore Wind Farm | GWYNT Y MOR OFFSHORE WIND FARM LIMITED | Gwynt y Mor 132/33kV Offshore Substation |  | 574 | 0 | 574 |  | Built | Direct Connection | OFTO | Wind Offshore | a0l4L0000005iq7QAA | PRO-000208 | BODE4 | 574 | BODE41
Hadyard Hill | SSE RENEWABLES WIND FARMS (UK) LIMITED | Maybole 132/33kV |  | 99.9 | 0 | 99.9 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005iozQAA | PRO-000170 | MAYB3 | 99.9 | MAYB3-
Hagshaw Energy Cluster Western Expansion | Spirebush Ltd | Spirebush 132kV Substation |  | 0 | 400 | 400 | 2028-07-01 | Awaiting Consents | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l4L0000005j1VQAQ | PRO-001692 | SPRB1 | 400 | SPRB1-
Hagshaw Hill Phase 1 | HAGSHAW HILL REPOWERING LTD | Coalburn 400/132kV |  | 0 | 30 | 30 | 2025-01-31 | Consents Approved | Direct Connection | SPT | Wind Onshore | a0l4L0000005io5QAA | PRO-000490 | COAL1 | 30 | COAL1-
Hagshaw Hill Phase 2 | HAGSHAW HILL REPOWERING LTD | Coalburn 400/132kV |  | 0 | 54 | 54 | 2025-01-31 | Consents Approved | Direct Connection | SPT | Wind Onshore | a0l4L0000005io6QAA | PRO-000514 | COAL1 | 54 | COAL1-
Hagshaw LDES | MITCHELL ENERGY LTD | Redshaw 132kV Substation. |  | 0 | 500 | 500 | 2036-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0lJ9000000PMvuIAG | PRO-005957 |  | 0
Hagshaw Wind Farm Repowering 2 | HAGSHAW REPOWERING 2 LTD | Hagshaw Repowering Phase 3 132kV |  | 0 | 84 | 84 | 2029-04-26 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l4L0000005iwUQAQ | PRO-002306 | HAGH3 | 84 | HAGH3-
Halbeath | Geocore Ltd | Halbeath 132kV Substation |  | 0 | 150 | 150 | 2029-07-31 | Scoping | Direct Connection | SPT | Demand;Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l4L0000005ivDQAQ | PRO-002266 |  | 150
Halfway Energy Park | DALRIADA RENEWABLES LIMITED | Coupar Angus GSP 400kV |  | 0 | 1000.29 | 1000.29 | 2035-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001HoBkAAK | PRO-004062 | COUA | 0 | COUA3-
Halsary Wind Farm | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Mybster 3 33kV Substation |  | 28.5 | 0 | 28.5 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005ipWQAQ | PRO-000189 | MYBS3 | 28.5 | MYBS3J
Hams Hall Green Energy Centre | HAMS HALL GREEN ENERGY LIMITED | Hams Hall 400kV Substation | 1 | 0 | 400 | 400 | 2028-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iirQAA | PRO-001765-1 | HAMH4 | 400 | HAMH41
Hams Hall Green Energy Centre | HAMS HALL GREEN ENERGY LIMITED | Hams Hall 400kV Substation | 2 | 0 | 625 | 1025 | 2032-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iirQAA | PRO-001765-2 | HAMH4 | 0 | HAMH41
Hare Craig Wind Farm | ENERGYFARM UK HARE CRAIG LLP | Hare Craig 33kV Substation |  | 0 | 46.2 | 46.2 | 2028-10-31 | Awaiting Consents | Direct Connection | SPT | Wind Onshore | a0l4L0000005iysQAA | PRO-000940 |  | 46.2
Hare Hill Repowering | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hare Hill Repowering 132/33kV Substation |  | 0 | 114 | 114 | 2029-10-31 | Scoping | Direct Connection | SPT | Wind Onshore | a0l8e000000f6A6AAI | PRO-003963 |  | 114
Hareshaw Rig Wind Farm | HARESHAW RIG WF LIMITED | Hopsrig Collector 132/33kV Substation |  | 0 | 40 | 40 | 2026-11-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005ipdQAA | PRO-000543 | HORI3 | 40 | HORI3A
Harestanes | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Harestanes 132/33kV | 1 | 125 | 0 | 125 |  | Built | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l4L0000005imbQAA | PRO-000064-1 | HARE3 | 125 | HARE3A
Harestanes | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Harestanes 132/33kV | 2 | 0 | 38.3 | 163.3 | 2028-03-31 | Under Construction/Commissioning | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l4L0000005imbQAA | PRO-000064-2 | HARE3 | 38.3 | HARE3A
Harestanes West Wind Farm | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Old Forest of Ae 33kV Substation |  | 0 | 56 | 56 | 2027-10-31 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005icnQAA | PRO-001075 | OFOA1 | 56 | OFOA1-
Harker Green Energy Centre | HARKER GREEN NG LIMITED | Harker 400kV Substation |  | 0 | 400 | 400 | 2028-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005igBQAQ | PRO-001709 | HARG4 | 400 | HARG41
Harker PV & BESS Sub | HARKER ENERGY PARK LIMITED | Harker 400kV Substation |  | 0 | 249.9 | 249.9 | 2037-11-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wSpAAI | PRO-002615 | HARG4 | 0 | HARG41
Harlaston | SSE DE SOLAR HOLDCO LIMITED | Harlaston 400kV Substation |  | 0 | 600 | 600 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f40fAAA | PRO-003814 |  | 0
Harting Rig Wind Farm | KYPE EXTENSION WIND FARM LIMITED | Kype Muir 132/33kV |  | 67.2 | 0 | 67.2 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005isKQAQ | PRO-000303 | KYPE3 | 67.2 | KYPE3-
Hartlepool | EDF ENERGY NUCLEAR GENERATION LIMITED | Hartlepool 275kV Substation |  | 1207 | -10 | 1197 | 2026-04-01 | Built | Direct Connection | NGET | Nuclear | a0l4L0000005ioKQAQ | PRO-000139 | HATL2 | 1197 | HATL21
Havbredey | HAVBREDEY LIMITED | NPI A 275/66kV Offshore Substation |  | 0 | 1500 | 1500 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l4L0000005iNUQAY | PRO-001628 |  | 0
Hawkhill BESS | Apatura Battery Ltd | Kincardine North 400kV Substation |  | 0 | 500 | 500 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000011ziLAAQ | PRO-003595 | KINC | 0 | KINC2-
Hawkwood Wind Farm | WILSON RENEWABLES IV LLP | Hawkwood Windfarm 33kV Substation |  | 0 | 34 | 34 | 2030-04-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l8e000000TPcUAAW | PRO-003450 |  | 34
Hawthorn BESS | REWE 8 LIMITED | Hawthorn Pit 400kV Substation |  | 0 | 200 | 200 | 2033-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l8e0000011xxtAAA | PRO-003492 | HAWP41 | 0 | HAWP41
Hawthorn Pit Green Energy Centre | INNOVA RENEWABLES LIMITED | Hawthorn Pit 400kV Substation |  | 0 | 1025 | 1025 | 2032-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ilDQAQ | PRO-002282 | HAWP41 | 0 | HAWP41
Heastabhal Wind Farm | RWE RENEWABLES UK ONSHORE WIND LIMITED | Heastabhal Wind Farm Substation 132 KV |  | 0 | 66 | 66 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l8e000000TPKIAA4 | PRO-003257 |  | 0
Heathland Wind Farm | EDF ENERGY RENEWABLES LIMITED | Heathland 132/33kV Substation |  | 0 | 80 | 80 | 2027-03-31 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l4L0000005igyQAA | PRO-001156 | HLND1 | 80 | HLND1-
Heckington Fen Solar Park | ECOTRICITY GENERATION LIMITED | Bicker Fen 400kV Substation |  | 0 | 400 | 400 | 2028-10-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ixuQAA | PRO-001903 | BICF4 | 400 | BICF41
Heysham 200MW BESS | Decerna Limited | Heysham 132kV Substation |  | 0 | 200 | 200 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000011ymWAAQ | PRO-003544 | HEYS1 | 0 | HEYS11
Heysham Green Energy Centre | INNOVA RENEWABLES LIMITED | Heysham 400kV Substation |  | 0 | 400 | 400 | 2028-10-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005igCQAQ | PRO-001710 | HEYS4 | 400 | HEYS41
Heysham Power Station | EDF ENERGY NUCLEAR GENERATION LIMITED | Heysham GSP |  | 2363 | 0 | 2363 |  | Built | Direct Connection | NGET | Nuclear | a0l4L0000005ioLQAQ | PRO-000140 | HEYS4 | 2363 | HEYS41
High Constellation Windfarm | HIGH CONSTELLATION WINDFARM LIMITED | Crossaig 132kV Substation |  | 0 | 50 | 50 | 2027-07-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005imKQAQ | PRO-000416 | CRSS1 | 50 | CRSS1J
High Marnham (Tertiary) | ENSO GREEN HOLDINGS K LIMITED | High Marnham 400kV Substation |  | 0 | 57 | 57 | 2029-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ip9QAA | PRO-000531 | HIGM4 | 57 | HIGM41
High Marnham 400 | ENSO GREEN HOLDINGS LIMITED | High Marnham 400kV Substation | 1 | 0 | 400 | 400 | 2033-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ivvQAA | PRO-002194-1 | HIGM4 | 0 | HIGM41
High Marnham 400 | ENSO GREEN HOLDINGS LIMITED | High Marnham 400kV Substation | 2 | 0 | 600 | 1000 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ivvQAA | PRO-002194-2 | HIGM4 | 0 | HIGM41
High Marnham BESS | JG PEARS GRID CONNECTION LIMITED | High Marnham 400kV Substation |  | 0 | 500 | 500 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TPcjAAG | PRO-003452 | HIGM4 | 0 | HIGM41
High Marnham Solar Farm | ANESCO LIMITED | High Marnham 400kV Substation |  | 0 | 99.9 | 99.9 | 2031-10-31 | Scoping | Direct Connection | NGET | PV Array (Photo Voltaic/solar) | a0l4L0000005iY7QAI | PRO-001845 | HIGM4 | 0 | HIGM41
High Mathernock Battery Storage | Forestry Finance Ltd | Devol Moor 132kV Substation |  | 0 | 334 | 334 | 2029-10-17 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005ivGQAQ | PRO-002273 | DEVM1 | 334 | DEVM1-
Highland BESS | Apatura Battery Ltd | Highland BESS 132kV Substation |  | 0 | 120 | 120 | 2030-05-30 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e000000f4PIAAY | PRO-003845 | BOAG | 120 | BOAG3-
Highland Wind Farm | HIGHLAND WIND FARM LIMITED | Highland Wind Farm 132/33kV substation |  | 0 | 168 | 168 | 2029-09-18 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l8e0000012ezHAAQ | PRO-004390 |  | 168
Highview Hunterston East Cryobattery | HVS SITECO LTD | Hunterston East 400kV |  | 0 | 200 | 200 | 2027-10-31 | Consents Approved | Direct Connection | SPT | Demand;Energy Storage System;Reactive Compensation | a0l4L0000005iYkQAI | PRO-001348 | HUNE4 | 200 | HUNE4-
Hill Street Solar PV/BESS Station | HILL STREET SHELFCO 1 LIMITED | Staffordshire Connection Node A 400kV Substation |  | 0 | 800 | 800 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000exlgAAA | PRO-003744 |  | 0
Hinkley Point B | EDF ENERGY NUCLEAR GENERATION LIMITED | Hinkley Point 400kV Substation |  | 0 | 0 | 0 |  | Built | Direct Connection | NGET | Nuclear | a0l4L0000005ioMQAQ | PRO-000141 | HINP4 | 0 | HINP41
Hinkley Point C | NNB GENERATION COMPANY (HPC) LIMITED | Hinkley Point 400kV Substation | 1 | 0 | 1670 | 1670 | 2029-03-31 | Scoping | Direct Connection | NGET | Nuclear | a0l4L0000005idVQAQ | PRO-001674-1 | SHUR4 | 1670 | SHUR41
Hinkley Point C | NNB GENERATION COMPANY (HPC) LIMITED | Hinkley Point 400kV Substation | 2 | 0 | 1670 | 3340 | 2030-07-31 | Scoping | Direct Connection | NGET | Nuclear | a0l4L0000005idVQAQ | PRO-001674-2 | SHUR4 | 1670 | SHUR41
Hipsey BESS | KONA ASSET 2 LIMITED | Dunstable 400kV Substation |  | 0 | 240 | 240 | 2032-10-29 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000010x1mAAA | PRO-003051 | SUND4 | 0 | SUND41
Hirfynydd and Mynydd Drumaur | EDF ENERGY RENEWABLES LIMITED | Swansea North 400kV Substation |  | 0 | 180 | 180 | 2029-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l4L0000005iw9QAA | PRO-001899 | SWAN41 | 180 | SWAN41
Hirwaun Power Station | HIRWAUN POWER LIMITED | Rhigos 400kV Substation |  | 0 | 299 | 299 | 2023-09-30 | Under Construction/Commissioning | Direct Connection | NGET | OCGT (Open Cycle Gas Turbine) | a0l4L0000005isPQAQ | PRO-000309 | RHIG4 | 299 | RHIG41
Hockliffe GEC (Ethos Green) | HOCKLIFFE GREEN ENERGY CENTRE LTD | Dunstable 400kV Substation |  | 0 | 850 | 850 | 2032-10-29 | Scoping | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l8e000000ViEzAAK | PRO-004342 | SUND4 | 0 | SUND41
Holdsworth Road | MAS 002 LIMITED | Bradford West 275kV Substation |  | 0 | 500 | 500 | 2036-10-24 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iMOQAY | PRO-002338 | BRAW2 | 0 | BRAW21
Hollandmey Renewable Energy Development | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Hollandmey Renewable Energy Development132/33kV Substation |  | 0 | 49.5 | 49.5 | 2029-05-01 | Consents Approved | Direct Connection | SHET | Wind Onshore | a0l4L0000005ibYQAQ | PRO-001094 | HOME1 | 49.5
Hope Battery Storage | Firma Vogt Solar Ltd | Blyth 400kV Substation |  | 0 | 400 | 400 | 2036-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005j8QQAQ | PRO-002520 | BLYT4 | 0 | BLYT41
Hopsrig Wind Farm | HOPSRIG WIND FARM LIMITED | Hopsrig Collector 132/33kV Substation |  | 0 | 48 | 48 | 2027-10-31 | Consents Approved | Direct Connection | SPT | Wind Onshore | a0l4L0000005isfQAA | PRO-000318 | HORI3 | 48 | HORI3A
Hornsea Power Station 1A | HORNSEA 1 LIMITED | Hornsea Platform 1A Offshore Substation |  | 400 | 0 | 400 |  | Built | Direct Connection | NGET | Wind Offshore | a0l4L0000005isUQAQ | PRO-000315 | KILL4 | 400 | KILL41
Hornsea Power Station 1B | HORNSEA 1 LIMITED | Hornsea Platform 1B Offshore Substation |  | 400 | 0 | 400 |  | Built | Direct Connection | NGET | Wind Offshore | a0l4L0000005ispQAA | PRO-000331 | KILL4 | 400 | KILL41
Hornsea Power Station 1C | HORNSEA 1 LIMITED | Hornsea Platform 1C Offshore Substation |  | 400 | 0 | 400 |  | Built | Direct Connection | NGET | Wind Offshore | a0l4L0000005isqQAA | PRO-000332 | KILL4 | 400 | KILL41
Hornsea Power Station 2A | BREESEA LIMITED | Hornsea Platform 2A Offshore Substation |  | 440 | 0 | 440 |  | Built | Direct Connection | NGET | Wind Offshore | a0l4L0000005isrQAA | PRO-000333 | KILL4 | 440 | KILL41
Hornsea Power Station 2B | SOUNDMARK WIND LIMITED | Hornsea Platform 2B Offshore Substation |  | 440 | 0 | 440 |  | Built | Direct Connection | NGET | Wind Offshore | a0l4L0000005issQAA | PRO-000334 | KILL4 | 440 | KILL41
Hornsea Power Station 2C | SONNINGMAY WIND LIMITED | Hornsea Power Station 2C Offshore platform Substation |  | 440 | 0 | 440 |  | Built | Direct Connection | NGET | Wind Offshore | a0l4L0000005istQAA | PRO-000335 | KILL4 | 440 | KILL41
Hornsea Power Station 3 | ORSTED HORNSEA PROJECT THREE (UK) LIMITED | Norwich Main 400kV Substation | 1 | 0 | 2250 | 2250 | 2026-10-01 | Consents Approved | Direct Connection | NGET | Energy Storage System;Wind Offshore | a0l4L0000005in7QAA | PRO-000434-1 | NORM42 | 2250 | NORM41
Hornsea Power Station 3 | ORSTED HORNSEA PROJECT THREE (UK) LIMITED | Norwich Main 400kV Substation | 2 | 0 | 750 | 3000 | 2028-12-31 | Consents Approved | Direct Connection | NGET | Energy Storage System;Wind Offshore | a0l4L0000005in7QAA | PRO-000434-2 | NORM41 | 750 | NORM41
Hornsea Power Station 4 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 2 | 0 | 1100 | 2600 | 2029-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005in6QAA | PRO-000435-2 | CREB4 | 1100 | CREB41
Hornsea Power Station 4 | ORSTED HORNSEA PROJECT FOUR LIMITED | Creyke Beck 400kV Substation | 1 | 0 | 1500 | 1500 | 2028-10-30 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005in6QAA | PRO-000435-1 | CREB4 | 1500 | CREB41
Housham PV & BESS | FOSSE GREEN ENERGY LIMITED | Navenby 400kV Substation |  | 0 | 240 | 240 | 2033-05-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ivBQAQ | PRO-002254 | BICF4 | 0 | BICF41
Humber Gateway Offshore Wind Farm | RWE RENEWABLES UK HUMBER WIND LIMITED | Humber Gateway 33/132kV Offshore Substation |  | 220 | 0 | 220 |  | Built | Direct Connection | OFTO | Wind Offshore | a0l4L0000005iqDQAQ | PRO-000214 | HEDO2 | 220 | HEDO21
Hunterston | EDF ENERGY NUCLEAR GENERATION LIMITED | Hunterston 400/132kV |  | 0 | 0 | 0 |  | Built | Direct Connection | SPT | Nuclear | a0l4L0000005ioOQAQ | PRO-000143 | HUER4 | 0 | HUER4-
Hunterston Battery Storage Facility | FLEXIBLEGRIDPOWER2 LTD | Ayrshire Grid 400kV Substation |  | 0 | 200 | 200 | 2025-08-20 | Scoping | Direct Connection | SPT | Energy Storage System;Reactive Compensation | a0l4L0000005igzQAA | PRO-001155 | AYRS4 | 200 | AYRS4-
Hunterston Energy Storage Facility | ENERGYGRIDPOWER2 LTD | Ayrshire Grid 400kV Substation |  | 0 | 200 | 200 | 2025-08-27 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005iNgQAI | PRO-001644 | AYRS4 | 200 | AYRS4-
Hunterston Hydrogen | STATKRAFT HYDROGEN UK HOLDING LIMITED | Hunterston 400/132kV |  | 0 | 5 | 5 | 2033-10-31 | Scoping | Direct Connection | SPT | Hydrogen | a0l8e000000f65UAAQ | PRO-003957 | HUER4 | 0 | HUER4-
Hunterston PARC BESS | Pulse Clean Energy Limited | Hunterston 400/132kV |  | 0 | 250 | 250 | 2033-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000f4mlAAA | PRO-003865 | HUER4 | 0 | HUER4-
Hunterston Wind Farm | GALILEO 01 LIMITED | Hunterston Farm 132/33kV |  | 0 | 70 | 70 | 2030-08-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l8e000000TP9yAAG | PRO-003165 | HUNF3 | 70 | HUNF3-
Huntingdon High Impact Energy Hub 1 | TELIS ENERGY UK LIMITED | West Anglia Connection Node H 400kVSubstation |  | 0 | 1000 | 1000 | 2034-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;Nuclear;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e0000012hmsAAA | PRO-004507 |  | 0
Hurlet Battery | P-FREQUENCY LTD | Neilston 400kV Substation |  | 0 | 400 | 400 | 2033-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0lJ9000000blJJIAY | PRO-004790 |  | 0
Hurst BESS | FIRSTWAY SOLAR LTD | North Kent Connection Node C 400kV Substation |  | 0 | 212 | 212 | 2038-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000012eydAAA | PRO-004388 |  | 0
Hurst BESS | LUMINOUS ENERGY GROUP LIMITED | North Kent Connection Node C 400kV Substation |  | 0 | 320 | 320 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001HxQoAAK | PRO-004249 |  | 0
INTOG 2 | CERULEAN WINDS LIMITED | Thorntonloch 400kV Substation |  | 0 | 1400 | 1400 | 2032-06-30 | Scoping | Direct Connection | SPT | Wind Offshore | a0l8e0000012hnbAAA | PRO-004514 |  | 0
IPC Grid Tremorfa | IPC GRID CONNECTION LIMITED | Imperial Park B 400kV Substation |  | 0 | 1000 | 1000 | 2036-12-06 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000eybgAAA | PRO-003765 | IMPP4 | 0 | IMPP41
Icewind Blyth | KARI ENERGY LIMITED | Blyth 400kV Substation |  | 0 | 1000 | 1000 | 2031-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005iwTQAQ | PRO-001717 | BLYT4 | 0 | BLYT41
Icewind Connah's Quay | KARI ENERGY LIMITED | Connah's Quay 400kV Substation |  | 0 | 1000 | 1000 | 2033-11-01 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005igIQAQ | PRO-001719 | CONQ4 | 0 | CONQ41
Icewind Hawthorn Pit | KARI ENERGY LIMITED | Hawthorn Pit 400kV Substation |  | 0 | 1000 | 1000 | 2031-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005igHQAQ | PRO-001718 | HAWP41 | 0 | HAWP41
Icewind Hinkley Point | KARI ENERGY LIMITED | Hinkley Point 400kV Substation |  | 0 | 1000 | 1000 | 2028-11-01 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005igJQAQ | PRO-001720 | HINP4 | 1000 | HINP41
Immingham | VPI IMMINGHAM LLP | Humber Refinery 400kV Substation |  | 1218 | 0 | 1218 |  | Built | Direct Connection | NGET | Energy Storage System;Gas Reciprocating | a0l4L0000005im7QAA | PRO-000053 | HUMR4 | 1218 | HUMR41
Immingham | VPI IMMINGHAM LLP | Humber Refinery 400kV Substation | 1 | 0 | 50 | 1268 | 2027-07-01 | Scoping | Direct Connection | NGET | Energy Storage System;Gas Reciprocating | a0l4L0000005im7QAA | PRO-000053-1 | HUMR4 | 50 | HUMR41
Immingham | VPI IMMINGHAM LLP | Humber Refinery 400kV Substation | 2 | 0 | 50 | 1318 | 2029-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;Gas Reciprocating | a0l4L0000005im7QAA | PRO-000053-2 | HUMR4 | 50 | HUMR41
Imperial Park BESS | KONA ASSET 4 LIMITED | Imperial Park B 400kV Substation |  | 0 | 225 | 225 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000012063AAA | PRO-003615 | IMPP4 | 0 | IMPP41
Inch Cape Offshore Wind Farm Platform 1 | INCH CAPE OFFSHORE LIMITED | Cockenzie 400/275kV |  | 0 | 540 | 540 | 2026-02-21 | Consents Approved | Direct Connection | SPT | Wind Offshore | a0l4L0000005it3QAA | PRO-000348 | COCK4 | 540 | COCK4Q
Inch Cape Offshore Wind Farm Platform 2 | INCH CAPE OFFSHORE LIMITED | Cockenzie 400/275kV |  | 0 | 540 | 540 | 2026-02-21 | Consents Approved | Direct Connection | SPT | Wind Offshore | a0l4L0000005it4QAA | PRO-000349 | COCK4 | 540 | COCK4Q
Indian Queens | GRIDMOVE LTD | Indian Queens 400kV Substation |  | 0 | 437 | 437 | 2031-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ix9QAA | PRO-001676 | INDQ4 | 0 | INDQ41
Indian Queens | INDIAN QUEENS POWER LIMITED | Indian Queens 400kV Substation |  | 140 | 0 | 140 |  | Built | Direct Connection | NGET | OCGT (Open Cycle Gas Turbine) | a0l4L0000005iZDQAY | PRO-001372 | INDQ4 | 140 | INDQ41
Indian Queens | PIVOTED POWER LLP | Indian Queens 400kV Substation |  | 0 | 47.5 | 47.5 | 2024-07-30 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005iqfQAA | PRO-000225 | INDQ4 | 47.5 | INDQ41
Indian Queens Energy Centre | IQ ENERGY CENTRE LIMITED | Indian Queens 400kV Substation |  | 0 | 47.5 | 47.5 | 2025-05-31 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iZCQAY | PRO-001371 | INDQ4 | 47.5 | INDQ41
Innerwick BESS | Rabbit Marketing Ltd | Branxton 132kV |  | 0 | 170 | 170 | 2028-07-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000010wlyAAA | PRO-002828 | BRNX1 | 170 | BRNX4-
Invergarry (part of the Garry Cascade) | SSE Generation Limited | Invergarry 132kV Substation |  | 20 | 0 | 20 |  | Built | Direct Connection | SHET | Hydro | a0l4L0000005ip0QAA | PRO-000171 | INGA1 | 20 | INGA1Q
Inveroykel Wind Farm | RWE RENEWABLES UK SWINDON LIMITED | Inveroykel Wind Farm 132kV |  | 0 | 191.4 | 191.4 | 2031-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l8e0000010wmDAAQ | PRO-002831 |  | 0
Iron Acton | IRON ACTON GREEN LIMITED | Iron Acton 275kV Substation | 3 | 0 | 20.6 | 120 | 2027-09-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iodQAA | PRO-000491-3 | IROA2 | 20.6 | IROA21
Iron Acton | HD000ACT LTD | Iron Acton 275kV Substation | 1 | 0 | 49.9 | 49.9 | 2025-06-30 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005inOQAQ | PRO-000455-1 | IROA2 | 49.9 | IROA21
Iron Acton | HD000ACT LTD | Iron Acton 275kV Substation | 2 | 0 | 70.1 | 120 | 2028-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005inOQAQ | PRO-000455-2 | IROA2 | 70.1 | IROA21
Iron Acton | IRON ACTON GREEN LIMITED | Iron Acton 275kV Substation | 1 | 49.9 | 0 | 49.9 |  | Built | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iodQAA | PRO-000491-1 | IROA2 | 49.9 | IROA21
Iron Acton | IRON ACTON GREEN LIMITED | Iron Acton 275kV Substation | 2 | 49.5 | 0 | 99.4 |  | Built | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iodQAA | PRO-000491-2 | IROA2 | 99.4 | IROA21
Ironbridge | IGP SOLAR 16 LIMITED | Ironbridge 400kV Substation |  | 0 | 600 | 600 | 2032-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iNVQAY | PRO-001629 | IRON4 | 0 | IRON41
Ironbridge Green Energy Centre | IRONBRIDGE GREEN NG LIMITED | Ironbridge 400kV Substation |  | 0 | 400 | 400 | 2029-10-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005igDQAQ | PRO-001711 | IRON4 | 400 | IRON41
Isenau Eight | Isenau Energy Storage Resources Eight Limited | Hawthorn Pit GSP |  | 0 | 249 | 249 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TP9oAAG | PRO-003164 | HAWP41 | 0 | HAWP41
Isenau Five | Isenau Energy Storage Resources Five Limited | Tealing 132kV Substation |  | 0 | 50 | 50 | 2029-06-30 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e000000TPCEAA4 | PRO-003190 | TEAL1 | 50 | TEAL1-
Isenau Four | Isenau Energy Storage Resources Four Limited | Corriemoillie 132/33kV Substation |  | 0 | 200 | 200 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000010xhIAAQ | PRO-003086 | CORI1 | 0 | CORI1J
Isenau Two | Isenau Energy Storage Resources Two Limited | Tealing 132kV Substation |  | 0 | 249.9 | 249.9 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000010xhwAAA | PRO-003091 | TEAL1 | 0 | TEAL1-
Isle of Man Offshore Wind Farm | Mooir Vannin Offshore Wind Farm Limited | Penwortham 400kV Substation |  | 0 | 1320 | 1320 | 2037-10-30 | Scoping | Direct Connection | NGET | Wind Offshore | a0l8e000000ex1KAAQ | PRO-003698 | PEWO41 | 0 | PEWO41
Iver | Juniper Energy Limited | Iver 275kV Substation |  | 0 | 49.9 | 49.9 | 2027-10-29 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ieNQAQ | PRO-001141 | IVER22 | 49.9 | IVER22
J102A Oldbury BESS | RWE RENEWABLES UK SOLAR AND STORAGE LIMITED | Severn Connection Node A 132kV Substation |  | 0 | 99.9 | 99.9 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000eyu0AAA | PRO-003784 |  | 0
J212 High Grove Solar | RWE RENEWABLES UK SOLAR AND STORAGE LIMITED | Necton 400kV Substation |  | 0 | 720 | 720 | 2031-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L000002yQWkQAM | PRO-002542 | NECT4 | 0 | NECT41
JBM Solar 12 - Shrewsbury Solar | JBM SOLAR PROJECTS 12 LTD | Shrewsbury GSP |  | 0 | 49.99 | 49.99 | 2024-10-30 | Scoping | Direct Connection | NGET | PV Array (Photo Voltaic/solar) | a0l4L0000005iiCQAQ | PRO-001146 | SHRE4 | 49.99 | SHRE4A
JBM Solar 13 - Melksham | JBM SOLAR PROJECTS 13 LIMITED | Melksham 400kV Substation |  | 0 | 49.99 | 49.99 | 2025-11-14 | Scoping | Direct Connection | NGET | Thermal | a0l4L0000005iogQAA | PRO-000495 | MELK4 | 49.99 | MELK41
JG Pears | JG PEARS GRID CONNECTION LIMITED | High Marnham 275kV Substation | 1 | 13 | 0 | 13 |  | Built | Direct Connection | NGET | CHP (Combined Heat and Power);Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l4L0000005irEQAQ | PRO-000250-1 | HIGM4 | 13 | HIGM41
JG Pears | JG PEARS GRID CONNECTION LIMITED | High Marnham 275kV Substation | 3 | 0 | 420 | 450 | 2033-10-31 | Scoping | Direct Connection | NGET | CHP (Combined Heat and Power);Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l4L0000005irEQAQ | PRO-000250-3 | HIMB2 | 0 | HIMB21
JG Pears | JG PEARS GRID CONNECTION LIMITED | High Marnham 275kV Substation | 2 | 0 | 17 | 30 | 2025-11-30 | Under Construction/Commissioning | Direct Connection | NGET | CHP (Combined Heat and Power);Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l4L0000005irEQAQ | PRO-000250-2 | HIGM4 | 17 | HIGM41
Jackdaw BESS | Downing Renewable Developments LLP | Leeds North Connection Node B 400kV Substation |  | 0 | 249.9 | 249.9 | 2036-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000ViJqAAK | PRO-004351 |  | 0
Jersey Farm BESS | CSE39 LIMITED | Jersey Farm 400kV Substation |  | 0 | 400 | 400 | 2032-10-25 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005iyRQAQ | PRO-002264 | EXET4 | 0 | EXET41
Jubilee Farm | STARLIGHT ENERGY UK LIMITED | Jubilee Farm 275kV Substation |  | 0 | 200 | 200 | 2034-08-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L000002yQX9QAM | PRO-002545 | HIGM2 | 0 | HIGM41
KX Alpha 1 Iron Acton | KXP ALPHA I LIMITED | Severn Connection Node A 400kv Substation |  | 0 | 99 | 99 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000ew2iAAA | PRO-003647 |  | 0
KX Alpha 2 Iron Acton | KXP ALPHA II LIMITED | Severn Connection Node A 400kv Substation |  | 0 | 99 | 99 | 2038-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000ew2nAAA | PRO-003648 |  | 0
KX Alpha 3 Iron Acton | KXP ALPHA III LIMITED | Severn Connection Node A 400kv Substation |  | 0 | 99.9 | 99.9 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000ew2sAAA | PRO-003649 |  | 0
KXP ALPHA 3 AYR BESS | KXP ALPHA III LIMITED | KXP Alpha 3 Ayr BESS 275kV Substation |  | 0 | 99 | 99 | 2037-10-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000ewYQAAY | PRO-003672 | AYR-2 | 0 | AYR-2Q
KXP Alpha 1 Little Horsted | KXP ALPHA I LIMITED | Sussex and Romney Connection Node A 400kV Substation |  | 0 | 99.9 | 99.9 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000eykzAAA | PRO-003776 |  | 0
KXP Alpha 2 Little Horsted | KXP ALPHA II LIMITED | Sussex and Romney Connection Node A 400kV Substation |  | 0 | 99.9 | 99.9 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000eyl4AAA | PRO-003777 |  | 0
KXP Alpha 3 Little Horsted | KXP ALPHA III LIMITED | Sussex and Romney Connection Node A 400kV Substation |  | 0 | 99.9 | 99.9 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000eyl5AAA | PRO-003778 |  | 0
KXP Alpha One | KXP ALPHA I LIMITED | Fawley 132kV Substation |  | 0 | 99.99 | 99.99 | 2036-10-24 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iyWQAQ | PRO-002348 | FAWL1 | 0 | FAWL11
KXP Alpha Three | KXP ALPHA III LIMITED | Fawley 132kV Substation |  | 0 | 99.99 | 99.99 | 2036-10-24 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iyDQAQ | PRO-002351 | FAWL1 | 0 | FAWL11
KXP Alpha Two | KXP ALPHA II LIMITED | Fawley 132kV Substation |  | 0 | 99.99 | 99.99 | 2036-10-24 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ikuQAA | PRO-002349 | FAWL1 | 0 | FAWL11
Keadby II | KEADBY GENERATION LIMITED | Keadby 400kV Substation |  | 893 | 0 | 893 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005isQQAQ | PRO-000310 | KEAD4 | 893 | KEAD41
Keadby North Power Station | KEADBY GENERATION LIMITED | Keadby 400kV Substation |  | 0 | 892 | 892 | 2031-10-31 | Awaiting Consents | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005iZMQAY | PRO-001980 | KEAD4 | 0 | KEAD41
Keadby South Power Station | KEADBY GENERATION LIMITED | Keadby 400kV Substation |  | 755 | 155 | 910 | 2034-04-30 | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005iYvQAI | PRO-001962 | KEAD4 | 755 | KEAD41
Kearsley | PIVOTED POWER LLP | Kearsley 400kV Substation |  | 0 | 49.9 | 49.9 | 2028-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005iudQAA | PRO-001064 | KEAR4 | 49.9 | KEAR41
Kearsley North Green Energy Centre | INNOVA RENEWABLES LIMITED | Kearsley GSP |  | 0 | 400 | 400 | 2028-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iyfQAA | PRO-001793 | KEAR4 | 400 | KEAR41
Kedrum Solar Farm | Rosside Energy Limited | Blackhillock 275kV Substation |  | 0 | 150 | 150 | 2030-05-30 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e000000TPc0AAG | PRO-003444 | BLHI2 | 150 | BLHI2A
Keith 132 Greener Grid Park | KEITH STORAGE SOLUTIONS LIMITED | Keith 1 132/33kV GSP Substation | 2 | 0 | 48 | 48 | 2025-05-31 | Consents Approved | Direct Connection | SHET | Energy Storage System | a0l4L0000005ifTQAQ | PRO-001129-2 | KEIT | 48 | KEIT3A
Keith 132 Greener Grid Park | KEITH STORAGE SOLUTIONS LIMITED | Keith 1 132/33kV GSP Substation | 1 | 0 | 0 | 0 |  | Built | Direct Connection | SHET | Energy Storage System | a0l4L0000005ifTQAQ | PRO-001129-1 | KEIT | 0 | KEIT3A
Keith BESS Station | IB VOGT UK LTD | Blackhillock substation |  | 0 | 400 | 400 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000011z3KAAQ | PRO-003565 | BLHI | 0 | BLHI1J
Keith Hill Wind Farm | DIAMOND WIND LIMITED | Keith Hill 33kV |  | 4.5 | 0 | 4.5 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005irFQAQ | PRO-000251 | KEIH3 | 4.5 | KEIH3-
Keith Solar Farm | KEITH SOLAR PV LIMITED | Keith Solar Farm 275kV Substation |  | 0 | 150 | 150 | 2028-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010waMAAQ | PRO-002699 | KEIT2 | 150 | KEIT2Q
Kellas Wind Farm | E Power Limited | Kellas Wind Farm 132kV Substation |  | 0 | 90 | 90 | 2030-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005iuZQAQ | PRO-002271 |  | 90
Kellhead | GREENTECH PROJECTS HOLDING UK LIMITED | Gretna 400/132kV |  | 0 | 200 | 200 | 2037-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar) | a0lJ9000000POaJIAW | PRO-006055 |  | 0
Kelloe Mains | TBC 003 LIMITED | Kelloe Mains 400kV Substation |  | 0 | 400 | 400 | 2029-11-22 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005itTQAQ | PRO-002425 |  | 400
Kemsley | PIVOTED POWER LLP | Kemsley 400kV Substation |  | 49.9 | 0 | 49.9 |  | Built | Direct Connection | NGET | Energy Storage System | a0l4L0000005iqkQAA | PRO-000235 | KEMS41 | 49.9 | KEMS41
Kennoxhead Wind Farm | ORSTED ONSHORE UK LIMITED | Kennoxhead GSP |  | 0 | 112 | 112 | 2028-04-01 | Consents Approved | Direct Connection | SPT | Wind Onshore | a0l4L0000005isgQAA | PRO-000319 | KENE | 112 | KENE3-
Kennoxhead Wind Farm Extension | KENNOXHEAD WIND FARM LIMITED | Middlemuir Wind Farm Collector Substation |  | 60 | 0 | 60 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005inZQAQ | PRO-000482 | MIDM | 60 | MIDM3-
Kilbraur North Wind Farm | EDF ENERGY RENEWABLES LIMITED | Kilbraur Wind Farm Substation |  | 0 | 79.2 | 79.2 | 2031-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l8e000000f6hCAAQ | PRO-003987 |  | 0
Kilbraur Wind Farm | KILBRAUR WIND ENERGY LIMITED | Kilbraur Wind Farm Substation |  | 67 | 0 | 67 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005iqgQAA | PRO-000226 |  | 67
Kilgallioch Wind Farm and Kilgallioch Wind Farm Extension - Turbines | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Kilgallioch 275kV Substation | 1 | 228 | 0 | 228 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005imcQAA | PRO-000065-1 | KILG2 | 228 | KILG2-
Kilgallioch Wind Farm and Kilgallioch Wind Farm Extension - Turbines | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Kilgallioch 275kV Substation | 2 | 0 | 46 | 274 | 2025-04-08 | Consents Approved | Direct Connection | SPT | Wind Onshore | a0l4L0000005imcQAA | PRO-000065-2 | KILG2 | 46 | KILG2-
Killingholme | UNIPER UK LIMITED | Killingholme 400kV Substation |  | 619 | 0 | 619 |  | Built | Direct Connection | NGET | OCGT (Open Cycle Gas Turbine) | a0l4L0000005ioTQAQ | PRO-000148 | KILL4 | 619 | KILL41
Killingholme BESS | O&G Solar (SPV 47) Limited | Killingholme 400kV Substation |  | 0 | 249.9 | 249.9 | 2035-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f4xDAAQ | PRO-003893 | KILL4 | 0 | KILL41
Killoch BESS | Renewable Energy Systems Limited | Killoch BESS 275kV substation |  | 0 | 150 | 150 | 2030-09-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000001Hq2FAAS | PRO-004171 |  | 150
Kilmarnock BESS | NORIKER POWER LTD | Kilmarnock South 400/275kV |  | 0 | 350 | 350 | 2025-07-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005iwSQAQ | PRO-001836 | KILS2 | 350 | KILS2-
Kilmarnock South Battery Storage | Weaver Power Limited | Kilmarnock South 275/33kV |  | 0 | 500 | 500 | 2027-04-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005ikQQAQ | PRO-001809 | KILS2 | 500 | KILS2-
Kilmorack (part of the Beauly Cascade) | SSE Generation Limited | Kilmorack GSP |  | 20 | 0 | 20 |  | Built | Direct Connection | SHET | Hydro | a0l4L0000005ip1QAA | PRO-000172 | KION | 20 | KION5-
Kincardine Battery Storage Facility | SPECTRUMRESERVE LTD | Fife Grid Services Facility 275kV Substation |  | 0 | 200 | 200 | 2026-03-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005iORQAY | PRO-000856 | FIGS2 | 200 | FIGS2-
Kincardine Energy Storage Facility | ENERGYGRIDPOWER3 LTD | Fife Grid Services Facility 275kV Substation |  | 0 | 200 | 200 | 2026-03-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005iP9QAI | PRO-001653 | FIGS2 | 200 | FIGS2-
Kingfisher Farm | REWE 6 LIMITED | Monk Fryston 275kV Substation |  | 0 | 200 | 200 | 2036-06-02 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L000002yQZyQAM | PRO-002555 | MONF21 | 0 | MONF21
Kingsnorth | ENSO GREEN HOLDINGS G LIMITED | Kingsnorth 132kV Substation |  | 0 | 120 | 120 | 2028-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iZ5QAI | PRO-001360 | KINO1 | 120 | KINO11
Kingsnorth BESS NP | NORIKER POWER LTD | Kingsnorth 400kV Substation |  | 0 | 500 | 500 | 2032-10-29 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000010wXVAAY | PRO-002665 | KINO4 | 0 | KINO41
Kingsnorth Power Station | Q-Energy Sustainable Investments Ltd | Kingsnorth 400kV Substation |  | 0 | 400 | 400 | 2032-10-29 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012kfbAAA | PRO-004718 | KINO4 | 0 | KINO41
Kinmuck PV and BESS Station | KINMUCK ENERGY STORAGE LIMITED | Peterhead GSP |  | 0 | 105 | 105 | 2027-05-31 | Awaiting Consents | Direct Connection | SHET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ievQAA | PRO-001700 | PEHE | 105 | PEHE1-
Kinoulton Solar & BESS | GREENTECH PROJECTS HOLDING UK LIMITED | Stoke Bardolph 400kV Substation |  | 0 | 500 | 500 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012hwCAAQ | PRO-004560 | STOB4 | 0 | STOB41
Kirkan Wind Farm | KIRKAN WIND FARM LIMITED | Corriemoillie 2 400/132kV Substation |  | 0 | 81.6 | 81.6 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l8e0000012g8WAAQ | PRO-004401 |  | 0
Kirkby | HD001KIR LTD | Kirkby 275kV Substation | 1 | 0 | 49.9 | 49.9 | 2025-09-30 | Consents Approved | Direct Connection | NGET | Gas Reciprocating | a0l4L0000005iceQAA | PRO-001084-1 | KIBY2 | 49.9 | KIBY21
Kirkby | HD001KIR LTD | Kirkby 275kV Substation | 2 | 0 | 7.1 | 57 | 2037-10-30 | Scoping | Direct Connection | NGET | Gas Reciprocating | a0l4L0000005iceQAA | PRO-001084-2 | KIBY2 | 0 | KIBY21
Kirkby (Tertiary) | PIVOTED POWER LLP | Kirkby GSP (ENW) |  | 0 | 57 | 57 | 2027-08-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005icfQAA | PRO-001083 | KIBY2 | 57 | KIBY21
Kirkby Green Energy Centre | INNOVA RENEWABLES LIMITED | Kirkby 275kV Substation |  | 0 | 400 | 400 | 2028-10-30 | Scoping | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iPZQAY | PRO-001869 | KIBY2 | 400 | KIBY21
Kirkcaldy BESS | Apatura Battery Ltd | Kirkcaldy BESS 132kV Substation |  | 0 | 100 | 100 | 2032-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000exlbAAA | PRO-003743 | GLNI | 0 | GLNI3-
Kirklands Farm BESS | Apatura Battery Ltd | Westfield 132/33kV |  | 0 | 200 | 200 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000011y2mAAA | PRO-003499 | WFIE3 | 0 | WFIE3-
Kirkton Wind Farm | Kirkton Wind Farm Ltd | Connagill 275kV Substation |  | 0 | 60 | 60 | 2028-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005ikRQAQ | PRO-001811 | CONN2 | 60 | CONN2J
Knockcronal Wind Farm | Knockcronal Wind Farm Limited | Knockcronal Wind Farm 33kV Substation |  | 0 | 59.4 | 59.4 | 2029-10-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005ikKQAQ | PRO-001801 |  | 59.4
Knocknagael BESS | FIELD KNOCKNAGAEL LTD | Knocknagael 132kV Substation |  | 0 | 200 | 200 | 2030-10-31 | Awaiting Consents | Direct Connection | SHET | Energy Storage System | a0l8e000000exNNAAY | PRO-003712 | KNOC1 | 200 | KNOC1J
Knockodhar Wind Farm | REG KNOCKODHAR LIMITED | Mark Hill 275/132kV |  | 0 | 120 | 120 | 2028-04-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005inYQAQ | PRO-000483 | MAHI1 | 120 | MAHI1-
Knockton Wind Farm | ORSTED ONSHORE UK LIMITED | Alyth 400kV Substation |  | 0 | 130.2 | 130.2 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l8e0000011yY5AAI | PRO-003524 |  | 0
Kynachan | Geocore Ltd | Errochty 132kV Substation |  | 0 | 300 | 300 | 2035-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000011y7JAAQ | PRO-003502 | ERRO1 | 0 | ERRO1A
Kype Muir | Onpath Energy Limited (KYPE MUIR WIND FARM) LIMITED | Coalburn 400/132kV |  | 88.4 | 0 | 88.4 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005isVQAQ | PRO-000316 | COAL1 | 88.4 | COAL1-
L48 BESS Burnside | Lower 48 Energy BESS Limited | New deer 275kV |  | 0 | 200 | 200 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000010xRpAAI | PRO-003063 | NEDE2 | 0 | NEDE4J
L48 BESS Dams of Craigie | Lower 48 Energy BESS Limited | L48 BESS Dams of Craigie |  | 0 | 220 | 220 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f4ZKAAY | PRO-003853 |  | 0
L48 BESS Glen App | Lower 48 Energy BESS Limited | L48 BESS Glen App |  | 0 | 200 | 200 | 2028-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000010xJ5AAI | PRO-003058 |  | 200
LGB300 | LG-B-300 | LGB300 400KV Substation |  | 0 | 600 | 600 | 2031-07-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e000000f52SAAQ | PRO-003907 |  | 0
Lacey's Farm BESS | Bluestone Energy Ltd | South Anglia Connection Node C 400kV Substation |  | 0 | 924 | 924 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001HomMAAS | PRO-004095 |  | 0
Lackenby PV & BESS Station | IB VOGT UK LTD | Lackenby 275kV Substation |  | 0 | 240 | 240 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000011yrKAAQ | PRO-003551 | LACK21 | 0 | LACK21
Ladyfield Renewable Energy Park | Ladyfield Renewable Energy Park Ltd | Creag Dhubh 275/132/33kV |  | 0 | 68 | 68 | 2029-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l4L0000005ia0QAA | PRO-002002 | CRDH1 | 68 | CRDH1J
Lagrae Battery Storage | LAGRAE BATTERY STORAGE LIMITED | Glenmuckloch 132kV Substation |  | 0 | 400 | 400 | 2036-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000001HrhiAAC | PRO-004214 | GLMU3 | 0 | GLMU3-
Lairdmannoch Energy Park | LAIRDMANNOCH ENERGY PARK LIMITED | Lairdmannoch Energy Park 132kV substation |  | 0 | 100 | 100 | 2030-06-28 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e000000eytlAAA | PRO-003781 |  | 100
Lairg II Wind Farm | ENERGYFARM UK LAIRG LLP | Lairg GSP |  | 0 | 50 | 50 | 2026-10-31 | Consents Approved | Direct Connection | SHET | Wind Onshore | a0l4L0000005ibkQAA | PRO-001434 | LAIR | 50 | LAIR3-
Lakeside Energy Drax | LAKESIDE ENERGY STORAGE LIMITED | Drax 132kV Substation |  | 99.9 | 0 | 99.9 |  | Built | Direct Connection | NGET | Energy Storage System | a0l4L0000005ifzQAA | PRO-001522 | DRAX1 | 99.9 | DRAX11
Laleham | Juniper Energy Limited | Laleham 275kV Substation |  | 0 | 49.9 | 49.9 | 2025-11-01 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iueQAA | PRO-001063 | LALE2 | 49.9 | LALE21
Lambeeth 240MW | ECODEV GROUP LTD | Pembroke 400kV Substation |  | 0 | 240 | 240 | 2037-12-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000012eEBAAY | PRO-004361 | PEMB4 | 0 | PEMB41
Lambloch BESS | Apatura Battery Ltd | Lambloch BESS 275kV Substation |  | 0 | 500 | 500 | 2029-05-28 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000011zPwAAI | PRO-003583 | BUSB2 | 500 | BUSB2-
Lamford Hill | Benbrack Wind Farm Limited | Lamford Hill 132kV/33kV Substation |  | 0 | 20 | 20 | 2026-10-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005izCQAQ | PRO-001481 |  | 20
Lanarkshire BESS | CARLTON POWER LIMITED | Strathaven 400/275kV |  | 0 | 500 | 500 | 2027-04-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005ivkQAA | PRO-002183 | STHA4 | 500 | STHA4A
Land at Leitholm | NOVENTUM POWER SOLAR 6 LIMITED | Eccles 400/132kV |  | 0 | 49.9 | 49.9 | 2031-07-31 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001HxadAAC | PRO-004265 | ECCL1 | 0 | ECCL1-
Landulph | PIVOTED POWER LLP | Landulph 400kV Substation |  | 0 | 49.9 | 49.9 | 2022-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005ifRQAQ | PRO-001131 | LAND4 | 49.9 | LAND41
Langage | EP LANGAGE LIMITED | Langage 400kV Substation |  | 905 | 0 | 905 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005itvQAA | PRO-000200 | LAGA4 | 905 | LAGA41
Langage 400 | ENSO GREEN HOLDINGS LIMITED | Langage 400kV Substation | 3 | 0 | 100 | 400 | 2038-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005itlQAA | PRO-002192-3 | LAGA4 | 0 | LAGA41
Langage 400 | ENSO GREEN HOLDINGS LIMITED | Langage 400kV Substation | 2 | 0 | 100 | 300 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005itlQAA | PRO-002192-2 | LAGA4 | 0 | LAGA41
Langage 400 | ENSO GREEN HOLDINGS LIMITED | Langage 400kV Substation | 1 | 0 | 200 | 200 | 2036-12-19 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005itlQAA | PRO-002192-1 | LAGA4 | 0 | LAGA41
Langage Battery Storage | LANGAGE ENERGY PARK LIMITED | Langage 400kV Substation |  | 0 | 249 | 249 | 2031-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iaCQAQ | PRO-002016 | LAGA4 | 0 | LAGA41
Langage Farm | Langage 10 Renewables Limited | Langage 400kV Substation |  | 0 | 1000 | 1000 | 2037-12-19 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L000002yQaSQAU | PRO-002561 | LAGA4 | 0 | LAGA41
Lapwing Fen II | Eclipse Power Networks Limited | Walpole 132kV Substation |  | 0 | 249.6 | 249.6 | 2029-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iZZQAY | PRO-001995 | WALP1 | 249.6 | WALP11
Larks Green Farm BESS | VOLTALIA UK LTD | Iron Acton 132kV Substation |  | 0 | 100 | 100 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f4Z0AAI | PRO-003849 | IROA1 | 0 | IROA11
Lawfield and Branxton Energy Park | Renewable Energy Systems Limited | Lawfield and Branxton Energy Park 400kV Substation |  | 0 | 400 | 400 | 2028-06-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005iu5QAA | PRO-002229 | BRNX4 | 400 | BRNX4-
Leadenham High Impact Green Energy Hub | TELIS ENERGY UK LIMITED | Trent Valley South Connection Node A 400k |  | 0 | 1000 | 1000 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;Nuclear;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e000000f40kAAA | PRO-003815 | BICF4 | 0 | BICF41
Learielaw Energy Storage | Learielaw Energy Storage Ltd | Broxburn 132/33kV |  | 0 | 100 | 100 | 2028-10-31 | Scoping | Direct Connection | SPT | Demand;Energy Storage System | a0l4L0000005jA7QAI | PRO-002531 | BROX3 | 100 | BROX3-
Learney BESS | IGP SOLAR 22 LIMITED | Learney Teed 132kV |  | 0 | 50 | 50 | 2032-10-01 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e000000TPI2AAO | PRO-003241 |  | 0
Lebanon Farm 2 BESS | Bluestone Energy Ltd | Warley 275kV Substation |  | 0 | 275 | 275 | 2030-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f5djAAA | PRO-003939 | WARL2 | 275 | WARL21
Legacy 400 | ENSO GREEN HOLDINGS LIMITED | Legacy 400kV Substation |  | 0 | 400 | 400 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l4L0000005iznQAA | PRO-002193 | LEGA41 | 0 | LEGA41
Legacy Green Energy Centre | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 3 | 0 | 225 | 1025 | 2033-10-28 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005idLQAQ | PRO-001662-3 | LEGA41 | 0 | LEGA41
Legacy Green Energy Centre | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 1 | 0 | 400 | 400 | 2026-10-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005idLQAQ | PRO-001662-1 | LEGA41 | 400 | LEGA41
Legacy Green Energy Centre | LEGACY GREEN ENERGY LIMITED | Legacy 400kV Substation | 2 | 0 | 400 | 800 | 2032-10-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005idLQAQ | PRO-001662-2 | LEGA41 | 0 | LEGA41
Legacy Tertiary Connection | HD639LEG LIMITED | Legacy 400kV Substation |  | 0 | 57 | 57 | 2024-08-31 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005izMQAQ | PRO-001171 | LEGA41 | 57 | LEGA41
Leighton Buzzard | Leighton Buzzard 10 Renewables Limited | West Anglia Connection Node A 400kV Substation |  | 0 | 1000 | 1000 | 2034-10-31 | Scoping | Direct Connection | NGET | Demand;PV Array (Photo Voltaic/solar) | a0l8e000000TPR0AAO | PRO-003411 | LEIB4 | 0 | LEIB4A
Leslie 200MW BESS | Apatura Battery Ltd | Leslie 200MW BESS 275kV Substation |  | 0 | 200 | 200 | 2032-05-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000001201MAAQ | PRO-003609 |  | 0
Lessnessock Energy Park | RENEWCO POWER LIMITED | Lessnessock |  | 0 | 114 | 114 | 2037-10-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0lJ9000000PDrNIAW | PRO-005033 |  | 0
Letch Beck Energy Park | Renewable Energy Systems Limited | Norton East 400kV Substation |  | 0 | 600 | 600 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L000002yQZUQA2 | PRO-002550 | NORT4 | 0 | NORT41
Lethans Wind Farm | BANKS RENEWABLES (LETHANS WIND FARM) LIMITED | Lethans 132kV Substation |  | 0 | 132 | 132 | 2027-06-30 | Consents Approved | Direct Connection | SPT | Wind Onshore | a0l4L0000005iZ9QAI | PRO-001367 | LETH1 | 132 | LETH1-
Lethans Wind Farm Extension | Banks Renewables (Lethans East Wind Farm) Limited | Lethans 132kV Substation |  | 0 | 85 | 85 | 2027-10-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l8e0000011ywSAAQ | PRO-003553 | LETH1 | 85 | LETH1-
Lethen Wind Farm | FRED. OLSEN RENEWABLES LIMITED | Lethen Wind Farm 132/33kV Substation |  | 0 | 114 | 114 | 2033-12-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005ivMQAQ | PRO-002307 |  | 0
Lightsource Auchans | Lightsource Renewable UK Development Limited | Lightsource Auchans 400kV Substation |  | 0 | 400 | 400 | 2033-10-28 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000f6fpAAA | PRO-003985 |  | 0
Lightsource Bagots Farm | Lightsource Renewable UK Development Limited | Drakelow 400kV Substation |  | 0 | 240 | 240 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;Wind Onshore | a0lJ9000000blMwIAI | PRO-004829 | DRAK4 | 0 | DRAK41
Lightsource Berthlwyd | Lightsource Renewable UK Development Limited | Mid Wales Connection Node A |  | 0 | 240 | 240 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0lJ9000000blP7IAI | PRO-004858 |  | 0
Lightsource Bodelwyddan | Lightsource Renewable UK Development Limited | Bodelwyddan 400kV Substation |  | 0 | 300 | 300 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f4rrAAA | PRO-003877 | BODE4 | 0 | BODE41
Lightsource Bramford PV & BESS | Lightsource Renewable UK Development Limited | South Anglia Connection Node A 400kV Substation |  | 0 | 240 | 240 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f42RAAQ | PRO-003835 | BRFO4 | 0 | BRFO41
Lightsource Braybrooke | Lightsource Renewable UK Development Limited | West Anglia Connection Node F 400kV Substation |  | 0 | 240 | 240 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f6pcAAA | PRO-003989 | BRAY4 | 0
Lightsource Enderby PV+BESS | Lightsource Renewable UK Development Limited | Derbyshire Connection Node B 400kV Substation |  | 0 | 240 | 240 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f4dhAAA | PRO-003854 |  | 0
Lightsource Ferryside PV | Lightsource Renewable UK Development Limited | South Wales West Connection Node C 400kV |  | 0 | 240 | 240 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000eyX9AAI | PRO-003761 |  | 0
Lightsource Folly Farm | Lightsource Renewable UK Development Limited | Severn Connection Node A 400kv Substation |  | 0 | 240 | 240 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;Wind Onshore | a0lJ9000000blMXIAY | PRO-004825 |  | 0
Lightsource Grendon PV+BESS | Lightsource Renewable UK Development Limited | West Anglia Connection Node C 400kV Substation |  | 0 | 240 | 240 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000exlWAAQ | PRO-003742 |  | 0
Lightsource Hawthorne Pit | Lightsource Renewable UK Development Limited | Hawthorn Pit 400kV Substation |  | 0 | 240 | 240 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f4PDAAY | PRO-003844 | HAWP41 | 0 | HAWP41
Lightsource Jubilee Farm | Lightsource Renewable UK Development Limited | Jubilee Farm 275kV Substation |  | 0 | 240 | 240 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0lJ9000000blLeIAI | PRO-004815 | HIGM2 | 0 | HIGM41
Lightsource Lower Frankton | Lightsource Renewable UK Development Limited | Cheshire Connection Node A 400kV Substation |  | 0 | 240 | 240 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f4e1AAA | PRO-003859 |  | 0
Lightsource Marston Vale 240MW PV+BESS | Lightsource Renewable UK Development Limited | Marston Vale 400kV Substation |  | 0 | 240 | 240 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f6OSAAY | PRO-003981 | MARV41 | 0 | MARV41
Lightsource Middleton | Lightsource Renewable UK Development Limited | Middleton 400KV Substation |  | 0 | 240 | 240 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0lJ9000000blLtIAI | PRO-004817 | MIDL4 | 0 | MIDL41
Lightsource Mon Solar 2 | LIGHTSOURCE SPV 204 LIMITED | Wylfa South 400kV Substation |  | 0 | 120 | 120 | 2037-11-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L000002yQb6QAE | PRO-002563 | WYLS4 | 0 | WYLS41
Lightsource Mount Annan BESS | Lightsource Renewable UK Development Limited | Chapelcross 132/33kV |  | 0 | 150 | 150 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000010x0KAAQ | PRO-003034 | CHAP3 | 0 | CHAP3-
Lightsource New Eggborough | Lightsource Renewable UK Development Limited | Leeds North Connection Node B 400kV Substation |  | 0 | 240 | 240 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;Wind Onshore | a0lJ9000000blMDIAY | PRO-004821 |  | 0
Lightsource Newchurch PV/BESS | Lightsource Renewable UK Development Limited | East Kent connection node A 400kV Substation |  | 0 | 240 | 240 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000exRuAAI | PRO-003717 | CANT4 | 0 | CANT41
Lightsource Norton East PV | Lightsource Renewable UK Development Limited | Norton East 400kV Substation |  | 0 | 240 | 240 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000exlRAAQ | PRO-003741 | NORT4 | 0 | NORT41
Lightsource Offerton | Lightsource Renewable UK Development Limited | Wearside Connection Node B 2 400kV Substation |  | 0 | 240 | 240 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0lJ9000000blL5IAI | PRO-004808 |  | 0
Lightsource Overton | Lightsource Renewable UK Development Limited | North Humber Connection Node E 400kV Substation |  | 0 | 240 | 240 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f69hAAA | PRO-003958 | OVER2 | 0 | OVER21
Lightsource Patford Bridge | Lightsource Renewable UK Development Limited | Derbyshire Connection Node I 400kV Substation |  | 0 | 240 | 240 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0lJ9000000blL0IAI | PRO-004807 |  | 0
Lightsource Pyworthy | Lightsource Renewable UK Development Limited | West Country Connection Node A 400kV Substation |  | 0 | 300 | 300 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001HodQAAS | PRO-004089 |  | 0
Lightsource Rhigos BESS | Lightsource Renewable UK Development Limited | South Wales West Connection Node A 400kV Substation |  | 0 | 300 | 300 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000exSdAAI | PRO-003726 | RHIG4 | 0 | RHIG41
Lightsource Shipley PV | Lightsource Renewable UK Development Limited | Sussex and Romney Connection Node B 400kV Substation |  | 0 | 240 | 240 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000exIeAAI | PRO-003707 |  | 0
Lightsource Threepwood | Lightsource Renewable UK Development Limited | Gala North 400/132kV Substation |  | 0 | 150 | 150 | 2030-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000001Hq20AAC | PRO-004168 | GALN1 | 150 | GALN1Q
Lightsource Willington | Lightsource Renewable UK Development Limited | Willington 400kV Substation |  | 0 | 240 | 240 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;Wind Onshore | a0lJ9000000blMSIAY | PRO-004824 | WILL1 | 0 | WILL11
Lightsource Yaxley PV | Lightsource Renewable UK Development Limited | North Anglia Connection Node E 400kV Substation |  | 0 | 240 | 240 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f4ArAAI | PRO-003837 | YAXL4 | 0 | YAXL41
Lightsourcebp Amlwch BESS and Hydrogen | Lightsource Renewable UK Development Limited | Wylfa South 400kV Substation |  | 0 | 600 | 600 | 2037-10-30 | Scoping | Direct Connection | NGET | Demand;Energy Storage System | a0lJ9000000blOxIAI | PRO-004856 | WYLS4 | 0 | WYLS41
Lightsourcebp Wakeleys Wind and BESS | Lightsource Renewable UK Development Limited | Wakeleys 400kV |  | 0 | 240 | 240 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;Wind Onshore | a0lJ9000000blMhIAI | PRO-004827 |  | 0
Lime Tree Energy Park | BNRG LANGMEAD LIMITED | Friston 400kV Substation |  | 0 | 249.9 | 249.9 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001HpUiAAK | PRO-004121 | FRIS41 | 0 | FRIS41
Limekiln | Limekiln Extension Limited | Limekilns 132/33kV substation |  | 0 | 106 | 106 | 2024-04-30 | Consents Approved | Direct Connection | SHET | Wind Onshore | a0l4L0000005itVQAQ | PRO-000515 |  | 106
Lincs Offshore Wind Farm | LINCS WIND FARM LIMITED | Lincs 33/132kV Offshore Substation |  | 265 | 0 | 265 |  | Built | Direct Connection | OFTO | Wind Offshore | a0l4L0000005iqEQAQ | PRO-000215 | WALP4 | 265 | WALP41
Lisa's Battery Storage | POTENCIA ENERGY LIMITED | Mybster 3 132/33kV Substation |  | 0 | 47 | 47 | 2030-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e000000TPNRAA4 | PRO-003280 | MYBS3 | 47 | MYBS3J
Lister Battery (formerly Lister Drive) | LISTER BATTERY LTD | Lister Drive 275kV Substation |  | 0 | 57 | 57 | 2023-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iz9QAA | PRO-001088 | LISD21 | 57 | LISD21
Lister Drive 275kV | LISTER DRIVE SOLUTIONS LIMITED | Lister Drive 275kV Substation |  | 0 | 0 | 0 |  | Built | Direct Connection | NGET | Reactive Compensation | a0l4L0000005iOdQAI | PRO-001248 | LISD21 | 0 | LISD21
Lister Drive Shaw | Carnegie (BES) Ltd | Lister Drive 275kV Substation |  | 0 | 57 | 57 | 2025-05-01 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005izrQAA | PRO-001342 | LISD21 | 57 | LISD21
Little Barford | RWE Generation UK Plc | Eaton Socon 400kV Substation |  | 740 | 0 | 740 |  | Built | Direct Connection | NGET | Energy Storage System | a0l4L0000005inpQAA | PRO-000125 | EASO41 | 740 | EASO41
Little Harrowden | Little Harrowden 10 Renewables Limited | West Anglia Connection Node F 400kV Substation |  | 0 | 1000 | 1000 | 2034-10-31 | Scoping | Direct Connection | NGET | Demand;PV Array (Photo Voltaic/solar) | a0l8e000000TPRPAA4 | PRO-003416 |  | 0
Little Horsted | CSE34 LIMITED | Little Horsted GSP |  | 0 | 49.9 | 49.9 | 2031-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iuAQAQ | PRO-002214 | LHOR4 | 0 | LHOR4A
Little Horsted | Lightsource Renewable UK Development Limited | Little Horsted 400kV Substation |  | 0 | 57 | 57 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000exRkAAI | PRO-003715 | LHOR4 | 0 | LHOR4A
Little Horsted Energy Park | ELEMENTS GREEN DEVELOPMENT LTD | Sussex and Romney Connection Node A 400kV Substation |  | 0 | 1260 | 1260 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e00000120NSAAY | PRO-003624 |  | 0
Littlebrook GEC (Ethos Green) | LITTLEBROOK GREEN ENERGY CENTRE LTD | Rowdown 400kV Substation |  | 0 | 400 | 400 | 2031-10-22 | Awaiting Consents | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l8e000000f5cXAAQ | PRO-003938 | ROWD42 | 0 | ROWD42
Littlewoods Wind Farm | EDF ENERGY RENEWABLES LIMITED | Littlewoods Wind Farm 132/33kV Substation |  | 0 | 68.4 | 68.4 | 2029-09-28 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005iNoQAI | PRO-001825 |  | 68.4
Llanwern 3 | FUTURE ENERGY LLANWERN LIMITED | Whitson 275kV Substation |  | 0 | 95 | 95 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001HxwDAAS | PRO-004317 | WHSO22 | 0 | WHSO22
Llanwern Phase 1 | GREENFIELDS (T) LIMITED | Whitson 275kV Substation |  | 0 | 95 | 95 | 2028-10-01 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iwPQAQ | PRO-001124 | WHSO21 | 95 | WHSO21
Llanwern Phase 2 | FUTURE ENERGY LLANWERN LIMITED | Whitson 275kV Substation |  | 0 | 190 | 190 | 2028-10-01 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iwOQAQ | PRO-001125 | WHSO22 | 190 | WHSO22
Llywelyn Extension Offshore Wind Farm | Renantis UK Limited | Pembroke 400kV Substation |  | 0 | 1000 | 1000 | 2036-12-06 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005iySQAQ | PRO-002406 | PEMB4 | 0 | PEMB41
Llywelyn Floating Offshore Wind Farm | Renantis UK Limited | Pembroke 400kV Substation |  | 0 | 300 | 300 | 2029-03-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005idPQAQ | PRO-001668 | PEMB4 | 300 | PEMB41
Llŷr Floating Wind | Llŷr Floating Wind Limited | Pembroke 400kV Substation |  | 0 | 200 | 200 | 2028-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005iZNQAY | PRO-001981 | PEMB4 | 200 | PEMB41
Loch Fearna Pumped Storage | FEARNA PSH LIMITED | Loch Fearna Pumped Storage 132/18kV |  | 0 | 300 | 300 | 2032-10-28 | Scoping | Direct Connection | SHET | Pump Storage | a0l8e0000010wOJAAY | PRO-002569 |  | 0
Loch Kemp PSH Phase 2 | STATERA ENERGY LIMITED | Loch Kemp 275kV substation |  | 0 | 300 | 300 | 2030-10-31 | Scoping | Direct Connection | SHET | Pump Storage | a0l4L0000005iwWQAQ | PRO-002285 |  | 300
Loch Kemp Pumped Storage | LOCH KEMP STORAGE LIMITED | Loch Kemp 275kV substation |  | 0 | 300 | 300 | 2027-10-31 | Scoping | Direct Connection | SHET | Pump Storage | a0l4L0000005ix2QAA | PRO-001559 |  | 300
Loch Liath Wind Farm | LOCH LIATH WIND FARM LIMITED | Loch Liath 132/33kV Substation |  | 0 | 99 | 99 | 2035-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005idSQAQ | PRO-001671 |  | 0
Loch Luichart Extension II | BLUEBELL WIND FARM LIMITED | Loch Luichart Extension II Substation |  | 0 | 36 | 36 | 2024-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005inUQAQ | PRO-000487 |  | 36
Loch na Cathrach Pumped Storage Hydro | STATKRAFT HIGHLANDS PSH LIMITED | Red John 275kV Switching Station | 1 | 0 | 450 | 450 | 2029-04-30 | Consents Approved | Direct Connection | SHET | Pump Storage | a0l4L0000005iqQQAQ | PRO-000570-1 | REJO2 | 450
Loch na Cathrach Pumped Storage Hydro | STATKRAFT HIGHLANDS PSH LIMITED | Red John 275kV Switching Station | 2 | 0 | 100 | 550 | 2030-10-31 | Consents Approved | Direct Connection | SHET | Pump Storage | a0l4L0000005iqQQAQ | PRO-000570-2 | REJO2 | 100
Loch nan Eun PSH | GLENDOE STORAGE LIMITED | Loch Nan Eun 275/18kV |  | 0 | 900 | 900 | 2029-10-31 | Scoping | Direct Connection | SHET | Pump Storage | a0l4L0000005ic7QAA | PRO-002063 | LHEU2 | 900
Lochay (Part of Killin Cascade Hydro Scheme) | SSE Generation Limited | Lochay GSP |  | 0 | 6.2 | 51.2 | 2027-01-01 | Under Construction/Commissioning | Direct Connection | SHET | Hydro | a0l4L0000005ip2QAA | PRO-000174 | LOCH | 51.2 | LOCH5J
Lochay (Part of Killin Cascade Hydro Scheme) | SSE Generation Limited | Lochay GSP |  | 0 | 6.2 | 51.2 | 2027-01-01 | Under Construction/Commissioning | Direct Connection | SHET | Hydro | a0l4L0000005ip2QAA | PRO-000174 | LOCH | 51.2 | LOCH5J
Lochay (Part of Killin Cascade Hydro Scheme) | SSE Generation Limited | Lochay GSP |  | 45 | 0 | 45 |  | Built | Direct Connection | SHET | Hydro | a0l4L0000005ip2QAA | PRO-000174 | LOCH | 45 | LOCH5J
Lochay (Part of Killin Cascade Hydro Scheme) | SSE Generation Limited | Lochay GSP |  | 45 | 0 | 45 |  | Built | Direct Connection | SHET | Hydro | a0l4L0000005ip2QAA | PRO-000174 | LOCH | 45 | LOCH5J
Lochluichart | LZN LIMITED | Corriemoillie 132kV Substation |  | 69 | 0 | 69 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005iqhQAA | PRO-000227 | CORI3 | 69 | CORI3-
Lochore BESS | LOCHORE BESS LTD | Westfield 132/33kV |  | 0 | 900 | 900 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000011xxFAAQ | PRO-003483 | WFIE1 | 0 | WFIE1A
Loganhead Windfarm | LOGANHEAD WF LIMITED | Hopsrig Collector 132/33kV Substation |  | 0 | 36 | 36 | 2027-10-31 | Awaiting Consents | Direct Connection | SPT | Wind Onshore | a0l4L0000005isNQAQ | PRO-000306 | HORI3 | 36 | HORI3A
London Array Offshore Wind Farm | LONDON ARRAY LIMITED | London Array 33/150kV Offshore Substations |  | 630 | 0 | 630 |  | Built | Direct Connection | OFTO | Wind Offshore | a0l4L0000005ipcQAA | PRO-000201 | CLEH4 | 630 | CLEH41
Long Stratton 400 | ENSO GREEN HOLDINGS X LIMITED | North Anglia Connection Node A 400kV |  | 0 | 400 | 400 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0lJ9000000blPvIAI | PRO-004868 |  | 0
Long Stratton BESS | FIELD DEVCO LTD | North Anglia Connection Node A 400kV |  | 0 | 400 | 400 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0lJ9000000blOTIAY | PRO-004850 |  | 0
Long Stratton PV & BESS Station | IGP INTERNATIONAL PROSPECTING LIMITED | Long Stratton 400kV |  | 0 | 500 | 500 | 2031-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ivJQAQ | PRO-002297 | EACS4 | 0
Longcroft Energy Park | Renewable Energy Systems Limited | Gala North 400/132kV Substation |  | 0 | 156 | 156 | 2030-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l8e0000010wTTAAY | PRO-002623 | GALN1 | 156 | GALN1Q
Longfield Solar | LONGFIELD SOLAR ENERGY FARM LIMITED | Bulls Lodge 400kV Substation | 2 | 0 | 0 | 500 | 2028-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ivqQAA | PRO-001053-2 | BULL4 | 0 | BULL41
Longfield Solar | LONGFIELD SOLAR ENERGY FARM LIMITED | Bulls Lodge 400kV Substation | 1 | 0 | 500 | 500 | 2027-12-15 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ivqQAA | PRO-001053-1 | BULL4 | 500 | BULL41
Longmorn Energy Park | ELGIN ENERGY ES CO LIMITED | Blackhillock 275kV Substation |  | 0 | 300 | 300 | 2031-08-15 | Scoping | Direct Connection | SHET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wcrAAA | PRO-002727 | BLHI2 | 0 | BLHI2A
Lorg Extension Wind Farm | RWE RENEWABLES UK ONSHORE WIND LIMITED | Lorg Wind Farm 132/32kV |  | 0 | 33 | 33 | 2029-08-13 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005iynQAA | PRO-002430 | LORG3 | 33 | LORG3-
Lorg Wind Farm | RWE RENEWABLES UK ONSHORE WIND LIMITED | Lorg Wind Farm 132/32kV |  | 0 | 69.5 | 69.5 | 2027-04-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005ikXQAQ | PRO-000153 | LORG3 | 69.5 | LORG3-
Lovedean (Tertiary) | LOVEDEAN GREEN LIMITED | Lovedean 400kV Substation |  | 0 | 57 | 57 | 2029-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005inXQAQ | PRO-000484 | LOVE4 | 57 | LOVE41
Lovedean Greener Grid Park | STATKRAFT UK LTD | Lovedean 400kV Substation |  | 0 | 49.9 | 49.9 | 2028-06-01 | Scoping | Direct Connection | NGET | Energy Storage System;Reactive Compensation | a0l4L0000005iPLQAY | PRO-001855 | LOVE4 | 49.9 | LOVE41
Low Harker BESS | Energi Generation 14 Ltd | Harker 400kV Substation |  | 0 | 400 | 400 | 2037-11-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f4nUAAQ | PRO-003873 | HARG4 | 0 | HARG41
Lower Pool Energy Park | Renewable Energy Systems Limited | Derbyshire Connection Node B 400kV Substation |  | 0 | 600 | 600 | 2030-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000011zQGAAY | PRO-003586 | ENDE4 | 600 | ENDE41
Ludgershall - Bicester Solar Farm PVDP | SolarFour Ltd | Chiltern Connection Node C 400kV Substation |  | 0 | 500 | 500 | 2038-11-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001HpehAAC | PRO-004140 |  | 0
Luichart (part of the Conon Cascade) | SSE Generation Limited | Luichart GSP |  | 34 | 0 | 34 |  | Built | Direct Connection | SHET | Hydro | a0l4L0000005ip3QAA | PRO-000175 | LUIC | 34 | LUIC5K
Lynefield BESS | WINDEL GRID 1 LIMITED | Borders Connection Node A 400kV Substation |  | 0 | 200 | 200 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000011yx6AAA | PRO-003555 | BLYT4 | 0 | BLYT41
M74 West Wind Farm | RENEWCO POWER LIMITED | M74 West Wind Farm 132kV |  | 0 | 249.9 | 249.9 | 2028-10-27 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l4L0000005itxQAA | PRO-002398 |  | 249.9
MALTBY DEV. | Firma Vogt Solar Ltd | Thurcroft 275kV Substation |  | 0 | 400 | 400 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010xRuAAI | PRO-003064 | THUR21 | 0 | THUR21
MARCHWOOD ENERGY STORAGE | BW ESS DEVELOPMENT UK LIMITED | Marchwood 400kV Substation |  | 0 | 200 | 200 | 2027-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iuwQAA | PRO-002190 | MAWO4 | 200 | MAWO41
Mablethorpe Green Energy Centre | MABLETHORPE GREEN ENERGY CENTRE LIMITED | Mablethorpe 400kV Substation |  | 0 | 1025 | 1025 | 2033-10-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iv9QAA | PRO-002255 | MABL4 | 0
Mablethorpe Storage | THEDDLETHORPE FLEXIBLE GENERATION LIMITED | Mablethorpe 400kV Substation |  | 0 | 1500 | 1500 | 2031-11-30 | Scoping | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine);Demand | a0l4L0000005iw4QAA | PRO-001979 | MABL4 | 0
Machair Offshore Wind Farm | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Machair 275/66kV Offshore Substation |  | 0 | 2000 | 2000 | 2033-09-16 | Scoping | Direct Connection | SPT | Wind Offshore | a0l4L0000005iZsQAI | PRO-001392 |  | 0
Magwind | MAGNORA OFFSHORE WIND AS | New Dounreay |  | 0 | 495 | 495 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l4L0000005iisQAA | PRO-001766 | DOUN | 0 | DOUN3-
Mannington | BAYWA R.E. UK LIMITED | Mannington 400kV Substation |  | 0 | 57 | 57 | 2025-05-20 | Scoping | Direct Connection | NGET | PV Array (Photo Voltaic/solar) | a0l4L0000005ibaQAA | PRO-001092 | MANN4 | 57 | MANN41
Mannington | PIVOTED POWER LLP | Mannington 400kV Substation |  | 0 | 47.5 | 47.5 | 2025-11-30 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005ibbQAA | PRO-001091 | MANN4 | 47.5 | MANN41
Mannington Tertiary | MANNINGTON ENERGY CENTRE LIMITED | Mannington 400kV Substation |  | 0 | 47.5 | 47.5 | 2025-10-30 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005izWQAQ | PRO-000464 | MANN4 | 47.5 | MANN41
Manor Farm | QAIR RENEWABLES UK LIMITED | East Anglia Connection Node E 400kV Substation |  | 0 | 500 | 500 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001HxaxAAC | PRO-004269 | EACS4 | 0
Manor Farm Solar Park | CSE42 LIMITED | Fawley GSP |  | 0 | 150 | 150 | 2036-10-24 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005il5QAA | PRO-002337 | FAWL4 | 0 | FAWL41
Manquhill Wind Farm | ENERGYFARM UK MANQUHILL LTD | Manquhill Wind Farm 132/33kV Substation |  | 0 | 56 | 56 | 2036-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l8e0000012jKMAAY | PRO-004662 |  | 0
Marchwood | MARCHWOOD POWER LIMITED | Marchwood 400kV Substation |  | 920 | 0 | 920 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005iq2QAA | PRO-000202 | MAWO4 | 920 | MAWO41
Margree Wind Farm | ENERGYFARM UK MARGREE LLP | SPT Margree collector substation |  | 0 | 50 | 50 | 2029-10-31 | Awaiting Consents | Direct Connection | SPT | Wind Onshore | a0l4L0000005ij9QAA | PRO-001789 | QUAN1 | 50 | QUAN1-
Mark Hill Wind Farm | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Mark Hill 275/132kV |  | 53 | 0 | 53 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005imdQAA | PRO-000066 | MAHI1 | 53 | MAHI1-
Market Harborough | CONNECTID 1 LIMITED | West Anglia Connection Node F 400kV Substation |  | 0 | 700 | 700 | 2034-10-31 | Scoping | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l8e000000TPMdAAO | PRO-003271 | MARH4 | 0 | MARH41
Market Harborough GEC (Ethos Green) | MARKET HARBOROUGH GREEN ENERGY CENTRE LTD | Market Harborough 400kV Substation |  | 0 | 560 | 560 | 2032-10-31 | Awaiting Consents | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l8e000000ViF4AAK | PRO-004343 | MARH41 | 0 | MARH41
Market Harborough Green Energy Hub | TELIS ENERGY UK LIMITED | Market Harborough 400kV Substation |  | 0 | 1000 | 1000 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;Hydro;Nuclear;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e00000120NNAAY | PRO-003623 | MARH42 | 0 | MARH42
Marston Farm 2 | 548 UK INVESTMENT HOLDINGS LIMITED | Marston Vale 400kV Substation |  | 0 | 700 | 700 | 2032-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wdzAAA | PRO-002740 | MARV41 | 0 | MARV41
Meall Dearg | ENERGYFARM UK MEALL DEARG LTD | New North West 132kV Substation |  | 0 | 150.2 | 150.2 | 2037-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0lJ9000000PNJwIAO | PRO-005981 |  | 0
Medway 3 Power Station | MEDWAY POWER LIMITED | Kingsnorth 400kV Substation |  | 0 | 500 | 500 | 2030-12-31 | Scoping | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine);Energy Storage System | a0l8e0000010wOxAAI | PRO-002578 | KINO4 | 500 | KINO41
Medway Power Station | MEDWAY POWER LIMITED | Grain 400kV Substation |  | 735 | 175 | 910 | 2028-10-30 | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005iq1QAA | PRO-000203 | MEDW4 | 910 | MEDW41
Melksham | LIME DOWN SOLAR PARK LIMITED | Melksham 400kV Substation |  | 0 | 500 | 500 | 2029-07-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iP1QAI | PRO-001605 | MELK4 | 500 | MELK41
Melksham (Tertiary) | MELKSHAM CALNE GREEN LIMITED | Melksham 400kV Substation |  | 0 | 57 | 57 | 2025-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005izlQAA | PRO-000463 | MELK4 | 57 | MELK41
Melksham BESS & PV | ELEMENTS GREEN LIMITED | Melksham 400kV Substation |  | 0 | 800 | 800 | 2037-10-15 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ikwQAA | PRO-002441 | MELK4 | 0 | MELK41
Melksham Grid Park ESS & PV | JEPIPHANY LIMITED | Melksham 400kV Substation |  | 0 | 90 | 90 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001Hq1bAAC | PRO-004164 | MELK4 | 0 | MELK41
Melkshem (Cartridge Farm) | Queequeg Renewables Ltd | Melksham 400kV Substation |  | 0 | 480 | 480 | 2037-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l8e000000TPCYAA4 | PRO-003193 | MELK4 | 0 | MELK41
Melton Mowbray Solar | CUBICO UK DEVELOPMENT LIMITED | West Anglia Connection Node I 400kV substation |  | 0 | 340 | 340 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0lJ9000000PDlrIAG | PRO-005004 |  | 0
Melvich Wind Energy Hub | Melvich Wind Energy Hub Limited | Melvich Community Wind Farm 132/33kV Substation |  | 0 | 57.6 | 57.6 | 2030-04-01 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l4L0000005iepQAA | PRO-001688 |  | 57.6
Menter Mon Morlais Anglesey Marine Energy | Menter Môn Morlais Limited | Penrhos GSP | 1 | 0 | 40 | 40 | 2028-03-31 | Under Construction/Commissioning | Direct Connection | NGET | Tidal | a0l4L0000005ieUQAQ | PRO-001134-1 | PERH | 40
Menter Mon Morlais Anglesey Marine Energy | Menter Môn Morlais Limited | Penrhos GSP | 2 | 0 | 20 | 60 | 2029-03-31 | Under Construction/Commissioning | Direct Connection | NGET | Tidal | a0l4L0000005ieUQAQ | PRO-001134-2 | PERH | 20
Menter Mon Morlais Anglesey Marine Energy | Menter Môn Morlais Limited | Penrhos GSP | 3 | 0 | 40 | 100 | 2030-03-31 | Under Construction/Commissioning | Direct Connection | NGET | Tidal | a0l4L0000005ieUQAQ | PRO-001134-3 | PERH | 40
Menter Mon Morlais Anglesey Marine Energy | Menter Môn Morlais Limited | Penrhos GSP | 4 | 0 | 80 | 180 | 2032-03-31 | Under Construction/Commissioning | Direct Connection | NGET | Tidal | a0l4L0000005ieUQAQ | PRO-001134-4 | PERH | 0
Mererid Offshore Wind Farm | South West Wind Holdco Limited | Alverdiscott 400kV Substation |  | 0 | 1008 | 1008 | 2036-12-06 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005ivOQAQ | PRO-002391 | ALVE4A | 0 | ALVE4A
Meridien Solar Farm | Downing Renewable Developments LLP | Weston Marsh 400kV Substation |  | 0 | 750 | 750 | 2033-06-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iujQAA | PRO-002399 | WEMA4 | 0
Merlin 2 Offshore Windfarm | OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation |  | 0 | 1500 | 1500 | 2031-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005iZbQAI | PRO-001997 | ALVE4A | 0 | ALVE4A
Merlin Offshore Wind Farm | OFFSHORE WIND LIMITED | Alverdiscott 400kV Substation |  | 0 | 300 | 300 | 2028-11-01 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005ihVQAQ | PRO-001728 | ALVE4A | 300 | ALVE4A
Merthyr Solar and Battery | E.E.W. ECO ENERGY WORLD DEVELOPMENT HOLDING LIMITED | Cilfynydd 400kV Substation | 2 | 0 | 65 | 175 | 2037-10-31 | Scoping | Direct Connection | NGET | PV Array (Photo Voltaic/solar) | a0l8e0000010wfMAAQ | PRO-002757-2 | CILF4 | 0 | CILF41
Merthyr Solar and Battery | E.E.W. ECO ENERGY WORLD DEVELOPMENT HOLDING LIMITED | Cilfynydd 400kV Substation | 1 | 0 | 110 | 110 | 2029-05-12 | Scoping | Direct Connection | NGET | PV Array (Photo Voltaic/solar) | a0l8e0000010wfMAAQ | PRO-002757-1 | CILF4 | 110 | CILF41
MeyGen Tidal | MEYGEN PLC | Gills Bay GSP | 1 | 0 | 28 | 28 | 2027-04-01 | Consents Approved | Direct Connection | SHET | Tidal | a0l4L0000005isuQAA | PRO-000336-1 | GILB | 28 | GILB1J
MeyGen Tidal | MEYGEN PLC | Gills Bay GSP | 2 | 0 | 43 | 71 | 2028-04-01 | Consents Approved | Direct Connection | SHET | Tidal | a0l4L0000005isuQAA | PRO-000336-2 | GILB | 43 | GILB1J
MeyGen Tidal | MEYGEN PLC | Gills Bay GSP | 3 | 0 | 83 | 154 | 2028-04-01 | Awaiting Consents | Direct Connection | SHET | Tidal | a0l4L0000005isuQAA | PRO-000336-3 | GILB | 83 | GILB1J
MeyGen Tidal | MEYGEN PLC | Gills Bay GSP | 4 | 0 | 83 | 237 | 2028-04-01 | Awaiting Consents | Direct Connection | SHET | Tidal | a0l4L0000005isuQAA | PRO-000336-4 | GILB | 83 | GILB1J
MeyGen Tidal | MEYGEN PLC | Gills Bay GSP | 5 | 0 | 50 | 287 | 2030-10-31 | Scoping | Direct Connection | SHET | Tidal | a0l4L0000005isuQAA | PRO-000336-5 | GILB | 50 | GILB1J
Mickleham Energy Storage | BW ESS DEVELOPMENT UK LIMITED | Rowdown 400kV Substation |  | 0 | 249 | 249 | 2031-10-22 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000011zKgAAI | PRO-003573 | ROWD41 | 0 | ROWD41
Mid Hill | Invenergy Development UK Ltd | Hawick 132kV Substation |  | 0 | 228 | 228 | 2034-10-30 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0lJ9000000PDlIIAW | PRO-005000 |  | 0
Mid Moile Wind Farm | ENERGIEKONTOR UK LTD | Arecleoch 132/33kV |  | 0 | 99 | 99 | 2031-10-31 | Scoping | Direct Connection | SPT | Wind Onshore | a0l8e000000f8Q7AAI | PRO-004036 | AREC3 | 0 | AREC3-
Middle Farm Chollerton | ENRAY POWER LTD | Borders Connection Node A 400kV |  | 0 | 240 | 240 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000ViF9AAK | PRO-004344 | FOUR2 | 0 | FOUR21
Middle Muir Wind Farm | OnPath Energy Limited (MIDDLE MUIR WIND FARM) LIMITED | Middlemuir 132/33kV |  | 51 | 0 | 51 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005ishQAA | PRO-000321 | MIDM3 | 51 | MIDM3-
Middleton BESS | Middleton Energy Storage Limited | Middleton 400KV Substation |  | 0 | 200 | 200 | 2026-11-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005j1YQAQ | PRO-002305 | MIDL4 | 200 | MIDL41
Middleton Farm BESS | Bluestone Energy Ltd | Neilston 400kV Substation |  | 0 | 937 | 937 | 2033-10-25 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000001HpUdAAK | PRO-004120 | NEIL4 | 0 | NEIL4Q
Midlands Estate Energy Park | Renewable Energy Systems Limited | West Burton 400kV Substation |  | 0 | 600 | 600 | 2029-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l4L0000005iwuQAA | PRO-001945 | WBUR41 | 600 | WBUR41
Mill Hill Tertiary Connection | HB333MIL LTD | Mill Hill 275kV Substation |  | 0 | 57 | 57 | 2025-10-24 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005iw8QAA | PRO-000493 | MILH2B | 57 | MILH2B
Millbrook Power | MILLBROOK POWER LIMITED | Marston Vale 400kV Substation |  | 0 | 299 | 299 | 2024-06-28 | Under Construction/Commissioning | Direct Connection | NGET | OCGT (Open Cycle Gas Turbine) | a0l4L0000005ilMQAQ | PRO-000373 | MARV41 | 299 | MARV41
Millennium Wind | MILLENNIUM WIND ENERGY LIMITED | Millennium GSP |  | 65 | 0 | 65 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005ipAQAQ | PRO-000530 | MILW | 65 | MILW3-
Milligansbush Battery Storage | Milligansbush Battery Storage Ltd | Milligansbush Battery Storage 132kV Substation |  | 0 | 200 | 200 | 2036-10-30 | Scoping | Direct Connection | SPT | Demand;Energy Storage System | a0l8e000000TPSXAA4 | PRO-003430 |  | 0
Millmoor Rig Wind Farm | ESB ASSET DEVELOPMENT UK LIMITED | Hawick GSP |  | 0 | 92.8 | 92.8 | 2029-10-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005iYMQAY | PRO-001936 | HAWI | 92.8 | HAWI3-
Minety | HB411MIN Limited | Minety 400kV Substation |  | 0 | 47.5 | 47.5 | 2024-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005inPQAQ | PRO-000454 | MITY4 | 47.5 | MITY41
Minety Tertiary (2) | JBM SOLAR PROJECTS 14 LTD | Minety GSP |  | 0 | 47.5 | 47.5 | 2024-10-30 | Scoping | Direct Connection | NGET | PV Array (Photo Voltaic/solar) | a0l4L0000005inQQAQ | PRO-000432 | MITY4 | 47.5 | MITY41
Minnygap | MINNYGAP ENERGY LIMITED | Moffat 132/33kV |  | 25 | 0 | 25 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005irJQAQ | PRO-000262 | MOFF3 | 25 | MOFF3-
Minnygryle Burn Energy Park | Wind 2 Project 6 Limited | Glenlee 132/11kV |  | 0 | 84 | 84 | 2036-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l8e000001HrDXAA0 | PRO-004204 | GLLE5 | 0 | GLLE5-
Moelfre Energy Park | MOELFRE ENERGY PARK LIMITED | Bodelwyddan 400kV Substation |  | 0 | 158.4 | 158.4 | 2026-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iekQAA | PRO-001500 | BODE4 | 158.4 | BODE41
Moffat BESS | Conrad Energy (Developments) II Limited | Moffat 400/132kV |  | 0 | 500 | 500 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000012jJiAAI | PRO-004654 | MOFF1 | 0 | MOFF1-
Mon Solar Farm | LIGHTSOURCE SPV 204 LIMITED | Wylfa South 400kV Substation |  | 0 | 240 | 240 | 2028-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ix8QAA | PRO-001480 | WYLS4 | 240 | WYLS41
Mona Offshore Wind Farm | Mona Offshore Wind Limited | Bodelwyddan 400kV Substation |  | 0 | 1500 | 1500 | 2029-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005iZrQAI | PRO-001391 | BODE4 | 1500 | BODE41
Monets Garden | MONETS GARDEN BATTERY LTD | Osbaldwick 400kV Substation |  | 0 | 57 | 57 | 2024-10-30 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005icgQAA | PRO-001082 | OSBA41 | 57 | OSBA41
Monk Fryston | Downing Renewable Developments LLP | Monk Fryston 275kV Substation |  | 0 | 249.9 | 249.9 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TPQCAA4 | PRO-003400 | MONF21 | 0 | MONF21
Monk Fryston | ENSO GREEN HOLDINGS LIMITED | Monk Fryston 400kV Substation |  | 0 | 400 | 400 | 2031-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ikVQAQ | PRO-002159 | MONF42 | 0 | MONF42
Monk Fryston | Light Valley Solar Limited | Monk Fryston 275kV Substation |  | 0 | 500 | 500 | 2029-12-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iy0QAA | PRO-001646 | MONF22 | 500 | MONF22
Monk Fryston BESS | HARMONY MF LIMITED | Monk Fryston 275kV Substation |  | 0 | 200 | 200 | 2029-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ixXQAQ | PRO-001619 | MONF22 | 200 | MONF22
Monk Fryston Energy Park | ELEMENTS GREEN DEVELOPMENT LTD | Monk Fryston 400kV Substation |  | 0 | 800 | 800 | 2035-10-24 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L000002yQWaQAM | PRO-002539 | MONF41 | 0 | MONF41
Monk Fryston SSE | SSE BATTERY MONK FRYSTON LIMITED | Monk Fryston 275kV Substation |  | 0 | 320 | 320 | 2025-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005ixyQAA | PRO-001627 | MONF21 | 320 | MONF21
Monk Fryston Tertiary Connection | HD777FRY LTD | Monk Fryston 275kV Substation |  | 0 | 57 | 57 | 2024-10-01 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005incQAA | PRO-000479 | MONF22 | 57 | MONF22
Moray East Offshore Wind Farm | MORAY OFFSHORE WINDFARM (EAST) LIMITED | New Deer 400kV Substation |  | 900 | 0 | 900 |  | Built | Direct Connection | SHET | Wind Offshore | a0l4L0000005ip7QAA | PRO-000533 | NEDE4 | 900 | NEDE4J
Moray West Offshore Windfarm | MORAY OFFSHORE WINDFARM (WEST) LIMITED | Moray Firth 220/33kV Platform 1 & 2 Offshore Substation |  | 860 | 0 | 860 |  | Built | Direct Connection | SHET | Wind Offshore | a0l4L0000005ifSQAQ | PRO-001130 |  | 860
Morecambe Offshore Wind Farm | OFFSHORE WIND LIMITED | Penwortham 400kV Substation |  | 0 | 480 | 480 | 2029-06-30 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005ibwQAA | PRO-001450 | PEWO41 | 480 | PEWO41
Moreton Estate | EPL NEWCO5 LIMITED | Chickerell B 400kV Substation |  | 0 | 480 | 480 | 2037-04-28 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f5BsAAI | PRO-003920 | CHIC41 | 0 | CHIC41
Morgan Offshore Wind Farm | Morgan Offshore Wind Limited | Penwortham 400kV Substation |  | 0 | 1500 | 1500 | 2029-11-30 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005ik5QAA | PRO-001594 | PEWO41 | 1500 | PEWO41
Morton Manor PV & BESS Station | IB VOGT UK LTD | High Marnham 400kV Substation |  | 0 | 240 | 240 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f41nAAA | PRO-003827 | HIGM4 | 0 | HIGM41
Morven A Offshore Wind Farm (Prev Phoenix 1A) | Morven Offshore Wind Limited | Phoenix 1A 275/66kV Offshore Substation |  | 0 | 1500 | 1500 | 2031-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005izJQAQ | PRO-001515 | HAWP41 | 0 | HAWP41
Morwind 300 | Morwind Ltd | Alverdiscott 400kV Substation |  | 0 | 300 | 300 | 2031-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005ixtQAA | PRO-001787 | ALVE4A | 0 | ALVE4A
Mosedale Energy | MOSEDALE ENERGY LIMITED | High Marnham 400kV Substation |  | 0 | 249 | 249 | 2033-03-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ivUQAQ | PRO-002319 | HIGM4 | 0 | HIGM41
Mossford (part of the Conon Cascade) | SSE Generation Limited | Mossford GSP |  | 18.7 | 0 | 18.7 |  | Built | Direct Connection | SHET | Hydro | a0l4L0000005ipQQAQ | PRO-000176 | MOSS | 18.7 | MOSS5-
Mossmorran Storage BESS | RUFUSIA LTD | Mossmorran 132/33kV |  | 0 | 100 | 100 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000exgxAAA | PRO-003738 | MOSM3 | 0 | MOSM3Q
Mossy Hill Wind Farm | MOSSY HILL SHETLAND LIMITED | Mossy Hill 132kV Substation |  | 0 | 48 | 48 | 2028-11-30 | Consents Approved | Direct Connection | SHET | Demand;Wind Onshore | a0l4L0000005iwmQAA | PRO-000461 | MSHL3 | 48 | MSHL3-
Motherwell 400MW BESS (Formerly Castlehill BESS) | Apatura Battery Ltd | Castlehill BESS 400kV Substation |  | 0 | 400 | 400 | 2030-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000011y79AAA | PRO-003500 | WISH2 | 400 | WISH2-
Mount Pleasant | HARMONY ENERGY LIMITED | Bishops Wood 275kV Substation |  | 0 | 200 | 200 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0lJ9000000PN5CIAW | PRO-005962 | BISW2 | 0 | BISW21
Mountain Fen | LIGHTSOURCE SPV 204 LIMITED | Coddington 400kV Substation |  | 0 | 240 | 240 | 2034-09-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f4x7AAA | PRO-003891 | EASO4 | 0 | EASO41
Muaitheabhal Wind Farm | UISENIS POWER LIMITED | Muaitheabhal 132/33kV Substation |  | 0 | 189 | 189 | 2030-10-31 | Consents Approved | Direct Connection | SHET | Wind Onshore | a0l4L0000005iroQAA | PRO-000272 |  | 189
Muir Mhor Offshore Wind Farm | MUIR MHÒR OFFSHORE WIND FARM LIMITED | Cirrus Offshore Windfarm Substation |  | 0 | 1000 | 1000 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l4L0000005izGQAQ | PRO-001698 | NEDE | 0 | NEDE4J
Murroch BESS | Apatura Battery Ltd | Murroch BESS 132kV Substation |  | 0 | 200 | 200 | 2031-05-22 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000001205eAAA | PRO-003610 | STLE | 0 | STLE3S
Mwdwl Eithin Energy Park | MOEL CHWA ENERGY PARK LIMITED | Gwyddelwern 400kV Substation |  | 0 | 81.2 | 81.2 | 2026-10-31 | Scoping | Direct Connection | NGET | Wind Onshore | a0l4L0000005ifqQAA | PRO-001511 | GWYD4 | 81.2 | GWYD41
Mybster 2 Battery Storage | POTENCIA ENERGY LIMITED | Mybster 3 132/33kV Substation |  | 0 | 500 | 500 | 2034-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000012gsmAAA | PRO-004479 | MYBS1 | 0 | MYBS1Q
Myreton BESS | GPC 1039 Ltd | Tealing 132kV Substation |  | 0 | 200 | 200 | 2028-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000010x1hAAA | PRO-003050 |  | 200
NEL Story | STORY FUTURE ENERGY LIMITED | Harker 400kV Substation |  | 0 | 240 | 240 | 2037-11-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f5rSAAQ | PRO-003940 | HARG4 | 0 | HARG41
Nant | SSE Generation Limited | Nant 132kV Substation |  | 15 | 0 | 15 |  | Built | Direct Connection | SHET | Hydro | a0l4L0000005ipRQAQ | PRO-000177 | NANT1 | 15 | NANT1Q
Nant Aman | NANT AMAN ENERGY PARK LIMITED | Rhigos 400kV Substation |  | 0 | 143 | 143 | 2030-12-13 | Scoping | Direct Connection | NGET | Wind Onshore | a0l4L0000005iNcQAI | PRO-001640 | RHIG4 | 143 | RHIG41
Nant Helen | SOLAR SECURITIES LIMITED | Rhigos B Substation |  | 0 | 500 | 500 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000010wgFAAQ | PRO-002766 | RHIG4 | 0 | RHIG41
Nant Y Maen Wind Farm | EDF ENERGY RENEWABLES LIMITED | Nant Y Maen 132KV Substation |  | 0 | 150 | 150 | 2032-05-01 | Scoping | Direct Connection | NGET | Wind Onshore | a0l4L0000005iv0QAA | PRO-001158 | NANT1 | 0 | NANT1Q
Narie | Invenergy Development UK Ltd | Glenlee 132/11kV |  | 0 | 297 | 297 | 2036-10-31 | Awaiting Consents | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l8e000001Hny0AAC | PRO-004048 | GLLE1 | 0 | GLLE1-
NatPower Allington Green Energy Park | NP SPV35 LIMITED | Cottam 400kV Substation |  | 0 | 1000 | 1000 | 2034-10-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l8e0000012eyYAAQ | PRO-004387 | COTT4 | 0 | COTT41
NatPower CoalBurn Green Energy Park | COALBURN ENERGY LIMITED | NatPower Green Energy Park 400kV Substation |  | 0 | 500 | 500 | 2036-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0lJ9000000PDspIAG | PRO-005041 |  | 0
NatPower Connah Quay Green Energy Park | NP SPV24 LIMITED | Connah's Quay 400kV Substation |  | 0 | 500 | 500 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0lJ9000000blK7IAI | PRO-004797 | CONQ4 | 0 | CONQ41
NatPower Gwyddelwern Green Energy Park | NP SPV31 Limited | North Wales connection Node A 400kV Substation |  | 0 | 1000 | 1000 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000012gbUAAQ | PRO-004432 |  | 0
NatPower Harburn Green Energy Park | YAXLEY ENERGY LIMITED | NatPower Harburn Green Energy Park 400kV Substation |  | 0 | 800 | 800 | 2033-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0lJ9000000PEBlIAO | PRO-005123 |  | 0
NatPower Hawthorn Pit Green Energy Park | NP SPV 29 LIMITED | Wearside Connection Node B 400kV Substation |  | 0 | 1000 | 1000 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0lJ9000000blM8IAI | PRO-004820 |  | 0
NatPower Immingham Green Energy Park | NATPOWER MARINE UK LIMITED | Trent Valley North Connection Node F 400kV Substation |  | 0 | 1000 | 1000 | 2034-10-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l8e0000012hwgAAA | PRO-004566 |  | 0
NatPower Kinoulton Green Energy Park | NP SPV32 LIMITED | Grendon 400kV Substation |  | 0 | 1330 | 1330 | 2034-12-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001I31pAAC | PRO-004333 | GREN4 | 0 | GREN41
NatPower Kintore2 Green Energy Park | NP SPV 41 LIMITED | Kintore 275kV |  | 0 | 500 | 500 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0lJ9000000blPHIAY | PRO-004860 | KINT2 | 0 | KINT2J
NatPower Llanteg Green Energy Park | NP SPV30 LIMITED | Llanteg 400kV Substation |  | 0 | 47.5 | 47.5 | 2028-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0lJ9000000blKvIAI | PRO-004806 |  | 47.5
NatPower Navenby Energy Park | NAVENBY ENERGY LIMITED | Navenby 400kV Substation |  | 0 | 1030 | 1030 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0lJ9000000PDm1IAG | PRO-005006 | BICF4 | 0 | BICF41
NatPower Nursling Energy Park | NATPOWER MARINE LIMITED | Nursling 400kV Substation |  | 0 | 1000 | 1000 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001HrCKAA0 | PRO-004190 | NURS41 | 0 | NURS41
NatPower Oswestry Green Energy Park | NP SPV 43 Limited | Oswestry Substation |  | 0 | 1000 | 1000 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0lJ9000000PDuCIAW | PRO-005057 |  | 0
NatPower Penrith Green Energy Park | NP SPV 39 LIMITED | Harker 400kV Substation |  | 0 | 1000 | 1000 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001HxblAAC | PRO-004278 | HARG4 | 0 | HARG41
NatPower Teesside Green Energy Park | NATPOWER MARINE LIMITED | Teeside Connection Node A 400kV Substation |  | 0 | 1000 | 1000 | 2035-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001HrYtAAK | PRO-004207 |  | 0
NatPower Tilbury Green Energy Park | NATPOWER MARINE UK LIMITED | South Anglia Connection Node C 400kV Substation |  | 0 | 1000 | 1000 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000012hwMAAQ | PRO-004562 |  | 0
NatPower Yaxley Green Energy Park | YAXLEY ENERGY LIMITED | North Anglia Connection Node C 400kV Substation |  | 0 | 1000 | 1000 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000012eVvAAI | PRO-004371 |  | 0
Native River (Capenhurst) | NATIVE RIVER LTD | Capenhurst 275kV Substation |  | 57 | 0 | 57 |  | Built | Direct Connection | NGET | Energy Storage System | a0l4L0000005iibQAA | PRO-001557 | CAPE2 | 57 | CAPE21
Natpower Basingstoke Green Energy Park | NP SPV23 LIMITED | Fleet 400kV Substation |  | 0 | 1000 | 1000 | 2038-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000expyAAA | PRO-003746 | FLEE4 | 0 | FLEE41
Natpower Enderby - Patford Bridge Green Energy Park | NP SPV33 LIMITED | Patford Bridge 400kV Substation |  | 0 | 1799 | 1799 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001Hpe3AAC | PRO-004132 | PAFB4A | 0 | PAFB4A
Natpower Thimbleby Green Energy Park | NP SPV 22 LIMITED | Thimbleby 400kV substation |  | 0 | 1000 | 1000 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000exh7AAA | PRO-003740 |  | 0
Natpower Upsall Green Energy Park | NP SPV 21 LIMITED | Upsall 400kV substation |  | 0 | 1000 | 1000 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000exh2AAA | PRO-003739 |  | 0
Navenby Farm | CODDINGTON 10 RENEWABLES LTD | Coddington 400kV Substation |  | 0 | 1000 | 1000 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001HnxlAAC | PRO-004045 | EASO4 | 0 | EASO41
Navenby GEC (Ethos Green) | NAVENBY GREEN ENERGY CENTRE LTD | Navenby 400kV Substation |  | 0 | 580 | 580 | 2033-10-30 | Awaiting Consents | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l8e000000f5Y8AAI | PRO-003936 | BICF4 | 0 | BICF41
Neart Na Gaoithe Offshore Wind Farm | NEART NA GAOITHE OFFSHORE WIND LIMITED | Neart Na Gaoithe 220/66KV Offshore Substation |  | 0 | 448 | 448 | 2023-06-01 | Consents Approved | Direct Connection | SPT | Wind Offshore | a0l4L0000005irpQAA | PRO-000273 | CRYR4 | 448 | CRYR4-
Necton Greener Grid Park | Necton Grid Solutions Limited | Necton 400kV Substation | 1 | 0 | 0 | 0 | 2026-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System;Reactive Compensation | a0l4L000002yQb1QAE | PRO-002562-1 | NECT4 | 0 | NECT41
Necton Greener Grid Park | Necton Grid Solutions Limited | Necton 400kV Substation | 2 | 0 | 78 | 78 | 2032-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;Reactive Compensation | a0l4L000002yQb1QAE | PRO-002562-2 | NECT4 | 0 | NECT41
Neilston 132kV Greener Grid Park | NEILSTON ENERGY LIMITED | Neilston 400/275/132kV | 1 | 0 | 50 | 50 | 2024-05-31 | Scoping | Direct Connection | SPT | Energy Storage System;Reactive Compensation | a0l4L0000005iYhQAI | PRO-001343-1 | NEIL1 | 50 | NEIL1-
Neilston 132kV Greener Grid Park | NEILSTON ENERGY LIMITED | Neilston 400/275/132kV | 2 | 0 | 100 | 150 | 2025-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;Reactive Compensation | a0l4L0000005iYhQAI | PRO-001343-2 | NEIL1 | 100 | NEIL1-
Neilston 400kV Greener Grid Park | STATKRAFT UK LTD | Neilston 400kV Substation |  | 0 | 600 | 600 | 2027-05-17 | Scoping | Direct Connection | SPT | Energy Storage System;Reactive Compensation | a0l4L0000005iasQAA | PRO-001419 | NEIL4 | 600 | NEIL4Q
Neilston Synchronous Compensation | NEILSTON GRID SERVICES LIMITED | Neilston 400kV Substation |  | 0 | 0 | 0 | 2024-07-31 | Consents Approved | Direct Connection | SPT | Reactive Compensation | a0l4L0000005iahQAA | PRO-001405 | NEIL4 | 0 | NEIL4Q
Net Zero Teesside Power Project | NET ZERO TEESSIDE POWER LIMITED | Tod Point 275kV Substation |  | 0 | 860 | 860 | 2027-07-30 | Consents Approved | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine);Demand | a0l4L0000005iyzQAA | PRO-001400 | TODP2 | 860 | TODP21
Nethercourt Solar & BESS Farm | GREENTECH PROJECTS HOLDING UK LIMITED | Nethercourt Substation |  | 0 | 240 | 240 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000TPXJAA4 | PRO-003437 |  | 0
Netherton Hub Bess | FIELD DEVCO LTD | Netherton 400kV Substation |  | 0 | 200 | 200 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000012kjdAAA | PRO-004753 | NETH3 | 0 | NETH3-
New Cumnock BESS | NEW CUMNOCK BESS LTD | New Cumnock 275/132kV Substation |  | 0 | 450 | 450 | 2033-10-30 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000011xxPAAQ | PRO-003485 | NECU2 | 0 | NECU2-
New Deer 2 BESS | FIELD DEVCO LTD | New Deer 2 400kV Substation |  | 0 | 200 | 200 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000012kk2AAA | PRO-004758 | NEDE4 | 0 | NEDE4J
New Deer BESS Station | ABBOTSHAUGH ENERGY STORAGE LIMITED | New Deer 2 400kV Substation |  | 0 | 500 | 500 | 2032-07-30 | Scoping | Direct Connection | SHET | Energy Storage System | a0l4L0000005iPMQAY | PRO-001856 | NEDE4 | 0 | NEDE4J
New Deer Battery Storage | Weaver Power Limited | New Deer 2 400kV Substation |  | 0 | 500 | 500 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l4L0000005ixLQAQ | PRO-001987 | NEDE4 | 0 | NEDE4J
New Marton GEC | NEW MARTON GREEN ENERGY CENTRE LIMITED | New Marton 400kV Substation |  | 0 | 550 | 550 | 2037-10-30 | Scoping | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0lJ9000000blJnIAI | PRO-004796 |  | 0
New Marton Solar Farm - PVDP | SolarFour Ltd | Cheshire Connection Node A 400kV Substation |  | 0 | 780 | 780 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001HpecAAC | PRO-004139 | LEGA4 | 0 | LEGA41
Newark BESS | SSE DE SOLAR HOLDCO LIMITED | Cottam 400kV Substation |  | 0 | 600 | 600 | 2033-09-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L000002yQa3QAE | PRO-002556 | COTT4 | 0 | COTT41
Newarthill Energy Park | Geocore (Newarthill) Ltd | Newarthill Energy Park 275kV Substation |  | 0 | 300 | 300 | 2027-10-28 | Awaiting Consents | Direct Connection | SPT | Energy Storage System | a0l4L0000005jACQAY | PRO-002532 | NEAR2 | 300 | NEAR2Q
Newchurch | SSE UTILITY SOLUTIONS LIMITED | Newchurch 400kV Substation |  | 0 | 400 | 400 | 2031-10-04 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ic4QAA | PRO-002056 | DUNG4 | 0 | DUNG41
Newlands Hill Wind Energy Hub | NEWLANDS HILL WIND ENERGY HUB LIMITED | Newlands Hill 132/33kV |  | 0 | 119 | 119 | 2030-04-03 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l4L000002yQY7QAM | PRO-002549 |  | 119
Nicolton Road BESS | Apatura Battery Ltd | Nicolton Road 275kV Substation |  | 0 | 250 | 250 | 2030-10-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000TPHTAA4 | PRO-003234 |  | 250
Ninfield | Ninfield 10 Renewables Limited | Sussex and Romney Connection Node A 400kV Substation |  | 0 | 1000 | 1000 | 2030-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000TPQqAAO | PRO-003408 | NINF4 | 1000 | NINF41
Ninfield Green Energy Centre | NINFIELD NG LIMITED | Ninfield 400kV Substation |  | 0 | 600 | 600 | 2031-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iMYQAY | PRO-002163 | NINF4 | 0 | NINF41
Ninfield Greener Grid Park | STATKRAFT UK LTD | Ninfield 400kV Substation | 1 | 0 | 0 | 0 | 2027-04-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;Reactive Compensation | a0l4L0000005ihhQAA | PRO-001756-1 | NINF4 | 0 | NINF41
Ninfield Greener Grid Park | STATKRAFT UK LTD | Ninfield 400kV Substation | 2 | 0 | 49.9 | 49.9 | 2031-01-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;Reactive Compensation | a0l4L0000005ihhQAA | PRO-001756-2 | NINF4 | 0 | NINF41
Ninfield Greener Grid Park | STATKRAFT UK LTD | Ninfield 400kV Substation | 3 | 0 | 400.1 | 450 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;Reactive Compensation | a0l4L0000005ihhQAA | PRO-001756-3 | NINF4 | 0 | NINF41
Norfolk Boreas | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 1 | 0 | 400 | 400 | 2029-10-01 | Awaiting Consents | Direct Connection | NGET | Wind Offshore | a0l4L0000005izTQAQ | PRO-000399-1 | NECT4 | 400 | NECT41
Norfolk Boreas | NORFOLK BOREAS LIMITED | Necton 400kV Substation | 2 | 0 | 920 | 1320 | 2030-12-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005izTQAQ | PRO-000399-2 | NECT4 | 920 | NECT41
Norfolk001 |  | Walpole 400kV Substation |  | 0 | 860 | 860 | 2031-11-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iZaQAI | PRO-001996 | WALP42 | 0 | WALP41
North East Offshore Wind Farm | CALEDONIA OFFSHORE WIND FARM LIMITED | New Deer 2 400kV Substation |  | 0 | 2000 | 2000 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l4L0000005ibmQAA | PRO-001436 | NEDE4 | 0 | NEDE4J
North Falls Offshore Wind Farm | NORTH FALLS OFFSHORE WIND FARM LIMITED | North Falls Offshore Platform Substation |  | 0 | 1000 | 1000 | 2030-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005izVQAQ | PRO-000451 | EACS4 | 1000
North Killingholme Power Project | UNIPER UK LIMITED | Killingholme 400kV Substation |  | 0 | 540 | 540 | 2030-09-30 | Consents Approved | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005iaKQAQ | PRO-001038 | KILL4 | 540 | KILL41
North Kyle New Cumnock | NORTH KYLE WIND FARM LIMITED | New Cumnock 275/132kV Substation | 1 | 0 | 79 | 79 | 2024-12-18 | Awaiting Consents | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l4L0000005inuQAA | PRO-000474-1 |  | 79
North Kyle New Cumnock | NORTH KYLE WIND FARM LIMITED | New Cumnock 275/132kV Substation | 2 | 0 | 133 | 212 | 2025-05-30 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l4L0000005inuQAA | PRO-000474-2 |  | 133
North Lanrigg Battery Storage | North Lanrigg Battery Storage Ltd | North Lanrigg Substation |  | 0 | 200 | 200 | 2028-10-30 | Scoping | Direct Connection | SPT | Demand;Energy Storage System | a0l8e0000010wXzAAI | PRO-002671 |  | 200
North Lowther Energy Initiative | NLEI LTD | NLEI Wind Farm Connection Substation |  | 0 | 151.2 | 151.2 | 2031-04-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005it0QAA | PRO-000344 |  | 0
NorthFleet 2 BESS | CSE41 LIMITED | NorthFleet 400kV Substation |  | 0 | 300 | 300 | 2028-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005itrQAA | PRO-002322 | NFLE4 | 300 | NFLE41
NorthFleet Tertiary | CSE29 LIMITED | NorthFleet 400kV Substation |  | 0 | 49.9 | 49.9 | 2026-06-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ibCQAQ | PRO-002038 | NFLE4 | 49.9 | NFLE41
Norton | BAYWA R.E. UK LIMITED | Norton 400kV Substation |  | 0 | 57 | 57 | 2025-05-01 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005ixsQAA | PRO-001537 | NORT4 | 57 | NORT41
Norton | ENSO GREEN HOLDINGS LIMITED | Norton 400kV Substation |  | 0 | 400 | 400 | 2032-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005itMQAQ | PRO-002157 | NORT4 | 0 | NORT41
Norton PV and BESS | Darlington Solar 1 Limited | Norton 275kV Substation |  | 0 | 40.9 | 40.9 | 2027-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ixWQAQ | PRO-001437 | NORT4 | 40.9 | NORT41
Norwich | PIVOTED POWER LLP | Norwich GSP |  | 0 | 57 | 57 | 2024-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iclQAA | PRO-001077 | NORM42 | 57 | NORM41
Norwich 2 | EDF ENERGY RENEWABLES LIMITED | Norwich Main 400kV Substation |  | 0 | 28 | 28 | 2033-06-30 | Scoping | Direct Connection | NGET | PV Array (Photo Voltaic/solar);Wind Onshore | a0l4L0000005itQQAQ | PRO-002408 | NORM42 | 0 | NORM41
Norwich Green Energy Centre | NORWICH GREEN ENERGY LIMITED | Norwich Main 400kW Substation |  | 0 | 400 | 400 | 2031-04-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iixQAA | PRO-001771 | NORM42 | 0 | NORM41
Norwich Main BESS | LONG STRATTON ENERGY PARK LIMITED | North Anglia Connection Node A 400kV | 1 | 0 | 249.9 | 249.9 | 2032-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f4xHAAQ | PRO-003894-1 |  | 0
Norwich Main BESS | LONG STRATTON ENERGY PARK LIMITED | North Anglia Connection Node A 400kV | 2 | 0 | 700 | 949.9 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f4xHAAQ | PRO-003894-2 |  | 0
Norwich Yare | ASHGREEN ENERGY FARM LIMITED | Norwich GSP |  | 0 | 49.5 | 49.5 | 2024-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005icmQAA | PRO-001076 | NORM41 | 49.5 | NORM41
Noventum - Astwood | NOVENTUM POWER SOLAR 12 LIMITED | West Anglia Connection Node C 400kV Substation |  | 0 | 480 | 480 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012j9PAAQ | PRO-004635 |  | 0
Noventum - Biggleswade | NOVENTUM POWER SOLAR 7 LIMITED | Biggleswade 400kV Substation |  | 0 | 249 | 249 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000ViASAA0 | PRO-004337 | BIGG4 | 0 | BIGG41
Noventum - Budby | NOVENTUM POWER SOLAR 15 LIMITED | Trent Valley South Connection Node D 400kV Substation |  | 0 | 380 | 380 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012jJEAAY | PRO-004652 |  | 0
Noventum - Stocksbridge | NOVENTUM POWER SOLAR 14 LIMITED | Leeds South Connection Node C 400kV Substation |  | 0 | 410 | 410 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000012jKHAAY | PRO-004661 |  | 0
Noventum -Long Stratton | Noventum Power Solar 8 Limited | North Anglia Connection Node A 400kV |  | 0 | 460 | 460 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012gHLAAY | PRO-004405 |  | 0
Noventum -New Marton | NOVENTUM POWER SOLAR 11 LIMITED | Cheshire Connection Node A 400kV Substation |  | 0 | 510 | 510 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012j9KAAQ | PRO-004634 |  | 0
Noventum Cottered | NOVENTUM POWER SOLAR 5 LIMITED | West Anglia Connection Node D 400kV Substation |  | 0 | 210 | 210 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001Hom7AAC | PRO-004092 |  | 0
Noventum Hawthorn Pit | NOVENTUM POWER SOLAR 2 LIMITED | Wearside Connection Node B 400kV Substation |  | 0 | 57 | 57 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000eySmAAI | PRO-003757 |  | 0
Noventum Market Harborough | NOVENTUM POWER SOLAR 1 LIMITED | West Anglia Connection Node F 400kV Substation |  | 0 | 249 | 249 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000eySrAAI | PRO-003759 | MARH4 | 0 | MARH41
Noventum Navenby | NOVENTUM POWER SOLAR 4 LIMITED | Trent Valley South Connection Node C 400kV Substation |  | 0 | 249 | 249 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f57EAAQ | PRO-003915 |  | 0
Noventum Yaxley | NOVENTUM POWER SOLAR 3 LIMITED | North Anglia Connection Node E 400kV Substation |  | 0 | 150 | 150 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000eySnAAI | PRO-003758 | YAXL4 | 0 | YAXL41
Noventum- Bridgwater | NOVENTUM POWER SOLAR 13 LIMITED | Woolavington 400kV Substation |  | 0 | 380 | 380 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000012jJ4AAI | PRO-004650 |  | 0
Nursling Tertiary | NURSLING ENERGY TWO LIMITED | Nursling 400kV Substation |  | 49.9 | 0 | 49.9 |  | Built | Direct Connection | NGET | Energy Storage System | a0l4L0000005iwMQAQ | PRO-001051 | NURS41 | 49.9 | NURS41
OWF3 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | OWF3 275/66kV Offshore Substation | 2 | 0 | 2000 | 3000 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l4L0000005iaiQAA | PRO-001406-2 |  | 0
OWF3 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | OWF3 275/66kV Offshore Substation | 1 | 0 | 1000 | 1000 | 2031-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l4L0000005iaiQAA | PRO-001406-1 |  | 0
OWPL Windfarm | OFFSHORE WIND POWER LIMITED | OWPL Windfarm Platform 220/66kV Offshore Substation | 2 | 0 | 1500 | 2250 | 2030-12-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l4L0000005iqSQAQ | PRO-000568-2 | OWPL4 | 1500 | OWPL4-
OWPL Windfarm | OFFSHORE WIND POWER LIMITED | OWPL Windfarm Platform 220/66kV Offshore Substation | 1 | 0 | 750 | 750 | 2029-12-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l4L0000005iqSQAQ | PRO-000568-1 | OWPL4 | 750 | OWPL4-
Oak Holt Solar | RWE RENEWABLES UK SOLAR AND STORAGE LIMITED | Trent Vally North Connection Node C 400kv Substation |  | 0 | 400 | 400 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012hpYAAQ | PRO-004539 |  | 0
Oaklands Farm Solar PV | BAYWA R.E. UK LIMITED | Drakelow 132kV Substation |  | 0 | 162.3 | 162.3 | 2025-06-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iz6QAA | PRO-001004 | DRAK1 | 162.3 | DRAK11
Oakley | SSE DE SOLAR HOLDCO LIMITED | Oakley 400kV Substation |  | 0 | 600 | 600 | 2038-11-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f414AAA | PRO-003818 |  | 0
Ochill BESS | CARLTON POWER LIMITED | Ochill 132kV Substation |  | 0 | 49.5 | 49.5 | 2028-08-18 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005jAlQAI | PRO-002536 |  | 49.5
Ocker Hill - Gresham House | Gresham House Devco Pipeline Limited | Ocker Hill 275kV Substation |  | 0 | 240 | 240 | 2027-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iuBQAQ | PRO-002213 | OCKH21 | 240 | OCKH21
Ocker Hill GSP | National Grid Electricity Distribution (West Midlands) Plc | Ocker Hill C 132kV GSP |  | 0 | 99.4 | 99.4 | 2026-05-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000010ws7AAA | PRO-002924 | OCKH1 | 99.4 | OCKH11
Ocker Hill Tertiary Connection | HD143OCK LTD | Ocker Hill 275kV Substation |  | 57 | 0 | 57 |  | Built | Direct Connection | NGET | Energy Storage System | a0l4L0000005iw7QAA | PRO-000462 | OCKH21 | 57 | OCKH21
Offerton 200MW BESS | Decerna Limited | Offerton 275kV Substation |  | 0 | 200 | 200 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0lJ9000000bldHIAQ | PRO-004910 | OFFE21 | 0 | OFFE21
Old Flatts Farm | Net Zero One Limited | Brinsworth 400kV Substation | 2 | 0 | 750 | 1500 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iQbQAI | PRO-001894-2 | BRIN4 | 0 | BRIN41
Old Flatts Farm | Net Zero One Limited | Brinsworth 400kV Substation | 1 | 0 | 750 | 750 | 2029-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iQbQAI | PRO-001894-1 | BRIN4 | 750 | BRIN41
Old Park Farm | STARLIGHT ENERGY UK LIMITED | Axminster 132kV Substation |  | 0 | 200 | 200 | 2038-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012kfgAAA | PRO-004719 | AXMI1 | 0 | AXMI11
Oldbury (Tertiary) | PIVOTED POWER LLP | Oldbury 275kV Substation | 1 | 0 | 49.9 | 49.9 | 2027-06-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005icoQAA | PRO-001074-1 | OLDB21 | 49.9 | OLDB21
Oldbury (Tertiary) | PIVOTED POWER LLP | Oldbury 275kV Substation | 2 | 0 | 7.1 | 57 | 2037-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005icoQAA | PRO-001074-2 | OLDB21 | 0 | OLDB21
Olivers Forest Wind Farm | Oliver Forest Wind Farm Limited | Olivers Forest Wind Farm 132kV Substation |  | 0 | 79.2 | 79.2 | 2031-04-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l8e0000010wVjAAI | PRO-002648 |  | 0
One Earth Solar Farm | ONE EARTH SOLAR FARM LIMITED | High Marnham 400kV Substation |  | 0 | 740 | 740 | 2029-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005izsQAA | PRO-001599 | HIGM4 | 740 | HIGM41
Orddu Energy Park | Orddu Energy Park Limited | Gwyddelwern 400kV Substation |  | 0 | 85.8 | 85.8 | 2037-10-31 | Scoping | Direct Connection | NGET | Wind Onshore | a0l8e000000f4ZAAAY | PRO-003851 | GWYD4 | 0 | GWYD41
Ormonde Offshore Wind Farm | ORMONDE ENERGY LIMITED | Ormonde 33/132kV Offshore Substation |  | 150 | 0 | 150 |  | Built | Direct Connection | OFTO | Wind Offshore | a0l4L0000005iqFQAQ | PRO-000216 | HEYS1 | 150 | HEYS11
Orrin (part of the Conon Cascade) | SSE Generation Limited | Orrin GSP |  | 18 | 0 | 18 |  | Built | Direct Connection | SHET | Hydro | a0l4L0000005ipSQAQ | PRO-000178 | ORRI | 18 | ORRI5-
Osbaldwick PV & BESS Sub | YORK ENERGY PARK LIMITED | Osbaldwick 400kV Substation |  | 0 | 249.9 | 249.9 | 2033-08-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wPCAAY | PRO-002582 | OSBA42 | 0 | OSBA42
Ourack Wind Farm | OURACK WIND FARM LLP | Ourack Wind Farm 132/33 kV Substation |  | 0 | 105 | 105 | 2030-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l4L0000005izDQAQ | PRO-001490 |  | 105
Ouse Energy Storage | Ouse Energy Limited | Kemsley 400kV Substation |  | 0 | 249 | 249 | 2027-10-27 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iPRQAY | PRO-001861 | KEMS41 | 249 | KEMS41
Overhill Wind Farm | ENERGYFARM UK OVERHILL LLP | Overhill 132kV Substation |  | 0 | 50 | 50 | 2029-06-06 | Consents Approved | Direct Connection | SPT | Wind Onshore | a0l4L0000005inwQAA | PRO-000472 | OHLL1 | 50 | OHLL1-
Overton Green Energy Centre | INNOVA RENEWABLES LIMITED | Overton 400kV Substation |  | 0 | 1025 | 1025 | 2035-10-24 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iwqQAA | PRO-002252 | OVER2 | 0 | OVER21
Overton Solar & Storage Farm | ELEMENTS GREEN LIMITED | Overton 275kV |  | 0 | 1400 | 1400 | 2032-06-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iuEQAQ | PRO-002175 | OVER2 | 0 | OVER21
Oxfordshire Energy Park | Low Carbon Solar Park 40 Limited | Chiltern Connection Node D 400kV |  | 0 | 500 | 500 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001HoTdAAK | PRO-004076 |  | 0
Oykel Wind Farm | STATKRAFT UK LTD | Oykel Wind Farm 132kV Substation |  | 0 | 79.2 | 79.2 | 2032-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l8e0000010wbPAAQ | PRO-002711 |  | 0
PVDP Scarning | SolarFour Ltd | Scarning 400kV Substation |  | 0 | 650 | 650 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f7BeAAI | PRO-003998 |  | 0
PVDP Woodbridge | SolarSeven Ltd | South Anglia Connection Node E 400kV Substation |  | 0 | 610 | 610 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f7BoAAI | PRO-004000 |  | 0
Pamber Farm | Queequeg Renewables Ltd | Bramley |  | 0 | 480 | 480 | 2037-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l8e0000010wg0AAA | PRO-002763 | BRLE4 | 0 | BRLE41
Park Farm Hybrid Solar and BESS | VOLTALIA UK LTD | Patford Bridge 400kV Substation |  | 0 | 332.4 | 332.4 | 2037-10-30 | Scoping | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f4Z5AAI | PRO-003850 | PAFB4B | 0 | PAFB4B
Partridge Farm BESS | Apatura Battery Ltd | Sellindge 400kV Substation |  | 0 | 500 | 500 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TPc5AAG | PRO-003445 | SELL4 | 0 | SELL4A
Patford Bridge Farm | 548 UK INVESTMENT HOLDINGS LIMITED | Patford Bridge 400kV Substation |  | 0 | 200 | 200 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wYiAAI | PRO-002680 | PAFB4A | 0 | PAFB4A
Patford Bridge Farm 2 | 548 UK INVESTMENT HOLDINGS LIMITED | New Patford Bridge 400kV Substation |  | 0 | 700 | 700 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010we4AAA | PRO-002741 | PAFB4 | 0 | PAFB4A
Patford Bridge PV & BESS | NORTHAMPTON ENERGY PARK LIMITED | Patford Bridge 400kV Substation |  | 0 | 249.9 | 249.9 | 2033-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001HrhdAAC | PRO-004213 | PAFB4B | 0 | PAFB4B
Peat Law Renewable Energy Park | VOLTALIA UK LTD | Gala North 400/132kV Substation |  | 0 | 253.28 | 253.28 | 2033-05-30 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0lJ9000000PDr8IAG | PRO-005030 |  | 0
Pelham BESS | PELHAM ENERGY PARK LIMITED | Pelham 400kV Substation |  | 0 | 249.9 | 249.9 | 2032-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000010wVKAAY | PRO-002645 | PELH4 | 0 | PELH41
Pelham Farm 2 | 548 UK INVESTMENT HOLDINGS LIMITED | Pelham 400kV Substation |  | 0 | 700 | 700 | 2032-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010we9AAA | PRO-002742 | PELH4 | 0 | PELH41
Pelham GEC (Ethos Green) | PELHAM GREEN ENERGY CENTRE LTD | Pelham 400kV Substation |  | 0 | 480 | 480 | 2035-05-31 | Awaiting Consents | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l8e000000f7xsAAA | PRO-004021 | PELH4 | 0 | PELH41
Pembroke (spare bay) | ENSO GREEN HOLDINGS LIMITED | Pembroke 132kV Substation |  | 0 | 120 | 120 | 2026-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iokQAA | PRO-000538 | PEMB1 | 120 | PEMB11
Pembroke BESS | RWE Generation UK Plc | Pembroke 400kV Substation |  | 0 | 350 | 350 | 2027-10-29 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005iyYQAQ | PRO-000337 | PEMB4 | 350 | PEMB41
Pembroke BESS and Solar Station | Renesola Hercules Energy 1 Limited | Pembroke 400kV Substation |  | 0 | 99.9 | 99.9 | 2028-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ia1QAA | PRO-002003 | PEMB4 | 99.9 | PEMB41
Pembroke Power Station | RWE Generation UK Plc | Pembroke 400kV Substation |  | 2199 | 0 | 2199 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005imAQAQ | PRO-000056 | PEMB4 | 2199 | PEMB41
Pen Y Cymoedd Wind Farm | PEN Y CYMOEDD WIND FARM LIMITED | Rhigos 400kV Substation |  | 228 | 0 | 228 |  | Built | Direct Connection | NGET | Wind Onshore | a0l4L0000005iwNQAQ | PRO-000217 | RHIG4 | 228 | RHIG41
Pencloe Windfarm | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | 1 | 0 | 85 | 85 | 2025-07-01 | Consents Approved | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l4L0000005isjQAA | PRO-000323-1 | PLOE3 | 85 | PLOE3-
Pencloe Windfarm | PENCLOE WIND ENERGY LIMITED | Pencloe 132/33kV Substation | 2 | 0 | 34 | 119 | 2028-04-01 | Awaiting Consents | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l4L0000005isjQAA | PRO-000323-2 | PLOE3 | 34 | PLOE3-
Peninsula Energy Park | Renantis UK Limited | Taynuilt GSP |  | 0 | 249.9 | 249.9 | 2035-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0lJ9000000blsMIAQ | PRO-004961 | TAYN | 0 | TAYN3-
Penketh Hall Farm | Net Zero One Limited | Fiddlers Ferry 275kV Substation |  | 0 | 249.9 | 249.9 | 2027-09-01 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iYJQAY | PRO-001932 | FIDF2 | 249.9 | FIDF21
Penn Battery Storage | ANGLO ENERGY STORAGE LTD | Penn 275kV Substation |  | 0 | 249 | 249 | 2033-06-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000010wa7AAA | PRO-002696 | PENN2 | 0 | PENN21
Penn Renewable BESS & Substation | O&G Solar (SPV 30) Limited | Penn 132kV Substation |  | 0 | 99.9 | 99.9 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005itsQAA | PRO-002393 | PENN1 | 0 | PENN11
Penninghame Wind Farm | EDF ENERGY RENEWABLES LIMITED | Penninghame Substation |  | 0 | 60 | 60 | 2031-10-31 | Scoping | Direct Connection | SPT | Wind Onshore | a0l8e0000010wm8AAA | PRO-002830 |  | 0
Penrhiwdarren Farm | QAIR RENEWABLES UK LIMITED | Cilfynydd 400kV Substation |  | 0 | 500 | 500 | 2037-09-15 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f41sAAA | PRO-003828 | CILF4 | 0 | CILF41
Pentir Green Energy Centre | INNOVA RENEWABLES LIMITED | Pentir 400kV Substation |  | 0 | 1025 | 1025 | 2037-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005il9QAA | PRO-002345 | PENT4 | 0 | PENT41
Pentland Floating Offshore Wind Farm | HIGHLAND WIND LIMITED | OWF-100 Substation |  | 0 | 100 | 100 | 2027-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l4L0000005idGQAQ | PRO-001472 | OWFD | 100 | OWFD1-
Penwortham BESS | CSE28 LIMITED | Penwortham 400kV Substation |  | 0 | 57 | 57 | 2027-06-01 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ibBQAQ | PRO-002037 | PEWO41 | 57 | PEWO41
Penwortham BESS | Penwortham (BES) Ltd | Penwortham 400kV Substation |  | 0 | 57 | 57 | 2024-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iuXQAQ | PRO-001804 | PEWO41 | 57 | PEWO41
Penwortham Green Energy Centre | PENWORTHAM GREEN ENERGY LIMITED | Penwortham 400kV Substation | 1 | 0 | 400 | 400 | 2026-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ierQAA | PRO-001694-1 | PEWO41 | 400 | PEWO41
Penwortham Green Energy Centre | PENWORTHAM GREEN ENERGY LIMITED | Penwortham 400kV Substation | 2 | 0 | 200 | 600 | 2037-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ierQAA | PRO-001694-2 | PEWO41 | 0 | PEWO41
Perry Barr BESS | Perry Barr Limited | Nechells East GSP |  | 0 | 249 | 249 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000012kikAAA | PRO-004745 | NECH | 0 | NECH11
Peterhead | SSE THERMAL GENERATION (SCOTLAND) LIMITED | Peterhead GSP |  | 1180 | 0 | 1180 |  | Built | Direct Connection | SHET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005impQAA | PRO-000082 | PEHE | 1180 | PEHE4J
Peterhead Battery | PETERHEAD FLEXPOWER LTD | Peterhead GSP |  | 0 | 500 | 500 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l4L0000005iZdQAI | PRO-001999 | PEHE | 0 | PEHE1-
Peterhead Carbon Capture | SSE THERMAL GENERATION (SCOTLAND) LIMITED | Peterhead 275kV |  | 0 | 910 | 910 | 2033-10-31 | Scoping | Direct Connection | SHET | CCGT (Combined Cycle Gas Turbine) | a0l8e0000012hooAAA | PRO-004529 | PEHE2 | 0 | PEHE2-
Peterhead PV and BESS Station | ETP UK 2 LTD | New Deer 2 400kV Substation |  | 0 | 480 | 480 | 2033-10-31 | Awaiting Consents | Direct Connection | SHET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wh3AAA | PRO-002775 | NEDE4 | 0 | NEDE4J
Petroc Extension Offshore Wind Farm | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Alverdiscott 400kV Substation |  | 0 | 1000 | 1000 | 2036-12-06 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005iM5QAI | PRO-002404 | ALVE4A | 0 | ALVE4A
Petroc Offshore Wind Farm | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Alverdiscott 400kV Substation |  | 0 | 300 | 300 | 2029-03-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005j1UQAQ | PRO-001661 | ALVE4A | 300 | ALVE4A
Philiphaugh Wind Farm | EDF ENERGY RENEWABLES LIMITED | Philipaugh Substation |  | 0 | 175 | 175 | 2033-05-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l8e0000010wbAAAQ | PRO-002708 |  | 0
Phoenix 1B Offshore Wind Farm | BP ALTERNATIVE ENERGY INVESTMENTS LIMITED | Phoenix 1B 275/66kV Offshore Substation |  | 0 | 1500 | 1500 | 2033-10-31 | Scoping | Direct Connection | SPT | Wind Offshore | a0l4L0000005izKQAQ | PRO-001519 |  | 0
Pittlesheugh Farm | Pittlesheugh Farm BESS Limited | Eccles 400/132kV |  | 0 | 340 | 340 | 2030-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L000002yQXdQAM | PRO-002547 | ECCL1 | 340 | ECCL1-
Pivot Power Harker Hybrid | PIVOTED POWER LLP | Harker 400kV Substation |  | 0 | 57 | 57 | 2029-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iu0QAA | PRO-001065 | HARG4 | 57 | HARG41
Plas Power Estate North Tertiary | LIGHTSOURCE SPV 192 LIMITED | Legacy 400kV Substation |  | 0 | 57 | 57 | 2026-08-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ixJQAQ | PRO-001050 | LEGA41 | 57 | LEGA41
Pogbie Wind Farm | POGBIE WIND FARM (GRID) LIMITED | Pogbie 33kV |  | 9.6 | 0 | 9.6 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005irKQAQ | PRO-000263 | POGB3 | 9.6 | POGB3-
Pollington Hybrid | EDF ENERGY RENEWABLES LIMITED | Leeds North Connection Node B 400kV Substation |  | 0 | 440 | 440 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0lJ9000000PDtYIAW | PRO-005049 |  | 0
Pond Flexible Energy Park | Pond Flexible Energy Park Limited | Bathgate 132/33kV Substation |  | 0 | 200 | 200 | 2031-06-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000TPDMAA4 | PRO-003201 | BAGA1 | 0 | BAGA1Q
Pond Hill Farm 1 | PD688IRO LTD | Minety 400kV Substation |  | 0 | 47.5 | 47.5 | 2025-04-30 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005ixqQAA | PRO-001637 | MITY4 | 47.5 | MITY41
Pond Hill Farm 2 BESS | PD688IRO LTD | Minety 400kV Substation |  | 0 | 47.5 | 47.5 | 2025-05-31 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005ixzQAA | PRO-001635 | MITY4 | 47.5 | MITY41
Poppleton GSP | NORTHERN POWERGRID (NORTHEAST) PLC | Poppleton 275kV Substation |  | 0 | 57 | 57 | 2039-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;Thermal | a0l8e0000010wvGAAQ | PRO-002967 | POPP2 | 0 | POPP21
Poppleton PV & BESS Sub | YORK ENERGY PARK LIMITED | Thormanby 400kV Substation |  | 0 | 249.9 | 249.9 | 2035-10-24 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wV5AAI | PRO-002642 |  | 0
Port of Mostyn | MOSTYN SEAPOWER LIMITED | Connah's Quay 400kV Substation | 1 | 0 | 70 | 70 | 2030-12-01 | Scoping | Direct Connection | NGET | Tidal | a0l4L0000005imFQAQ | PRO-000421-1 | CONQ4 | 70 | CONQ41
Port of Mostyn | MOSTYN SEAPOWER LIMITED | Connah's Quay 400kV Substation | 2 | 0 | 140 | 210 | 2031-06-01 | Scoping | Direct Connection | NGET | Tidal | a0l4L0000005imFQAQ | PRO-000421-2 | CONQ4 | 0 | CONQ41
Port of Mostyn | MOSTYN SEAPOWER LIMITED | Connah's Quay 400kV Substation | 3 | 0 | 210 | 420 | 2032-01-01 | Scoping | Direct Connection | NGET | Tidal | a0l4L0000005imFQAQ | PRO-000421-3 | CONQ4 | 0 | CONQ41
Portwind | SOURCE ENERGIE LIMITED | Chickerell 400kV Substation |  | 0 | 2500 | 2500 | 2036-12-06 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Offshore | a0l4L0000005ibKQAQ | PRO-002046 | CHIC4A | 0 | CHIC4A
Powersite @ Drakelow | POWERSITE LTD | Drakelow 400kV Substation |  | 0 | 380 | 380 | 2020-10-01 | Under Construction/Commissioning | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005ilFQAQ | PRO-000364 | DRAK4 | 380 | DRAK41
Priestgill Wind Farm | PRIESTGILL WIND FARM LIMITED | Elvanfoot 400/275/33kV |  | 0 | 43.63 | 43.63 | 2026-11-30 | Consents Approved | Direct Connection | SPT | Wind Onshore | a0l4L0000005imsQAA | PRO-000448 | ELVA3 | 43.63 | ELVA3A
Progress Power Station | PROGRESS POWER LIMITED | Yaxley 400kV Substation |  | 0 | 299 | 299 | 2024-06-28 | Under Construction/Commissioning | Direct Connection | NGET | OCGT (Open Cycle Gas Turbine) | a0l4L0000005irqQAA | PRO-000274 | YAXL4 | 299 | YAXL41
Project Invicta | The Farm Energy Company Limited | East Kent Connection Node B 400kV Substation |  | 0 | 340 | 340 | 2036-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001Hpe8AAC | PRO-004133 | CANT4 | 0 | CANT41
Project Number 4 | Greta IV Limited | North Anglia Connection Node B 400kV Substation |  | 0 | 500 | 500 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010walAAA | PRO-002704 |  | 0
Project Number 6 | Trent BESS II Limited | Cottam 400kV Substation |  | 0 | 500 | 500 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000exuGAAQ | PRO-003748 | COTT4 | 0 | COTT41
Project Number 8 | Trent BESS I Limited | Trent Valley South Connection Node B 400kV Substation. |  | 0 | 500 | 500 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001HoKyAAK | PRO-004072 |  | 0
Protos Power Station | KEADBY GENERATION LIMITED | Elton 400kV Substation |  | 0 | 910 | 910 | 2037-11-01 | Scoping | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l8e0000010wlUAAQ | PRO-002823 |  | 0
Quantans Hill Wind Farm | VATTENFALL WIND POWER LTD | Quantans Hill 132kV Substation |  | 0 | 95 | 95 | 2029-07-02 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005iOeQAI | PRO-001247 | QUAN1 | 95 | QUAN1-
Quintfall Forest Hybrid Wind and BESS 1 | VOLTALIA UK LTD | Gills Bay 132kV |  | 0 | 98.5 | 98.5 | 2037-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0lJ9000000POPvIAO | PRO-006032 |  | 0
Race Bank Wind Farm | RACE BANK WIND FARM LIMITED | Race Bank 132kV Substation |  | 565 | 0 | 565 |  | Built | Direct Connection | NGET | Wind Offshore | a0l4L0000005iqCQAQ | PRO-000213 | WALP4 | 565 | WALP41
Rampion Extension Offshore Wind Farm | RAMPION EXTENSION DEVELOPMENT LIMITED | Rampion Offshore Wind Farm |  | 0 | 1200 | 1200 | 2026-08-01 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005io1QAA | PRO-000467 | BOLN4 | 1200 | BOLN41
Rampion Offshore Wind Farm | RAMPION OFFSHORE WIND LIMITED | Rampion 33/132kV Offshore |  | 400 | 0 | 400 |  | Built | Direct Connection | NGET | Wind Offshore | a0l4L0000005iqoQAA | PRO-000248 | BOLN4 | 400 | BOLN41
Ranby | SSE DE SOLAR HOLDCO LIMITED | Jubilee Farm 275kV Substation |  | 0 | 600 | 600 | 2034-08-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L000002yQa8QAE | PRO-002557 | HIGM2 | 0 | HIGM41
Rassau | ENSO GREEN HOLDINGS LIMITED | Rassau 400kV Substation |  | 0 | 400 | 400 | 2030-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l4L0000005idkQAA | PRO-002087 | RASS4 | 400 | RASS41
Rassau Stability Services Limited | WP Grid Services 16 Limited | Rassau 400kV Substation |  | 0 | 0 | 0 | 2037-10-31 | Scoping | Direct Connection | NGET | Reactive Compensation | a0l8e000000f5XsAAI | PRO-003931 | RASS4 | 0 | RASS41
Rat Hall Mod App | Downing Renewable Developments LLP | Burwell South 400kV Substation | 1 | 0 | 200 | 200 | 2032-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f41YAAQ | PRO-003824-1 | BURW4 | 0 | BURW41
Rat Hall Mod App | Downing Renewable Developments LLP | Burwell South 400kV Substation | 2 | 0 | 500 | 700 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f41YAAQ | PRO-003824-2 | BURW4 | 0 | BURW41
Rat Hall Solar | Downing Renewable Developments LLP | Burwell South 400kV Substation |  | 0 | 200 | 200 | 2032-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f4xCAAQ | PRO-003892 | BURW4 | 0 | BURW41
Ratcliffe on Soar | UNIPER UK LIMITED | Ratcliffe-On-Soar 400kV Substation |  | 225 | 0 | 225 |  | Built | Direct Connection | NGET | OCGT (Open Cycle Gas Turbine) | a0l4L0000005izSQAQ | PRO-000050 | RATS4 | 225 | RATS41
Ratcliffe on Soar Farm | KEGWORTH 10 RENEWABLES LTD | Kegworth B 400kV Substation |  | 0 | 1000 | 1000 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f4nFAAQ | PRO-003871 | RATS4 | 0 | RATS41
Ratcliffe-on-Soar | ENSO GREEN HOLDINGS C LIMITED | Ratcliffe-On-Soar 132kV Substation |  | 0 | 190 | 190 | 2029-07-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iyvQAA | PRO-001361 | RATS1 | 190 | RATS11
Ratcliffe-on-Soar II | ENSO GREEN HOLDINGS LIMITED | Ratcliffe-On-Soar 400kV Substation |  | 0 | 590 | 590 | 2033-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005itNQAQ | PRO-002158 | RATS4 | 0 | RATS41
Rattray BESS and Solar Plant | GREENTECH PROJECTS HOLDING UK LIMITED | St Fergus |  | 0 | 300 | 300 | 2037-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0lJ9000000POaOIAW | PRO-006056 |  | 0
Ravengill Renewable Energy Park | RENEWCO POWER LIMITED | Elvanfoot 275/132/33kV |  | 0 | 249.9 | 249.9 | 2036-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e000001HxRSAA0 | PRO-004257 | ELVA1 | 0 | ELVA1-
Rawhills Battery Energy Storage Facility | ALCEMI STORAGE DEVELOPMENTS 6 LIMITED | Coalburn 400kV GIS Substation |  | 0 | 500 | 500 | 2027-04-16 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005ifjQAA | PRO-001503 | COAL4 | 500 | COAL4-
Rayleigh 1 Tertiary | RAYLEIGH GREEN LIMITED | Rayleigh Main 400kV Substation |  | 0 | 47.5 | 47.5 | 2028-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005io4QAA | PRO-000460 | RAYL41 | 47.5 | RAYL41
Rayleigh 2 Tertiary | ENSO GREEN HOLDINGS LIMITED | Rayleigh Main 400kV Substation |  | 0 | 47.5 | 47.5 | 2028-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005io2QAA | PRO-000466 | RAYL41 | 47.5 | RAYL41
Red House Farm - Friston 400kV 249MW connection | CAMBRIDGE POWER LIMITED | South Anglia Connection Node E 400kV Substation |  | 0 | 249 | 249 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000ez2cAAA | PRO-003787 |  | 0
Red Moss Farm | QAIR RENEWABLES UK LIMITED | Red Moss Farm 132kV Substation |  | 0 | 300 | 300 | 2030-10-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000010wSfAAI | PRO-002613 | REDM1 | 300 | REDM1Q
Redhall BESS | ANESCO LIMITED | Wearside Connection Node D 400kV Substation |  | 0 | 300 | 300 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000012gtaAAA | PRO-004487 |  | 0
Redshaw Energy Park | BAYWA R.E. UK LIMITED | Linnmill 132/33kV |  | 0 | 500 | 500 | 2031-10-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000f6bGAAQ | PRO-003982 | LINM1 | 0 | LINM1Q
Rhigos BESS | Enviromena Project Management UK Limited | Rhigos B Substation |  | 0 | 221 | 221 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000010wSuAAI | PRO-002616 | RHIG4 | 0 | RHIG41
Rhigos BESS | KONA ASSET 4 LIMITED | South Wales West Connection Node A 400kV Substation |  | 0 | 225 | 225 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001205tAAA | PRO-003613 | RHIG4 | 0 | RHIG41
Rhigos BESS | REWE 11 Limited | South Wales West Connection Node A 400kV Substation |  | 0 | 200 | 200 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001HpCVAA0 | PRO-004109 | RHIG4 | 0 | RHIG41
Riccarton | M2 Energy Storage Limited | Currie 275/132kV |  | 0 | 150 | 150 | 2029-04-13 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010xS4AAI | PRO-003066 | CURR1 | 150 | CURR1A
Richborough 1 | RICHBOROUGH ENERGY PARK LIMITED | Richborough 400kV Substation |  | 50 | 0 | 50 |  | Built | Direct Connection | NGET | Energy Storage System | a0l4L0000005j01QAA | PRO-001165 | RICH4 | 50 | RICH41
Richborough 2 | RICHBOROUGH ENERGY PARK LIMITED | Richborough 400kV Substation |  | 50 | 0 | 50 |  | Built | Direct Connection | NGET | Energy Storage System | a0l4L0000005j02QAA | PRO-001164 | RICH4 | 50 | RICH41
Rigifa BESS | FIELD DEVCO LTD | Gills Bay 132kV |  | 0 | 200 | 200 | 2029-12-12 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000010wfRAAQ | PRO-002758 | GILB1 | 200 | GILB1J
Rivox Wind Farm | RIVOX WIND ENERGY HUB LIMITED | Rivox 132/33kV |  | 0 | 220 | 220 | 2031-10-10 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l4L0000005iYSQAY | PRO-001944 |  | 0
Robin Rigg East Offshore Wind Farm | RWE RENEWABLES UK ROBIN RIGG EAST LIMITED | Robin Rigg East 132/33kV Offshore Substation |  | 86 | 0 | 86 |  | Built | Direct Connection | OFTO | Wind Offshore | a0l4L0000005ipaQAA | PRO-000194 | HARG1 | 86 | HARG11
Robin Rigg West Offshore Wind Farm | RWE RENEWABLES UK ROBIN RIGG WEST LIMITED | Robin Rigg West Offshore Wind Farm Substation |  | 92 | 0 | 92 |  | Built | Direct Connection | OFTO | Wind Offshore | a0l4L0000005ipbQAA | PRO-000195 | HARG1 | 92 | HARG11
Rochdale BESS | Rochdale (BES) Ltd | Rochdale 275kV Substation |  | 0 | 57 | 57 | 2027-07-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iuUQAQ | PRO-001805 | ROCH2 | 57 | ROCH21
Rochester Renewable Project | VATTENFALL WIND POWER LTD | Kingsnorth 132kV Substation |  | 0 | 60 | 60 | 2028-09-22 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l4L0000005iwrQAA | PRO-002097 | KINO1 | 60 | KINO11
Rocksavage | ROCKSAVAGE POWER COMPANY LTD | Rocksavage 400kV Substation |  | 810 | 0 | 810 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005iq3QAA | PRO-000204 | ROCK4 | 810 | ROCK41
Roger Hill Farm | QAIR RENEWABLES UK LIMITED | Roger Hill Farm 132kV substation |  | 0 | 200 | 200 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000exIjAAI | PRO-003708 |  | 0
Rosefield | Rosefield Energyfarm Limited | East Claydon 400kV Substation |  | 0 | 500 | 500 | 2031-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iwIQAQ | PRO-001044 | ECLA4 | 0 | ECLA41
Rothienorman Battery | Rothienorman Flexpower A Ltd | Rothienorman 400kV Substation |  | 0 | 500 | 500 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l4L0000005iZ1QAI | PRO-001971 | ROTI4 | 0 | ROTI4J
Rothienorman Sync Comp | ROTHIENORMAN GRID SERVICES LIMITED | Rothienorman 400kV Substation |  | 0 | 0 | 0 |  | Built | Direct Connection | SHET | Reactive Compensation | a0l4L0000005ibtQAA | PRO-001445 | ROTI4 | 0 | ROTI4J
Rowan Wind Energyfarm | ENERGYFARM ROWAN LLP | Crossaig 132kV Substation |  | 0 | 90.8 | 90.8 | 2034-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l8e000000f41TAAQ | PRO-003823 | CRSS1 | 0 | CRSS1J
Rowancraig Wind Farm | Koehler Renewable Energy UK Limited | Glenglass 132/33kV |  | 0 | 40 | 40 | 2028-10-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005iMUQAY | PRO-002455 | GLGL3 | 40 | GLGL3-
Rugby High Impact Green Energy Hub (HIGEH) 1 | TELIS ENERGY UK LIMITED | Enderby 400kV Substation |  | 0 | 1000 | 1000 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;Nuclear;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e00000120NcAAI | PRO-003626 | ENDE4 | 0 | ENDE41
Rugeley | IGP SOLAR 17 LIMITED | Rugeley 400kV Substation |  | 0 | 600 | 600 | 2031-08-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iNWQAY | PRO-001630 | RUGE4 | 0 | RUGE41
Rugeley | RUGELEY POWER GENERATION LIMITED | Rugeley GSP |  | 0 | 50 | 50 | 2032-10-30 | Scoping | Direct Connection | NGET | Coal | a0l4L0000005iq8QAA | PRO-000209 | RUGE4 | 0 | RUGE41
Rugeley Battery Storage | RUGELEY POWER GENERATION LIMITED | Rugeley 400kV Substation |  | 0 | 400 | 400 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iu9QAA | PRO-002215 | RUGE4 | 0 | RUGE41
Rutherend Farm | ECOCEL ENERGY (STORAGE) LTD | East Kilbride 275kV Substation |  | 0 | 200 | 200 | 2033-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000012hotAAA | PRO-004530 | EKIL2 | 0 | EKIL2Q
Rye House | RYE HOUSE 10 RENEWABLES LIMITED | London North East Connection Node A |  | 0 | 1000 | 1000 | 2031-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000TPRAAA4 | PRO-003413 |  | 0
Rye House | VPI POWER LIMITED | Rye House GSP |  | 715 | 0 | 715 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005ipYQAQ | PRO-000191 | RYEH41 | 715 | RYEH41
Rye House (Tertiary) | ENSO GREEN HOLDINGS N LIMITED | Rye House 400kV Substation |  | 0 | 57 | 57 | 2027-06-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005izaQAA | PRO-000564 | RYEH41 | 57 | RYEH41
Ryhall Farm | 548 UK INVESTMENT HOLDINGS LIMITED | Casewick 400kV Substation |  | 0 | 200 | 200 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wZ2AAI | PRO-002684 | RYHA4 | 0 | RYHA4A
Ryhall PV & BESS | GREAT CASTERTON ENERGY PARK LIMITED | Ryhall 400kV Substation |  | 0 | 400 | 400 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012eoUAAQ | PRO-004379 | RYHA41 | 0 | RYHA4A
SAE Usk 1 | SIMEC USKMOUTH POWER LIMITED | South Wales East Node A 275kV Substation |  | 0 | 349 | 349 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000011zZ5AAI | PRO-003590 | USKM2 | 0 | USKM21
SAGE Solar | SAGE NORTH SEA LIMITED | St Fergus Mobil |  | 0 | 20 | 20 | 2025-06-30 | Scoping | Direct Connection | SHET | Demand;PV Array (Photo Voltaic/solar) | a0l4L0000005iybQAA | PRO-002119 | PEHE | 20 | PEHE1-
SANDFORD | SSE DE SOLAR HOLDCO LIMITED | Sandford 400kV |  | 0 | 600 | 600 | 2037-10-20 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wRXAAY | PRO-002600 | SAFO4 | 0 | SAFO41
SAVE OUR PLANET | SAVE OUR PLANET ENERGY LIMITED | DRAGON GREEN 400kV SUBSTATION |  | 0 | 500 | 500 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012iy3AAA | PRO-004613 | LOVE4 | 0 | LOVE41
SHBEC | EP SHB LIMITED | South Humber Bank 400kV Substation |  | 0 | 83 | 83 | 2029-07-01 | Consents Approved | Direct Connection | NGET | Waste | a0l4L0000005itJQAQ | PRO-001096 | SHBA4 | 83 | SHBA41
SPITTAL MAINS BATTERY ENERGY STORAGE | WRE Broomhill Limited | Spittal 275kV Substation |  | 0 | 200 | 200 | 2030-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l4L0000005j8zQAA | PRO-002523 | SPIT2 | 200 | SPIT2J
SPR CS1 | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Alverdiscott 400kV Substation |  | 0 | 1000 | 1000 | 2037-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l8e0000011xxKAAQ | PRO-003484 | ALVE4A | 0 | ALVE4A
SSE Celtic Sea 1 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Alverdiscott 400kV Substation |  | 0 | 1500 | 1500 | 2036-12-06 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005iyPQAQ | PRO-002405 | ALVE4A | 0 | ALVE4A
SSE Ferrybridge BESS | SSE UTILITY SOLUTIONS LIMITED | Ferrybridge B 132kV Substation |  | 0 | 150 | 150 | 2024-06-28 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005ikAQAQ | PRO-001614 | FERR1 | 150 | FERR11
SSE Fiddlers Ferry Battery Energy Storage | SSE UTILITY SOLUTIONS LIMITED | Fiddlers Ferry 275kV Substation |  | 0 | 150 | 150 | 2025-04-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005ihmQAA | PRO-001762 | FIDF2 | 150 | FIDF21
SSE Offshore 1 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 1 400/66KV OFFSHORE SUBSTATION |  | 0 | 1320 | 1320 | 2033-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005iecQAA | PRO-001488 |  | 0
SSE Offshore 2 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE OFFSHORE 2 220/66KV OFFSHORE SUBSTATION |  | 0 | 600 | 600 | 2031-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005ieeQAA | PRO-001491 |  | 0
SSE Offshore 3 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | SSE Offshore 3 220/66kV Offshore Substation |  | 0 | 600 | 600 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l4L0000005iedQAA | PRO-001489 |  | 0
SSE Offshore 4 | SSE RENEWABLES OFFSHORE WINDFARM HOLDINGS LIMITED | Cousland 400kV |  | 0 | 1008 | 1008 | 2033-10-31 | Scoping | Direct Connection | SPT | Wind Offshore | a0l4L0000005iwQQAQ | PRO-002145 | TORN4 | 0 | TORN4-
SSE Spittal Energy Park | SSE DE SOLAR HOLDCO LIMITED | Spittal 400kV |  | 0 | 600 | 600 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000TPKSAA4 | PRO-003259 | SPIT4 | 0 | SPIT1J
STABLE GREEN ENERGY | LH NGET GRID SERVICES LIMITED | Sussex and Romney Connection Node A 400kV Substation |  | 0 | 500 | 500 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001HxRDAA0 | PRO-004254 |  | 0
STALLINGBOROUGH CARBON CAPTURE CCGT | RWE STALLINGBOROUGH LIMITED | Grimsby West 400kV Substation |  | 0 | 906 | 906 | 2035-05-30 | Scoping | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine);Demand | a0l8e000000f4mvAAA | PRO-003867 | GRIW4 | 0 | GRIW41
Salamander Offshore Wind Farm | SALAMANDER WIND PROJECT COMPANY LIMITED | Peterhead GSP |  | 0 | 200 | 200 | 2029-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l4L0000005ifrQAA | PRO-001512 | PEHE | 200 | PEHE1-
Saltcoats NEP BESS Facility | NEW ENERGY PARTNERSHIP LIMITED | Saltcoats 132/33kV |  | 0 | 100 | 100 | 2029-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000010wkgAAA | PRO-002813 | SACO3 | 100 | SACO3J
Saltend | Saltend Cogeneration Company Limited | Saltend South 400kV Substation |  | 1100 | 0 | 1100 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005imDQAQ | PRO-000059 | SAES2 | 1100 | SAES21
Saltend North BESS & PV | EEB74 LIMITED | Hedon 275kV Substation |  | 0 | 200 | 200 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005itUQAQ | PRO-002236 | SAEN1 | 0 | SAEN11
Salters Battery Storage | BUCCLEUCH ESTATES LTD (THE) | Dalkeith 400kV Substation |  | 0 | 200 | 200 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000001HpjiAAC | PRO-004150 | SMEA2 | 0 | SMEA2-
Saltholme BESS | Harmony SH Limited | Saltholme 275kV Substation |  | 0 | 200 | 200 | 2035-10-26 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000010xJ0AAI | PRO-003057 | SALH2 | 0 | SALH21
Sand Quarry Old Glasgow Road BESS | GPC 1134 Ltd | Kilwinning GSP |  | 0 | 100 | 100 | 2029-05-07 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000010wavAAA | PRO-002706 | KILW | 100 | KILW3-
Sandy Knowe Wind Farm | SANDY KNOWE WIND FARM LIMITED | Sandyknowe 132/33kV | 2 | 0 | 21.6 | 108 | 2027-10-31 | Awaiting Consents | Direct Connection | SPT | Wind Onshore | a0l4L0000005it1QAA | PRO-000345-2 | SAKN1 | 21.6 | SAKN1-
Sandy Knowe Wind Farm | SANDY KNOWE WIND FARM LIMITED | Sandyknowe 132/33kV | 1 | 86.4 | 0 | 86.4 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005it1QAA | PRO-000345-1 | SAKN1 | 86.4 | SAKN1-
Sanquhar II Wind Farm | SANQUHAR II COMMUNITY WIND CO LTD | Glenglass 132kV Substation | 2 | 0 | 113 | 250 | 2027-02-28 | Consents Approved | Direct Connection | SPT | Wind Onshore | a0l4L0000005it6QAA | PRO-000352-2 |  | 113
Sanquhar II Wind Farm | SANQUHAR II COMMUNITY WIND CO LTD | Glenglass 132kV Substation | 1 | 0 | 137 | 137 | 2026-07-31 | Consents Approved | Direct Connection | SPT | Wind Onshore | a0l4L0000005it6QAA | PRO-000352-1 |  | 137
Sanquhar Wind Farm | SANQUHAR COMMUNITY WIND COMPANY LIMITED | Sanquhar 132/33kV |  | 30 | 0 | 30 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005iZ8QAI | PRO-001366 | SNQR3 | 30 | SNQR3-
Scaraben Offshore Wind Farm | BLUEFLOAT ENERGY UK HOLDINGS LIMITED | Scaraben 132kV Offshore Substation |  | 0 | 100 | 100 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l4L0000005iulQAA | PRO-002401 | SCRA1 | 0
Scarning | CONNECTID 3 LIMITED | North Anglia Connection Node C 400kV Substation |  | 0 | 800 | 800 | 2034-10-31 | Scoping | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l8e000000TPN2AAO | PRO-003275 |  | 0
Scatsta Greener Grid Park | STATKRAFT UK LTD | Scatsta 132kV |  | 0 | 49.9 | 49.9 | 2028-10-31 | Scoping | Direct Connection | SHET | Demand;Energy Storage System | a0l4L0000005iYqQAI | PRO-001955 |  | 49.9
Scatsta1 Greener Grid Park | STATKRAFT UK LTD | Scatsta 132kV |  | 0 | 5 | 5 | 2028-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000010wXpAAI | PRO-002669 |  | 5
Scaw Law Wind Farm | ORSTED ONSHORE UK LIMITED | Scaw Law 132kV substation |  | 0 | 60 | 60 | 2036-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l8e000001Hr2mAAC | PRO-004174 |  | 0
Scawd Law Wind Farm | FRED. OLSEN RENEWABLES LIMITED | Gala North 400/132kV Substation |  | 0 | 64 | 64 | 2032-04-30 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0lJ9000000PF4WIAW | PRO-005865 |  | 0
Scira-Dudgeon Extension | EQUINOR NEW ENERGY LIMITED | Norwich Main 400kV Substation | 1 | 0 | 719 | 719 | 2030-01-01 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005izYQAQ | PRO-000507-1 | NORM41 | 719 | NORM41
Scira-Dudgeon Extension | EQUINOR NEW ENERGY LIMITED | Norwich Main 400kV Substation | 2 | 0 | 231 | 950 | 2031-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005izYQAQ | PRO-000507-2 | NORM42 | 0 | NORM41
Scira-Dudgeon Extension | EQUINOR NEW ENERGY LIMITED | Norwich Main 400kV Substation | 3 | 0 | 400 | 1350 | 2034-10-01 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005izYQAQ | PRO-000507-3 | NORM41 | 0 | NORM41
Sclenteuch Energy Park | Renewable Energy Systems Limited | Sclenteuch Energy Park 132kV |  | 0 | 54 | 54 | 2029-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l4L0000005iuvQAA | PRO-002195 |  | 54
Scoop Hill Wind Farm | CWP Energy Limited | Scoop Hill Wind Farm 132kV Substation |  | 0 | 500 | 500 | 2027-10-31 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005ismQAA | PRO-000327 |  | 500
Scotsburn Road | TBC 002 LIMITED | Fyrish 275kV Substation |  | 0 | 170 | 170 | 2030-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l4L0000005iM8QAI | PRO-002376 | FYRI2 | 170 | FYRI2J
Seabank | SEABANK POWER LIMITED | Seabank 400kV Substation |  | 1234 | 0 | 1234 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005im6QAA | PRO-000052 | SEAB4 | 1234 | SEAB41
Seabank (Tertiary) | PIVOTED POWER LLP | Seabank 400kV Substation |  | 0 | 49.9 | 49.9 | 2023-11-01 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005icuQAA | PRO-001068 | SEAB4 | 49.9 | SEAB41
Seagreen 1 Offshore Wind Farm | Seagreen Wind Energy Limited | Tealing 275/33kV Substation |  | 1075 | 0 | 1075 |  | Built | Direct Connection | SHET | Wind Offshore | a0l4L0000005ipFQAQ | PRO-000527 | TEAL2 | 1075 | TEAL2A
Seagreen 1A Offshore Wind Farm | SEAGREEN 1A LIMITED | Cockenzie 400/275kV |  | 0 | 500 | 500 | 2028-04-01 | Under Construction/Commissioning | Direct Connection | SPT | Wind Offshore | a0l4L0000005izHQAQ | PRO-000703 | COCK4 | 500 | COCK4Q
Sealtainn Offshore Wind Farm | Shetland Offshore Wind Limited | Sealtainn 275kV Offshore |  | 0 | 500 | 500 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l8e0000010wXuAAI | PRO-002670 |  | 0
Seat Hill Wind Farm | ORSTED ONSHORE UK LIMITED | Seat Hill 132kV Substation |  | 0 | 90 | 90 | 2035-10-30 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0lJ9000000PEyBIAW | PRO-005850 |  | 0
Sellindge (Tertiary) | PIVOTED POWER LLP | Sellindge 400kV Substation |  | 0 | 49.9 | 49.9 | 2024-11-01 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005icvQAA | PRO-001067 | SELL4 | 49.9 | SELL4A
Sellindge Grid Stability Services | SELLINDGE GRID SERVICES LIMITED | Sellindge 400kV Substation |  | 0 | 0 | 0 | 2026-08-11 | Consents Approved | Direct Connection | NGET | Reactive Compensation | a0l4L0000005ikiQAA | PRO-002206 | SELL4 | 0 | SELL4A
Sellindge West | Sellindge West 10 Renewables Limited | East Kent connection node A 400kV Substation |  | 0 | 1000 | 1000 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000TPR5AAO | PRO-003412 | SELL4 | 0 | SELL4A
Severn Power | SEVERN POWER LIMITED | Uskmouth 275kV Substation |  | 850 | 0 | 850 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005iq4QAA | PRO-000205 | USKM21 | 850 | USKM21
Sheaf Energy | SHEAF ENERGY LIMITED | Richborough 400kV Substation |  | 0 | 249 | 249 | 2025-04-30 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005ihYQAQ | PRO-001745 | RICH4 | 249 | RICH41
Sheilhill Battery Storage | Sheilhill Battery Storage Limited | St Fergus |  | 0 | 100 | 100 | 2033-10-31 | Awaiting Consents | Direct Connection | SHET | Demand;Energy Storage System | a0l4L0000005ivQQAQ | PRO-002149 | PEHE | 0 | PEHE1-
Sheirdrim Wind Farm | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Sheirdrim 132kV Substation |  | 0 | 84 | 84 | 2032-04-01 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005icwQAA | PRO-001066 |  | 0
Shepherds Rig Wind Farm | SETT WIND DEVELOPMENT LIMITED | Shepherds Rig Wind Farm 132kV Substation |  | 0 | 84.6 | 84.6 | 2024-07-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005io9QAA | PRO-000511 | SHRG1 | 84.6 | SHRG1T
Sheringham Shoal Offshore Wind Farm | SCIRA OFFSHORE ENERGY LIMITED | Sheringham Shoal 33/132kV Offshore Substations |  | 315 | 0 | 315 |  | Built | Direct Connection | OFTO | Wind Offshore | a0l4L0000005iqAQAQ | PRO-000211 | NORM1 | 315 | NORM11
Shipley Road BESS | CSE43 LIMITED | DRAGON GREEN 400kV SUBSTATION |  | 0 | 400 | 400 | 2031-10-21 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L000002yQZoQAM | PRO-002553 | LOVE4 | 0 | LOVE41
Shotwick BESS | Shotwick Land Limited | Capenhurst 400kV Substation |  | 0 | 349.99 | 349.99 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000011yOzAAI | PRO-003515 | CAPE4 | 0 | CAPE4A
Shropshire Energy Park | LOW CARBON SOLAR PARK 34 LIMITED | Shrewsbury 400kV Substation |  | 0 | 500 | 500 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000TPAhAAO | PRO-003172 | SHRE4 | 0 | SHRE4A
Shurton BESS | FIELD DEVCO LTD | West Country Connection Node D 400kV Substation |  | 0 | 200 | 200 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001HxQjAAK | PRO-004248 |  | 0
Siddington BESS Station | IB VOGT UK LTD | Daines 400kV Substation |  | 0 | 240 | 240 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f5zzAAA | PRO-003942 | DAIN4 | 0 | DAIN41
Sinclair Offshore Wind Farm | SINCLAIR OFFSHORE WIND FARM LIMITED | Peterhead 400kV Substation |  | 0 | 100 | 100 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l8e000000ez6zAAA | PRO-003790 | PEHE4 | 0 | PEHE4J
Sizewell B | EDF ENERGY NUCLEAR GENERATION LIMITED | Sizewell 132kV Substation |  | 1230 | 0 | 1230 |  | Built | Direct Connection | NGET | Nuclear | a0l4L0000005ioQQAQ | PRO-000144 | SIZE4 | 1230 | SIZE41
Sizewell C | Sizewell C Limited | Sizewell 400kV Substation | 2 | 0 | 1670 | 3340 | 2036-07-31 | Consents Approved | Direct Connection | NGET | Nuclear | a0l4L0000005ioPQAQ | PRO-000145-2 | SIZE4 | 0 | SIZE41
Sizewell C | Sizewell C Limited | Sizewell 400kV Substation | 1 | 0 | 1670 | 1670 | 2035-07-31 | Consents Approved | Direct Connection | NGET | Nuclear | a0l4L0000005ioPQAQ | PRO-000145-1 | SIZE4 | 0 | SIZE41
Sizing John (Rainhill) | SIZING JOHN LIMITED | Rainhill GSP | 1 | 0 | 57 | 57 | 2024-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005ijxQAA | PRO-001581-1 | RAIN1 | 57 | RAIN11
Sizing John (Rainhill) | SIZING JOHN LIMITED | Rainhill GSP | 2 | 0 | 85.5 | 142.5 | 2026-09-25 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005ijxQAA | PRO-001581-2 | RAIN1 | 85.5 | RAIN11
Sleat Hybrid | GALILEO 13 LIMITED | Broadford GSP |  | 0 | 100 | 100 | 2034-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l8e000000f7p3AAA | PRO-004014 | BROA | 0 | BROA3-
Slickly Wind Farm | Slickly Wind Farm Limited | Slickly Wind Farm 132kV Substation |  | 0 | 114 | 114 | 2029-12-12 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005ifvQAA | PRO-001517 | SLCK1 | 114 | SLCK1-
Sloy G2 and G3 | SSE Generation Limited | Sloy GSP |  | 80 | 0 | 80 |  | Built | Direct Connection | SHET | Hydro | a0l4L0000005ipTQAQ | PRO-000182 | SLOY | 80 | SLOY5L
Smeaton BESS | KONA ASSET 3 LIMITED | Smeaton 400/275kV |  | 0 | 228 | 228 | 2028-06-23 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000010wUMAAY | PRO-002635 | SMEA2 | 228 | SMEA2-
Sofia Offshore Wind Farm | SOFIA OFFSHORE WIND FARM LIMITED | Dogger Bank 220kV Offshores | 1 | 0 | 132 | 132 | 2024-09-01 | Consents Approved | Direct Connection | NGET | Wind Offshore | a0l4L0000005imVQAQ | PRO-000404-1 | LACK4 | 132 | LACK41
Sofia Offshore Wind Farm | SOFIA OFFSHORE WIND FARM LIMITED | Dogger Bank 220kV Offshores | 2 | 0 | 1188 | 1320 | 2025-04-01 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005imVQAQ | PRO-000404-2 | LACK4 | 1188 | LACK41
Somerford | PD688IRO LTD | Minety 400kV Substation |  | 0 | 47.5 | 47.5 | 2025-06-30 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ixeQAA | PRO-001631 | MITY4 | 47.5 | MITY41
Somerset Energy Park | LOW CARBON SOLAR PARK 35 LIMITED | Somerset Energy Park Substation |  | 0 | 500 | 500 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000011yGUAAY | PRO-003512 |  | 0
South Brook | JBM SOLAR LIMITED | Melksham 400kV Substation |  | 0 | 35.5 | 35.5 | 2037-06-28 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iwKQAQ | PRO-002402 | MELK4 | 0 | MELK41
South Humber Bank | EP SHB LIMITED | South Humber Bank 400kV Substation |  | 1365 | 0 | 1365 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005itwQAA | PRO-000366 | SHBA4 | 1365 | SHBA41
South Kyle 2 Wind farm | VATTENFALL WIND POWER LTD | South Kyle 2 132/33kV Substation |  | 0 | 92.4 | 92.4 | 2030-07-31 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l4L0000005ivbQAA | PRO-001963 | SOKY1 | 92.4 | SOKY1-
South Kyle Wind Farm | SOUTH KYLE WIND FARM LIMITED | New Cumnock 275/132kV |  | 235 | 0 | 235 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005ioJQAQ | PRO-000137 | NECU1 | 235 | NECU1-
South Powrie Farm | QAIR RENEWABLES UK LIMITED | Tealing 132kV Substation |  | 0 | 500 | 500 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e000000ViKAAA0 | PRO-004353 | TEAL1 | 0 | TEAL1-
Southery | SSE UTILITY SOLUTIONS LIMITED | Southery 400kV Substation |  | 0 | 600 | 600 | 2031-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ivgQAA | PRO-002172 |  | 0
Southfields | PD503HAN LTD | Minety 400kV Substation |  | 0 | 47.5 | 47.5 | 2025-06-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ixfQAA | PRO-001632 | MITY4 | 47.5 | MITY41
Southfields Farm | PD688IRO LTD | Minety 400kV Substation |  | 0 | 47.5 | 47.5 | 2028-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005iyAQAQ | PRO-001852 | MITY4 | 47.5 | MITY41
Spalding | SPALDING ENERGY COMPANY LTD | Spalding North 400kV Substation |  | 950 | 0 | 950 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005iq5QAA | PRO-000206 | SPLN4 | 950 | SPLN41
Spalding Energy Expansion | SPALDING ENERGY EXPANSION LIMITED | Spalding North 400kV Substation | 1 | 299.99 | 0 | 299.99 |  | Built | Direct Connection | NGET | Energy Storage System;OCGT (Open Cycle Gas Turbine) | a0l4L0000005irDQAQ | PRO-000249-1 | SPLN4 | 299.99 | SPLN41
Spalding Energy Expansion | SPALDING ENERGY EXPANSION LIMITED | Spalding North 400kV Substation | 2 | 0 | 550 | 849.99 | 2030-10-30 | Consents Approved | Direct Connection | NGET | Energy Storage System;OCGT (Open Cycle Gas Turbine) | a0l4L0000005irDQAQ | PRO-000249-2 | SPLN4 | 550 | SPLN41
Spalding High Impact Energy Hub | TELIS ENERGY UK LIMITED | West Anglia Connection Node G 400kV Substation |  | 0 | 1000 | 1000 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;Nuclear;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e0000012hnqAAA | PRO-004517 |  | 0
Spalding PV and BESS Station | ETP UK 1 LTD | Weston Marsh 400kV Substation |  | 0 | 480 | 480 | 2033-07-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wgUAAQ | PRO-002768 | WEMA4 | 0
Spennymoor | PIVOTED POWER LLP | Spennymoor 400kV Substation |  | 0 | 49.9 | 49.9 | 2028-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005ieQQAQ | PRO-001138 | SPEN41 | 49.9 | SPEN41
Spennymoor BESS | CSE27 LIMITED | Spennymoor 400kV Substation |  | 0 | 49.9 | 49.9 | 2032-06-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ib9QAA | PRO-002035 | SPEN42 | 0 | SPEN42
Spennymoor BESS Station | IGP INTERNATIONAL PROSPECTING LIMITED | Spennymoor 400kV Substation |  | 0 | 400 | 400 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000ewj7AAA | PRO-003681 | SPEN41 | 0 | SPEN41
Spennymoor GSP | NORTHERN POWERGRID (NORTHEAST) PLC | Spennymoor GSP |  | 0 | 139.1 | 139.1 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wvUAAQ | PRO-002970 | SPEN1 | 0 | SPEN11
Spennymoor Greener Grid Park | STATKRAFT UK LTD | Spennymoor 400kV Substation | 2 | 0 | 500 | 500 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;Reactive Compensation | a0l4L0000005ibFQAQ | PRO-002041-2 | SPEN41 | 0 | SPEN41
Spennymoor Greener Grid Park | STATKRAFT UK LTD | Spennymoor 400kV Substation | 1 | 0 | 0 | 0 | 2027-10-29 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;Reactive Compensation | a0l4L0000005ibFQAQ | PRO-002041-1 | SPEN42 | 0 | SPEN42
Spennymoor PV & BESS Sub | O&G Solar (SPV 20) Limited | Spennymoor 400kV Substation |  | 0 | 249.9 | 249.9 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010x1cAAA | PRO-003049 | SPEN42 | 0 | SPEN42
Spiorad Na Mara Offshore Wind Farm | SPIORAD NA MARA LIMITED | NPI C 220/66KV OFFSHORE SUBSTATION |  | 0 | 740 | 740 | 2030-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l4L0000005iNeQAI | PRO-001642 |  | 740
Spittal BESS | FIELD DEVCO LTD | Spittal 275kV Substation |  | 0 | 300 | 300 | 2030-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e000000TPJoAAO | PRO-003255 | SPIT2 | 300 | SPIT2J
Spittal BESS Station | IGP ENERGY STORAGE 5 LIMITED | Spittal 400kV |  | 0 | 1000 | 1000 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e00000120IgAAI | PRO-003618 | SPIT4 | 0 | SPIT1J
Springfield Solar and Battery | VOLTALIA UK LTD | Branxton 400/132kV |  | 0 | 166.61 | 166.61 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wXQAAY | PRO-002664 | BRNX4 | 0 | BRNX4-
Springwell | SPRINGWELL ENERGYFARM LIMITED | Navenby 400kV Substation | 1 | 0 | 400 | 400 | 2029-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iPHQAY | PRO-001850-1 | BICF4 | 400 | BICF41
Springwell | SPRINGWELL ENERGYFARM LIMITED | Navenby 400kV Substation | 3 | 0 | 800 | 1600 | 2033-06-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iPHQAY | PRO-001850-3 |  | 0
Springwell | SPRINGWELL ENERGYFARM LIMITED | Navenby 400kV Substation | 2 | 0 | 400 | 800 | 2030-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iPHQAY | PRO-001850-2 | BICF4 | 400 | BICF41
St Asaph SSE | SSE DE SOLAR HOLDCO LIMITED | Bodelwyddan 400kV Substation |  | 0 | 600 | 600 | 2037-11-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f40uAAA | PRO-003816 | BODE4 | 0 | BODE41
St Dennis Hendra | SAMBAR POWER LIMITED | Indian Queens 400kV Substation |  | 0 | 47.5 | 47.5 | 2024-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005ivrQAA | PRO-001133 | INDQ4 | 47.5 | INDQ41
St Fergus | IB VOGT UK LTD | St Fergus |  | 0 | 100 | 100 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000012hvYAAQ | PRO-004557 | PEHE | 0 | PEHE1-
Stallingborough PV & BESS Station | IGP INTERNATIONAL PROSPECTING LIMITED | Grimsby West 400kV Substation |  | 0 | 500 | 500 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wysAAA | PRO-003021 | GRIW4 | 0 | GRIW41
Stalybridge BESS | CSE32 LIMITED | Stalybridge 275kV Substation |  | 0 | 57 | 57 | 2027-05-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ibAQAQ | PRO-002036 | STAL2 | 57 | STAL21
Statkraft SEWF | STATKRAFT UK LTD | Orrin GSP |  | 0 | 100.8 | 100.8 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0lJ9000000blMrIAI | PRO-004828 | CORI3 | 0 | CORI3-
Staythorpe | ENSO GREEN HOLDINGS LIMITED | Staythorpe 400kV Substation |  | 0 | 400 | 400 | 2030-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005idgQAA | PRO-002083 | STAY41 | 400 | STAY41
Staythorpe (BESS and PV) | SSE STAYTHORPE POWER LIMITED | Staythorpe 400kV Substation |  | 0 | 437 | 437 | 2028-09-28 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ixDQAQ | PRO-001615 | STAY41 | 437 | STAY41
Staythorpe C | RWE Generation UK Plc | Staythorpe 400kV Substation |  | 1752 | 0 | 1752 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine);Demand | a0l4L0000005imBQAQ | PRO-000057 | STAY41 | 1752 | STAY41
Stirling BESS | ANESCO LIMITED | Peterhead 400kV Substation |  | 0 | 300 | 300 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000012groAAA | PRO-004466 | PEHE4 | 0 | PEHE4J
Stockhills Farm | BSR APPLICATIONS LIMITED | Severn Connection Node A 400kv Substation |  | 0 | 800 | 800 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e000001Hy5TAAS | PRO-004323 |  | 0
Stoke Bardolph | Stoke Bardolph 10 Renewables Limited | Trent Valley South Connection Node D 400kV Substation |  | 0 | 1000 | 1000 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000TPQbAAO | PRO-003405 | STOB4 | 0 | STOB41
Stoke Bardolph | Source Galileo Limited | Trent Valley South Connection Node D 400kV Substation |  | 0 | 240 | 240 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f7PNAAY | PRO-004009 | STOB4 | 0 | STOB41
Stoke Bardolph 400 | ENSO GREEN HOLDINGS LIMITED | Stoke Bardolph 400kV Substation | 1 | 0 | 200 | 200 | 2030-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005itiQAA | PRO-002191-1 | STOB4 | 200 | STOB41
Stoke Bardolph 400 | ENSO GREEN HOLDINGS LIMITED | Stoke Bardolph 400kV Substation | 2 | 0 | 100 | 300 | 2031-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005itiQAA | PRO-002191-2 | STOB4 | 0 | STOB41
Stoke Bardolph 400 | ENSO GREEN HOLDINGS LIMITED | Stoke Bardolph 400kV Substation | 3 | 0 | 100 | 400 | 2032-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005itiQAA | PRO-002191-3 | STOB4 | 0 | STOB41
Stornoway Wind Farm | STORNOWAY WIND FARM LIMITED | Stornoway 132/33kV Substation |  | 0 | 180 | 180 | 2030-10-31 | Consents Approved | Direct Connection | SHET | Wind Onshore | a0l4L0000005ixYQAQ | PRO-000346 | KILO1 | 180 | KILO1-
Stracathro BESS | OPDE UK LIMITED | Stracathro BESS 275kV Substation |  | 0 | 249 | 249 | 2032-06-30 | Scoping | Direct Connection | SHET | Demand;Energy Storage System | a0l4L0000005ittQAA | PRO-002392 |  | 0
Stranoch Wind Farm | Stranoch Windfarm Limited | Stranoch Wind 132/33kV Substation |  | 0 | 102 | 102 | 2026-10-09 | Consents Approved | Direct Connection | SPT | Wind Onshore | a0l4L0000005inqQAA | PRO-000127 | STOC3 | 102 | STOC3-
StrataStore - Cheshire Energy Storage Facility | KISTOS ENERGY STORAGE LTD | Gorstage 400kV Substation |  | 0 | 200 | 200 | 2037-11-30 | Scoping | Direct Connection | NGET | Energy Storage System;Reactive Compensation | a0l8e000000f6K5AAI | PRO-003978 |  | 0
Strathaven BESS | IGP ENERGY STORAGE 2 LIMITED | Strathaven 400/275kV |  | 0 | 300 | 300 | 2033-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000001HxmCAAS | PRO-004298 | STHA4 | 0 | STHA4A
Strathy North Wind | STRATHY WIND FARM LIMITED | Strathy North 132/33kV Substation |  | 67.65 | 0 | 67.65 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005ihRQAQ | PRO-001553 | STRW3 | 67.65 | STRW3-
Strathy South Wind | SSE Generation Limited | Strathy South 132/33kV Substation |  | 0 | 207.6 | 207.6 | 2027-04-25 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005ix6QAA | PRO-000183 | STSO1 | 207.6 | STSO1A
Strathy Wood | RWE RENEWABLES UK ONSHORE WIND LIMITED | Strathy Wood 132/33kV Substation | 2 | 0 | 9.1 | 63.5 | 2026-09-30 | Consents Approved | Direct Connection | SHET | Wind Onshore | a0l4L0000005ionQAA | PRO-000154-2 | STWO3 | 9.1 | STWO3-
Strathy Wood | RWE RENEWABLES UK ONSHORE WIND LIMITED | Strathy Wood 132/33kV Substation | 1 | 0 | 54.4 | 54.4 | 2026-09-30 | Consents Approved | Direct Connection | SHET | Wind Onshore | a0l4L0000005ionQAA | PRO-000154-1 | STWO3 | 54.4 | STWO3-
Strichen North BESS | MUIRDEN ENERGY LLP | Strichen GSP |  | 0 | 25 | 25 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e000001Hr31AAC | PRO-004177 | STRI | 0 | STRI3-
Stromar Offshore Windfarm | Stromar Offshore Wind Farm Limited | Cygnus 220/66kV Offshore Substation |  | 0 | 1000 | 1000 | 2033-10-31 | Scoping | Direct Connection | SHET | Wind Offshore | a0l4L0000005izNQAQ | PRO-001530 | NEDE4 | 0 | NEDE4J
Stronelairg | STRONELAIRG WIND FARM LIMITED | Stronelairg 132/33kV Substation |  | 227.8 | 0 | 227.8 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005ipUQAQ | PRO-000184 | STRL1 | 227.8 | STRL1-
Sundhope Wind Farm | Black Knowe Energy Limited | Sundhope 132kV Substation |  | 0 | 180 | 180 | 2033-05-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l8e0000010wgPAAQ | PRO-002767 |  | 0
Sundon | SUNDON BATTERY STORAGE LIMITED | Sundon 400kV Substation |  | 0 | 50 | 50 | 2025-09-05 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ifQQAQ | PRO-001132 | SUND41 | 50 | SUND41
Sundon | SUNDON GREEN LIMITED | Sundon GSP |  | 0 | 39.9 | 39.9 | 2023-11-10 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005invQAA | PRO-000473 | SUND1 | 39.9 | SUND11
Sundon BESS | CSE30 LIMITED | Sundon 400kV Substation |  | 0 | 300 | 300 | 2031-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ibDQAQ | PRO-002039 | SUND42 | 0 | SUND42
Sundon Farm | 548 UK INVESTMENT HOLDINGS LIMITED | Dunstable 400kV Substation |  | 0 | 200 | 200 | 2032-10-29 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wZ7AAI | PRO-002685 | SUND4 | 0 | SUND41
Sundon Farm 2 | 548 UK INVESTMENT HOLDINGS LIMITED | Dunstable 400kV Substation |  | 0 | 700 | 700 | 2032-10-29 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010weTAAQ | PRO-002746 | SUND4 | 0 | SUND41
Sundon Pivoted Power | PIVOTED POWER LLP | Sundon 400kV Substation |  | 49.9 | 0 | 49.9 |  | Built | Direct Connection | NGET | Energy Storage System | a0l4L0000005ifXQAQ | PRO-001123 | SUND42 | 49.9 | SUND42
Sundon Storage | STATERA ENERGY LIMITED | Sundon 400kV Substation |  | 0 | 500 | 500 | 2027-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ivxQAA | PRO-001910 | SUND41 | 500 | SUND41
Sunnica | SUNNICA LIMITED | Burwell 400kV Substation |  | 0 | 500 | 500 | 2030-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ilSQAQ | PRO-000393 | BURW4 | 500 | BURW41
Sutton Bridge | SUTTON BRIDGE POWER GENERATION | Walpole 400kV Substation |  | 850 | 0 | 850 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005iq6QAA | PRO-000207 | WALP41 | 850 | WALP41
Sutton Courtenay | TBC PARTNERS LIMITED | Didcot 132kV Substation |  | 0 | 150 | 150 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001HxbWAAS | PRO-004276 | DIDC1 | 0 | DIDC41
Swansea | ENSO GREEN HOLDINGS LIMITED | Swansea North 400kV Substation |  | 0 | 400 | 400 | 2032-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005idjQAA | PRO-002086 | SWAN41 | 0 | SWAN41
Swansea Greener Grid Park - Connection 1 | Swansea Grid Solutions Limited | Swansea North 400kV Substation | 2 | 0 | 85 | 97 | 2028-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;Reactive Compensation | a0l4L0000005ifaQAA | PRO-001120-2 | SWAN41 | 85 | SWAN41
Swansea Greener Grid Park - Connection 1 | Swansea Grid Solutions Limited | Swansea North 400kV Substation | 1 | 0 | 12 | 12 | 2024-08-31 | Consents Approved | Direct Connection | NGET | Energy Storage System;Reactive Compensation | a0l4L0000005ifaQAA | PRO-001120-1 | SWAN41 | 12 | SWAN41
Swansea Greener Grid Park - Connection 2 | Swansea Grid Solutions Limited | Swansea North 400kV Substation |  | 0 | 0 | 0 | 2025-07-31 | Consents Approved | Direct Connection | NGET | Reactive Compensation | a0l4L0000005ibIQAQ | PRO-002044 | SWAN41 | 0 | SWAN41
Swansea North | PIVOTED POWER LLP | Swansea North 400kV Substation |  | 0 | 49.9 | 49.9 | 2026-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ifbQAA | PRO-001119 | SWAN41 | 49.9 | SWAN41
Swansea North Green Energy Centre | INNOVA RENEWABLES LIMITED | Swansea North 400kV Substation |  | 0 | 1025 | 1025 | 2028-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iygQAA | PRO-001794 | SWAN41 | 1025 | SWAN41
Swansea North-Rhigos Solar& BESS & Wind | TYLER HILL RENEWABLES LIMITED | South Wales West Connection Node A 400kV Substation |  | 0 | 400 | 400 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e000001Hoz9AAC | PRO-004099 | RHIG4 | 0 | RHIG41
Sweet Briar Energy Park | SWEET BRIAR 2 ENERGY PARK LIMITED | South Humber Connection Node A |  | 0 | 800 | 800 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0lJ9000000PDu2IAG | PRO-005055 |  | 0
TH Bridge Farm | FRV TH Powertek Limited | Imperial Park B 400kV Substation |  | 0 | 400 | 400 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TPS9AAO | PRO-003425 | IMPP4 | 0 | IMPP41
TH Didcot | FRV TH Powertek Limited | Chiltern Connection Node D 400kV |  | 0 | 200 | 200 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TPSDAA4 | PRO-003426 |  | 0
TH Knaresborough | FRV TH Powertek Limited | Leeds North Connection Node A 400kV Substation |  | 0 | 200 | 200 | 2036-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001HpdtAAC | PRO-004131 |  | 0
TH Maes Melin | FRV TH Powertek Limited | South Wales West Connection Node A 400kV Substation |  | 0 | 200 | 200 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TPS8AAO | PRO-003424 |  | 0
TH Ninfield | FRV TH Powertek Limited | Ninfield GSP |  | 0 | 200 | 200 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001HpCfAAK | PRO-004111 | NINF4 | 0 | NINF41
TH Renfrewshire | FRV TH Powertek Limited | TH Renfrwshire 275kV Substation |  | 0 | 250 | 250 | 2033-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000001HrCAAA0 | PRO-004188 |  | 0
TH Stocking Pelham | FRV TH Powertek Limited | West Anglia Connection Node E 400kV Substation |  | 0 | 400 | 400 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000010wiVAAQ | PRO-002791 | PELH4 | 0 | PELH41
TH Stow Manor | FRV TH Powertek Limited | Trent Valley South Connection Node B 400kV Substation. |  | 0 | 400 | 400 | 2034-10-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l8e0000010xfQAAQ | PRO-003077 |  | 0
TH West Weybridge | FRV TH Powertek Limited | London West Connection Node B 400kV Substation |  | 0 | 200 | 200 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000011ycrAAA | PRO-003531 |  | 0
THE CLEAN FUTURE | THE CLEAN FUTURE RENEWABLES LIMITED | Killingholme 400kV Substation |  | 0 | 500 | 500 | 2033-05-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iaFQAQ | PRO-002019 | KILL4 | 0 | KILL41
Tangy IV WF | SSE RENEWABLES SERVICES (UK) LIMITED | Tangy IV 132KV Substation |  | 0 | 96 | 96 | 2026-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005iz2QAA | PRO-001408 | TNGF1 | 96 | TNGF1-
Tarenni | TARENNI ENERGY PARK LIMITED | Rhigos 400kV Substation |  | 0 | 188 | 188 | 2028-10-01 | Scoping | Direct Connection | NGET | Wind Onshore | a0l4L0000005iNdQAI | PRO-001641 | RHIG4 | 188 | RHIG41
Taunton | PIVOTED POWER LLP | Taunton 400kV Substation | 2 | 0 | 50.1 | 100 | 2037-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005icpQAA | PRO-001073-2 | TAUN41 | 0 | TAUN41
Taunton | PIVOTED POWER LLP | Taunton 400kV Substation | 1 | 0 | 49.9 | 49.9 | 2031-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005icpQAA | PRO-001073-1 | TAUN42 | 0 | TAUN42
Tealing BESS (100MW) | GPC 1039 Ltd | Tealing 132kV Substation |  | 0 | 100 | 100 | 2028-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l4L0000005itbQAA | PRO-002436 | TEAL1 | 100 | TEAL1-
Tealing Energy Park | Onpath Energy Limited | Tealing 400kV Substation |  | 0 | 1400 | 1400 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e0000010xh8AAA | PRO-003084 | TEAL4 | 0 | TEAL3W
Tees CCPP | SEMBCORP UTILITIES (UK) LIMITED | Greystones A and B 275kV Substations | 3 | 0 | 340 | 700 | 2026-03-11 | Consents Approved | Direct Connection | NGET | Energy Storage System;OCGT (Open Cycle Gas Turbine) | a0l4L0000005ibWQAQ | PRO-001048-3 | GRST2A | 340 | GRST2A
Tees CCPP | SEMBCORP UTILITIES (UK) LIMITED | Greystones A and B 275kV Substations | 4 | 0 | 490 | 1190 | 2027-09-30 | Consents Approved | Direct Connection | NGET | Energy Storage System;OCGT (Open Cycle Gas Turbine) | a0l4L0000005ibWQAQ | PRO-001048-4 | GRST2B | 490 | GRST2B
Tees CCPP | SEMBCORP UTILITIES (UK) LIMITED | Greystones A and B 275kV Substations | 1 | 0 | 150 | 150 | 2023-09-30 | Under Construction/Commissioning | Direct Connection | NGET | Energy Storage System;OCGT (Open Cycle Gas Turbine) | a0l4L0000005ibWQAQ | PRO-001048-1 | GRST2A | 150 | GRST2A
Tees CCPP | SEMBCORP UTILITIES (UK) LIMITED | Greystones A and B 275kV Substations | 6 | 0 | 235 | 1700 | 2030-09-30 | Consents Approved | Direct Connection | NGET | Energy Storage System;OCGT (Open Cycle Gas Turbine) | a0l4L0000005ibWQAQ | PRO-001048-6 | GRST2A | 235 | GRST2A
Tees CCPP | SEMBCORP UTILITIES (UK) LIMITED | Greystones A and B 275kV Substations | 2 | 0 | 210 | 360 | 2024-09-30 | Consents Approved | Direct Connection | NGET | Energy Storage System;OCGT (Open Cycle Gas Turbine) | a0l4L0000005ibWQAQ | PRO-001048-2 | GRST2B | 210 | GRST2B
Tees CCPP | SEMBCORP UTILITIES (UK) LIMITED | Greystones A and B 275kV Substations | 5 | 0 | 275 | 1465 | 2027-09-30 | Consents Approved | Direct Connection | NGET | Energy Storage System;OCGT (Open Cycle Gas Turbine) | a0l4L0000005ibWQAQ | PRO-001048-5 | GRST2B | 275 | GRST2B
Tees Renewable Energy Plant | MGT TEESSIDE LIMITED | Lackenby GSP |  | 285 | 0 | 285 |  | Built | Direct Connection | NGET | Biomass | a0l4L0000005irsQAA | PRO-000278 | LACK6 | 285 | LACK61
Teindland Wind Farm | TEINDLAND WIND FARM LIMITED | Blackhillock substation |  | 0 | 112.2 | 112.2 | 2029-09-28 | Scoping | Direct Connection | SHET | Demand;Wind Onshore | a0l4L0000005iNkQAI | PRO-001821 | BLHI | 112.2 | BLHI1J
Teviot Wind Farm | TEVIOT WF LIMITED | Teviot 400/132kV Substation |  | 0 | 522.9 | 522.9 | 2033-05-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005iPbQAI | PRO-000855 | TEVI4 | 0
Tewitt Farm BESS | Apatura Battery Ltd | Leeds North Connection Node D 400kV Substation |  | 0 | 200 | 200 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f5BdAAI | PRO-003917 |  | 0
Thanet Offshore Wind Farm | THANET OFFSHORE WIND LIMITED | Thanet 33/132kV Offshore Substation |  | 300 | 0 | 300 |  | Built | Direct Connection | OFTO | Wind Offshore | a0l4L0000005iqBQAQ | PRO-000212 | RICH1 | 300 | RICH11
The Beacon | Beacon Solar Limited | Alverdiscott GSP |  | 0 | 1200 | 1200 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0lJ9000000PDtEIAW | PRO-005046 | ALVE4A | 0 | ALVE4A
The Droves (formerly Swaffham PV & BESS) | IGP INTERNATIONAL PROSPECTING LIMITED | Swaffham 400KV Substation |  | 0 | 500 | 500 | 2033-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000eyK3AAI | PRO-003754 |  | 0
Thormanby Solar PV & BESS | BAYWA R.E. UK LIMITED | Thormanby 400kV Substation |  | 0 | 350 | 350 | 2033-10-28 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iuyQAA | PRO-002123 |  | 0
Thorney Edge | ARL Energy Development Limited | Cellarhead 400kV Substation |  | 0 | 300 | 300 | 2037-11-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iu3QAA | PRO-002327 | CELL4 | 0 | CELL41
Thornton | IGP SOLAR 19 LIMITED | Thornton 400kV Substation |  | 0 | 500 | 500 | 2031-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iOrQAI | PRO-001647 | THTO42 | 0 | THTO42
Thornton BESS | REWE 9 LIMITED | Thornton 400kV Substation |  | 0 | 200 | 200 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000ewjRAAQ | PRO-003684 | THTO43 | 0 | THTO43
Thornton Facility | BALWEN LIMITED | Thornton 400kV Substation | 3 | 0 | 200 | 399.96 | 2028-10-27 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iebQAA | PRO-001484-3 | THTO42 | 200 | THTO42
Thornton Facility | BALWEN LIMITED | Thornton 400kV Substation | 2 | 0 | 99.98 | 199.96 | 2026-10-23 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iebQAA | PRO-001484-2 | THTO42 | 99.98 | THTO42
Thornton Facility | BALWEN LIMITED | Thornton 400kV Substation | 4 | 0 | 530.03 | 929.99 | 2031-11-28 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iebQAA | PRO-001484-4 | THTO41 | 0 | THTO41
Thornton Facility | BALWEN LIMITED | Thornton 400kV Substation | 1 | 0 | 99.98 | 99.98 | 2024-10-25 | Under Construction/Commissioning | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iebQAA | PRO-001484-1 | THTO41 | 99.98 | THTO41
Thornton PV & BESS Sub | O&G Solar (SPV 57) Limited | Thornton B 400kV Substation |  | 0 | 249.9 | 249.9 | 2035-10-26 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001HpemAAC | PRO-004141 | THTO42 | 0 | THTO42
Thorpe Marsh 1 (Tertiary) | ENSO GREEN HOLDINGS I LIMITED | Thorpe Marsh 400kV Substation |  | 0 | 57 | 57 | 2028-10-30 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005inyQAA | PRO-000470 | THOM41 | 57 | THOM41
Thorpe Marsh Energy Park | Thorpe Marsh Green Energy Hub Limited | Thorpe Marsh 400kV Substation |  | 0 | 1400 | 1400 | 2026-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iNOQAY | PRO-001620 | THOM42 | 1400 | THOM42
Thorpe Marsh Green Energy Centre | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 1 | 0 | 400 | 400 | 2030-10-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005igNQAQ | PRO-001724-1 | THOM41 | 400 | THOM41
Thorpe Marsh Green Energy Centre | INNOVA RENEWABLES LIMITED | Thorpe Marsh 400kV Substation | 2 | 0 | 625 | 1025 | 2032-08-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005igNQAQ | PRO-001724-2 | THOM41 | 0 | THOM41
Thurcroft BESS | HARMONY ENERGY LIMITED | Thurcroft GSP |  | 0 | 99.9 | 99.9 | 2031-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iwjQAA | PRO-002313 | THUR21 | 0 | THUR21
Thurrock Power Station | THURROCK FLEXIBLE GENERATION LIMITED | Tilbury 275kV Substation | 1 | 0 | 300 | 300 | 2024-11-28 | Under Construction/Commissioning | Direct Connection | NGET | Energy Storage System;Gas Reciprocating | a0l4L0000005ivpQAA | PRO-000494-1 | TILB2 | 300 | TILB21
Thurrock Power Station | THURROCK FLEXIBLE GENERATION LIMITED | Tilbury 275kV Substation | 2 | 0 | 450 | 750 | 2025-10-31 | Under Construction/Commissioning | Direct Connection | NGET | Energy Storage System;Gas Reciprocating | a0l4L0000005ivpQAA | PRO-000494-2 | TILB2 | 450 | TILB21
Thurso South BESS | WP Grid Storage 3 Limited | Thurso South 275kV Substation’ |  | 0 | 100 | 100 | 2030-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e000000ewOOAAY | PRO-003655 | THUS2 | 100 | THUS2J
Thurso South Synchronous Compensation | THURSO GRID SERVICES LIMITED | Thurso GSP |  | 0 | 0 | 0 |  | Built | Direct Connection | SHET | Reactive Compensation | a0l4L0000005iapQAA | PRO-001415 | THUS | 0 | THUS3-
Tillbridge Solar | TILLBRIDGE SOLAR LIMITED | Cottam 400kV Substation |  | 0 | 500 | 500 | 2028-08-27 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ifWQAQ | PRO-001126 | COTT4 | 500 | COTT41
Tinnisburn Wind Farm | BAYWA R.E. UK LIMITED | Gretna Green 132 kV Substation |  | 0 | 70 | 70 | 2031-10-30 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l8e000000f7BUAAY | PRO-003997 | GRNA1 | 0 | GRNA1-
Toddleburn Wind Farm | SSE TODDLEBURN LIMITED | Toddleburn 33kV |  | 27.6 | 0 | 27.6 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005ipVQAQ | PRO-000185 | TODD3 | 27.6 | TODD3-
Tolkien Solar Farm | Tolkien Solar Farm Limited | Tolkien Farm 132kV Substation |  | 0 | 200 | 200 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ikfQAA | PRO-002294 |  | 0
Tomchrasky Wind Farm | E Power Limited | Tomchrasky Wind Farm 132kV Substation |  | 0 | 74.4 | 74.4 | 2029-10-31 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005ixoQAA | PRO-002270 |  | 74.4
Torfichen Energy Park | Renewable Energy Systems Limited | Torfichen Energy Park 132kV Substation |  | 0 | 150 | 150 | 2030-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0l8e0000010wRIAAY | PRO-002598 |  | 150
Tormsdale Windfarm | ASUK HOLDCO 1 LIMITED | Mybster 3 132/33kV Substation |  | 0 | 70 | 70 | 2027-06-30 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005iRQQAY | PRO-001904 | MYBS3 | 70 | MYBS3J
Torness | EDF ENERGY NUCLEAR GENERATION LIMITED | Torness 400/132kV |  | 1250 | 0 | 1250 |  | Built | Direct Connection | SPT | Nuclear | a0l4L0000005ioRQAQ | PRO-000146 | TORN4 | 1250 | TORN4-
Torridge Offshore Wind Farm | GWYNT GLAS OFFSHORE WIND FARM LIMITED | Alverdiscott 400kV Substation |  | 0 | 1500 | 1500 | 2031-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005iy6QAA | PRO-001917 | ALVE4A | 0 | ALVE4A
Tralorg Wind Farm | TRALORG WIND FARM LIMITED | Tralorg 33kV |  | 20 | 0 | 20 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005itAQAQ | PRO-000357 | TRLO3 | 20 | TRLO3-
Trawsfynydd B Cwmni Egino | Cwmni Egino | Trawsfynydd 275kV Substation |  | 0 | 940 | 940 | 2037-11-01 | Scoping | Direct Connection | NGET | Nuclear | a0l8e0000012gZAAAY | PRO-004421 | TRAW2 | 0 | TRAW21
Triton Knoll Offshore Wind Farm | TRITON KNOLL OFFSHORE WIND FARM LIMITED | Triton Knoll Offshore Substation |  | 824 | 0 | 824 |  | Built | Direct Connection | NGET | Wind Offshore | a0l4L0000005ipZQAQ | PRO-000193 | BICF4 | 824 | BICF41
Troston Wind Farm | TROSTON WINDFARM LIMITED | Margree 132kV Collector Substation |  | 0 | 68 | 68 | 2029-10-31 | Awaiting Consents | Direct Connection | SPT | Wind Onshore | a0l4L0000005iffQAA | PRO-001115 | TRSN1 | 68 | TRSN1-
Tulliallan BESS | IGP ENERGY STORAGE 6 LIMITED | Kincardine North 400kV Substation |  | 0 | 500 | 500 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e00000120IhAAI | PRO-003619 | KINC4 | 0 | KINC2-
Tween Bridge Solar Park | RWE RENEWABLES UK SOLAR AND STORAGE LIMITED | Tween Bridge 400kV | 2 | 0 | 250 | 590 | 2032-11-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iZUQAY | PRO-001990-2 |  | 0
Tween Bridge Solar Park | RWE RENEWABLES UK SOLAR AND STORAGE LIMITED | Tween Bridge 400kV | 1 | 0 | 340 | 340 | 2029-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iZUQAY | PRO-001990-1 |  | 340
Twentyshilling Wind Farm | TWENTYSHILLING LIMITED | Glenglass 132/33kV |  | 37.8 | 0 | 37.8 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005iZ7QAI | PRO-001365 | GLGL3 | 37.8 | GLGL3-
Twyn Hywel Cillfynydd | Twyn Hywel Energy Park Ltd | Cilfynydd 400kV Substation |  | 0 | 160 | 160 | 2026-03-31 | Scoping | Direct Connection | NGET | Wind Onshore | a0l4L0000005izFQAQ | PRO-001497 | CILF4 | 160 | CILF41
Tyler Hill Bicker Fen | FRV TH Powertek Limited | Bicker Fen 400kV Substation |  | 0 | 400 | 400 | 2035-05-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000012gcNAAQ | PRO-004443 | BICF4 | 0 | BICF41
Tyler Hill Iver | FRV TH Powertek Limited | London West Connection Node A 400kV Substation |  | 0 | 199.92 | 199.92 | 2038-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l8e000001HpeDAAS | PRO-004134 |  | 0
Upper Beoch Windfarm | BROCKWELL ENERGY LIMITED | New Cumnock North 132kV Substation |  | 0 | 80 | 80 | 2033-10-31 | Scoping | Direct Connection | SPT | Wind Onshore | a0l8e000001HoGMAA0 | PRO-004068 | NECU1 | 0 | NECU1-
Uskmouth | USKMOUTH ENERGY STORAGE LIMITED | Uskmouth 132kV Substation | 1 | 0 | 230 | 230 | 2024-06-30 | Under Construction/Commissioning | Direct Connection | NGET | Energy Storage System | a0l4L0000005izuQAA | PRO-000220-1 | USKM1 | 230 | USKM11
Uskmouth | USKMOUTH ENERGY STORAGE LIMITED | Uskmouth 132kV Substation | 2 | 0 | 119.9 | 349.9 | 2038-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005izuQAA | PRO-000220-2 | USKM1 | 0 | USKM11
Uskmouth - New Connection | AW1 ENERGY STORAGE LIMITED | Uskmouth 275kV Substation |  | 0 | 120 | 120 | 2026-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iytQAA | PRO-001357 | USKM21 | 120 | USKM21
VPI Immingham B OCGT | VPI IMMINGHAM B LIMITED | Humber Refinery 400kV Substation |  | 0 | 299 | 299 | 2026-01-16 | Scoping | Direct Connection | NGET | OCGT (Open Cycle Gas Turbine) | a0l4L0000005iPcQAI | PRO-000854 | HUMR4 | 299 | HUMR41
Valorous Offshore Wind Farm | Blue Gem Wind Limited | Pembroke 400kV Substation |  | 0 | 300 | 300 | 2031-10-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005iZlQAI | PRO-001383 | PEMB4 | 0 | PEMB41
Vanguard | NORFOLK VANGUARD WEST LIMITED | Necton 400kV Substation |  | 0 | 1320 | 1320 | 2025-12-01 | Consents Approved | Direct Connection | NGET | Wind Offshore | a0l4L0000005izXQAQ | PRO-000459 | NECT4 | 1320 | NECT41
Vanguard East | Norfolk Vanguard East Ltd | Necton 400kV Substation | 1 | 0 | 400 | 400 | 2028-04-01 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005izdQAA | PRO-000580-1 | NECT4 | 400 | NECT41
Vanguard East | Norfolk Vanguard East Ltd | Necton 400kV Substation | 2 | 0 | 920 | 1320 | 2028-12-31 | Scoping | Direct Connection | NGET | Wind Offshore | a0l4L0000005izdQAA | PRO-000580-2 | NECT4 | 920 | NECT41
Viking Wind Farm | VIKING ENERGY WIND FARM LLP | Kergord GSP |  | 443 | 0 | 443 |  | Built | Direct Connection | SHET | Wind Onshore | a0l4L0000005isvQAA | PRO-000338 | KERG | 443 | KERG1-
WELBAR ENERGY STORAGE | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 1 | 0 | 349.9 | 349.9 | 2026-10-30 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005ieyQAA | PRO-001735-1 | HAMH4 | 349.9 | HAMH41
WELBAR ENERGY STORAGE | WELBAR ENERGY STORAGE LIMITED | Hams Hall 400kV Substation | 2 | 0 | 50 | 399.9 | 2032-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005ieyQAA | PRO-001735-2 | HAMH4 | 0 | HAMH41
WHITEHILL BESS | GPC 1210 Ltd | Whitehill Bess 275/132kV Substation |  | 0 | 500 | 500 | 2029-10-01 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e0000012jIBAAY | PRO-004639 |  | 500
WORSET LANE BESS | FIELD HARTMOOR LTD | Hartmoor 275kV Substation |  | 0 | 200 | 200 | 2026-10-25 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l8e000000ew2xAAA | PRO-003650 | HARM2 | 200 | HARM21
Wakeleys BESS | EPL NEWCO6 LIMITED | Wakeleys 400kV |  | 0 | 480 | 480 | 2033-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f5BxAAI | PRO-003921 |  | 0
Walham 700MW BESS | GPC 1154 Ltd | Walham 400kV Substation |  | 0 | 700 | 700 | 2038-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L000002yQZZQA2 | PRO-002551 | WALH4 | 0 | WALH41
Walham PV & BESS Sub | GLOUCESTER ENERGY PARK LIMITED | Walham 400kV Substation |  | 0 | 249 | 249 | 2033-11-17 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005j8WQAQ | PRO-002522 | WALH4 | 0 | WALH41
Walney 3 Offshore Wind Farm | WALNEY EXTENSION LIMITED | Walney 3 Offshore Substation |  | 330 | 0 | 330 |  | Built | Direct Connection | NGET | Wind Offshore | a0l4L0000005iqlQAA | PRO-000239 | MIDL4 | 330 | MIDL41
Walney 4 Offshore Wind Farm | WALNEY EXTENSION LIMITED | Walney 4 Offshore Substation |  | 330 | 0 | 330 |  | Built | Direct Connection | NGET | Wind Offshore | a0l4L0000005iqmQAA | PRO-000240 | MIDL4 | 330 | MIDL41
Walney I Offshore Wind Farm | WALNEY (UK) OFFSHORE WINDFARMS LIMITED | Walney 1 33/132kV Offshore Substation |  | 182 | 0 | 182 |  | Built | Direct Connection | OFTO | Wind Offshore | a0l4L0000005iqGQAQ | PRO-000221 | MIDL4 | 182 | MIDL41
Walney II Offshore Wind Farm | WALNEY (UK) OFFSHORE WINDFARMS LIMITED | Walney 2 33/132kV Substation |  | 182 | 0 | 182 |  | Built | Direct Connection | OFTO | Wind Offshore | a0l4L0000005iqHQAQ | PRO-000222 | MIDL4 | 182 | MIDL41
Walpole | PIVOTED POWER LLP | Walpole 400kV Substation |  | 49.9 | 0 | 49.9 |  | Built | Direct Connection | NGET | Energy Storage System | a0l4L0000005ifgQAA | PRO-001114 | WALP41 | 49.9 | WALP41
Walpole 1 (Tertiary) | WALPOLE GREEN LIMITED | Walpole 400kV Substation |  | 0 | 57 | 57 | 2025-07-15 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ipkQAA | PRO-000556 | WALP41 | 57 | WALP41
Walpole 2 (tertiary) | ENSO GREEN HOLDINGS R LIMITED | Walpole 400kV Substation |  | 0 | 100 | 100 | 2027-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ioVQAQ | PRO-000505 | WALP41 | 100 | WALP41
Walpole Flexible Generation | FLEXIBLE GENERATION 1 LTD | Walpole 400kV Substation |  | 0 | 2000 | 2000 | 2033-06-30 | Scoping | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine);Energy Storage System | a0l4L0000005ikmQAA | PRO-002440 | WALP4 | 0 | WALP41
Walpole Grid Services Facility | Conrad (Walpole) Limited | Walpole 400kV Substation |  | 0 | 0 | 0 | 2025-05-30 | Consents Approved | Direct Connection | NGET | Reactive Compensation | a0l8e000000exSnAAI | PRO-003728 | WALP41 | 0 | WALP41
Waltham Cross BESS | SHAW-ENERGI LTD | Waltham Cross 400kV Substation |  | 0 | 300 | 300 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000ewXcAAI | PRO-003665 | WALX41 | 0 | WALX41
Waltham Cross BESS | ENSO GREEN HOLDINGS LIMITED | Waltham Cross 400kV Substation |  | 0 | 57 | 57 | 2028-09-29 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005icCQAQ | PRO-002070 | WALX41 | 57 | WALX41
Waltham Cross Farm | Waltham Cross 2 Renewables Limited | Waltham Cross 400kV Substation |  | 0 | 200 | 200 | 2033-04-04 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wZHAAY | PRO-002687 | WALX41 | 0 | WALX41
Waltham Cross Farm 2 | Waltham Cross 7 Renewables Limited | Waltham Cross B 400kV Substation |  | 0 | 700 | 700 | 2033-04-04 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wedAAA | PRO-002748 | WALX41 | 0 | WALX41
Waltham Cross PV & BESS Sub | EPPING ENERGY PARK LIMITED | Waltham Cross B 400kV Substation |  | 0 | 249.9 | 249.9 | 2032-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0lJ9000000PERuIAO | PRO-005801 | WALX41 | 0 | WALX41
Walton Road Energy Project | Lightsource Renewable UK Development Limited | Drakelow 400kV Substation |  | 0 | 240 | 240 | 2029-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iuxQAA | PRO-002225 | DRAK4 | 240 | DRAK41
Warley | WARLEY BATTERY STORAGE | Warley 275kV Substation |  | 0 | 57 | 57 | 2027-08-31 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005ifhQAA | PRO-001113 | WARL2 | 57 | WARL21
Warley (tertiary) | WARLEY GREEN LIMITED | Warley 275kV Substation | 1 | 0 | 49.9 | 49.9 | 2023-07-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iplQAA | PRO-000555-1 | WARL2 | 49.9 | WARL21
Warley (tertiary) | WARLEY GREEN LIMITED | Warley 275kV Substation | 2 | 0 | 7.1 | 57 | 2024-06-28 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iplQAA | PRO-000555-2 | WARL2 | 7.1 | WARL21
Warley 2 | CSE26 LIMITED | Warley 275kV Substation | 1 | 0 | 150 | 150 | 2029-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iPFQAY | PRO-001848-1 | WARL2 | 150 | WARL21
Warley 2 | CSE26 LIMITED | Warley 275kV Substation | 2 | 0 | 50 | 200 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iPFQAY | PRO-001848-2 | WARL2 | 0 | WARL21
Warley Battery Energy Storage | ABBEY PROPERTIES CAMBRIDGESHIRE LIMITED | Warley 275kV Substation |  | 0 | 200 | 200 | 2029-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iwpQAA | PRO-002321 | WARL2 | 200 | WARL21
Warley PV & BESS | O&G Solar (SPV 36) Limited | Warley 275kV Substation |  | 0 | 249.9 | 249.9 | 2031-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L000002yQWQQA2 | PRO-002537 | WARL2 | 0 | WARL21
Watchman Energy Park | RENEWCO POWER LIMITED | Watchman 132kV Substation |  | 0 | 249.9 | 249.9 | 2036-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e000001HxRXAA0 | PRO-004258 |  | 0
Waternish Wind Farm Substaion | WIND DEVELOPMENT HOLDINGS LIMITED | Waternish Wind Farm 12KV Substation |  | 0 | 81.6 | 81.6 | 2034-04-30 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005ikeQAA | PRO-002295 |  | 0
Watten Wind Farm | EDF ENERGY RENEWABLES LIMITED | Mybster 3 GSP |  | 0 | 52.8 | 52.8 | 2028-06-30 | Scoping | Direct Connection | SHET | Wind Onshore | a0l4L0000005iYGQAY | PRO-001928 | MYBS | 52.8 | MYBS3N
Weaver BESS | Frodsham Devco Limited | Frodsham 400kV Substation |  | 0 | 240 | 240 | 2037-11-01 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000010wOPAAY | PRO-002571 | FROD4 | 0 | FROD41
Welbeck-Newark Solar Farm - PVDP | SolarTen Ltd | High Marnham 400kV Substation |  | 0 | 710 | 710 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001HpeXAAS | PRO-004138 | HIGM4 | 0 | HIGM41
Wern Tarw Storage | CENIN RENEWABLES LIMITED | Cilfynydd 400kV Substation |  | 0 | 249 | 249 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0lJ9000000PFDVIA4 | PRO-005874 | CILF4 | 0 | CILF41
West Andershaw Wind Farm | WEST ANDERSHAW WIND FARM LIMITED | West Andershaw 132kV Substation |  | 0 | 85.8 | 85.8 | 2030-04-30 | Scoping | Direct Connection | SPT | Wind Onshore | a0l8e0000010wPRAAY | PRO-002584 |  | 85.8
West Botley High Impact Green Energy Hub | TELIS ENERGY UK LIMITED | Botley West 400kV Substation |  | 0 | 100 | 100 | 2037-10-31 | Scoping | Direct Connection | NGET | Demand;Energy Storage System;Nuclear;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e0000012gbjAAA | PRO-004435 | COWL4 | 0 | COWL41
West Burton | ENSO GREEN HOLDINGS A LIMITED | West Burton 132kV Substation |  | 0 | 120 | 120 | 2027-06-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iYCQAY | PRO-001323 | WBUR1 | 120 | WBUR11
West Burton B | WEST BURTON B LIMITED | West Burton 400kV Substation | 1 | 1333 | 500 | 1833 | 2027-10-30 | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine);Energy Storage System | a0l4L0000005ilIQAQ | PRO-000369-1 | WBUR42 | 1833 | WBUR42
West Burton B | WEST BURTON B LIMITED | West Burton 400kV Substation | 2 | 0 | 48 | 1881 | 2034-10-30 | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine);Energy Storage System | a0l4L0000005ilIQAQ | PRO-000369-2 | WBUR41 | 0 | WBUR41
West Burton Solar Project | WEST BURTON SOLAR PROJECT LIMITED | West Burton 400kV Substation |  | 0 | 480 | 480 | 2028-11-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ipfQAA | PRO-000561 | WBUR42 | 480 | WBUR42
West Haddon | SSE DE SOLAR HOLDCO LIMITED | West Haddon 400kV Substation |  | 0 | 600 | 600 | 2039-10-01 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000f41EAAQ | PRO-003820 |  | 0
West Haddon | West Haddon 10 Renewables Limited | Derbyshire Connection Node A 400kV Substation |  | 0 | 1000 | 1000 | 2037-10-30 | Scoping | Direct Connection | NGET | Demand;PV Array (Photo Voltaic/solar) | a0l8e000000TPRUAA4 | PRO-003417 |  | 0
West Melton PV & BESS Station | IB VOGT UK LTD | Leeds North Connection Node C 400kV Substation |  | 0 | 200 | 200 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001HoBfAAK | PRO-004061 |  | 0
West Oxfordshire Energy Park | LOW CARBON SOLAR PARK 43 LIMITED | Chiltern Connection Node D 400kV |  | 0 | 500 | 500 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001Hxm2AAC | PRO-004296 |  | 0
West Saval Battery Storage | West Saval Battery Storage Ltd | West Saval Substation 132 kV |  | 0 | 200 | 200 | 2030-10-31 | Scoping | Direct Connection | SHET | Demand;Energy Storage System | a0l8e0000011yC5AAI | PRO-003510 |  | 200
West Weybridge | EL (WEST WEYBRIDGE) LIMITED | West Weybridge 275kV Substation |  | 0 | 57 | 57 | 2027-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l8e000001Hy5YAAS | PRO-004324 | WWEY22 | 57 | WWEY22
West Weybridge | West Weybridge 10 Renewables Limited | London West Connection Node B 400kV Substation |  | 0 | 1000 | 1000 | 2038-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000000TPQwAAO | PRO-003410 |  | 0
West Weybridge (Tertiary) | ENSO GREEN HOLDINGS LIMITED | West Weybridge 275kV Substation | 1 | 0 | 49.9 | 49.9 | 2025-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ipoQAA | PRO-000552-1 | WWEY21 | 49.9 | WWEY21
West Weybridge (Tertiary) | ENSO GREEN HOLDINGS LIMITED | West Weybridge 275kV Substation | 2 | 0 | 7.1 | 57 | 2027-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ipoQAA | PRO-000552-2 | WWEY21 | 7.1 | WWEY21
West of Duddon Sands Offshore Wind Farm | MORECAMBE WIND LIMITED | West of Duddon Sands 34/155kV Offshore Substation |  | 382 | 0 | 382 |  | Built | Direct Connection | OFTO | Wind Offshore | a0l4L0000005iq9QAA | PRO-000210 | HEYS4 | 382 | HEYS41
Westermost Rough Offshore Wind Farm | WESTERMOST ROUGH LIMITED | Westermost Rough Offshore Substation |  | 206.5 | 0 | 206.5 |  | Built | Direct Connection | OFTO | Wind Offshore | a0l4L0000005iqIQAQ | PRO-000223 | HEDO | 206.5 | HEDO21
Westerton Lane BESS | Apatura Battery Ltd | Busby 275kV |  | 0 | 150 | 150 | 2029-09-17 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000TPLzAAO | PRO-003267 | BUSB2 | 150 | BUSB2-
Westfield BESS | BROCKWELL ENERGY LIMITED | Westfield 275/132kV |  | 0 | 350 | 350 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000001HrdGAAS | PRO-004210 | WFIE2 | 0 | WFIE2-
Wether Hill | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Wether Hill 132/33KV Substation |  | 0 | 66 | 66 | 2031-09-29 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005ig2QAA | PRO-001527 |  | 0
White Cairns BESS | CBS ENERGY STORAGE ASSETS UK LIMITED | Peterhead 275kV |  | 0 | 400 | 400 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e000001HrmFAAS | PRO-004219 | PEHE2 | 0 | PEHE2-
Whitecraig BESS | Apatura Battery Ltd | Dalkeith 400kV Substation |  | 0 | 200 | 200 | 2031-06-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000TPKwAAO | PRO-003265 | SMEA4 | 0 | SMEA4Q
Whitegate Tertiary Connection | HD144WHI LTD | Whitegate 275kV Substation |  | 0 | 57 | 57 | 2024-06-30 | Consents Approved | Direct Connection | NGET | Energy Storage System | a0l4L0000005io8QAA | PRO-000512 | WHGA2 | 57 | WHGA21
Whitehill Battery Storage | Whitehill Battery Storage Ltd | Easterhouse 275/33kV |  | 0 | 200 | 200 | 2026-10-31 | Awaiting Consents | Direct Connection | SPT | Energy Storage System | a0l4L0000005idpQAA | PRO-002093 | EERH3 | 200 | EERH3-
Whitehouse BESS station | IGP INTERNATIONAL PROSPECTING LIMITED | Crossaig 132kV Substation |  | 0 | 249 | 249 | 2034-10-31 | Scoping | Direct Connection | SHET | Demand;Energy Storage System | a0l4L0000005iu6QAA | PRO-002237 | CRSS1 | 0 | CRSS1J
Whitelaw Brae BESS | BUK23 Limited | Whitelaw Brae WF 33kV Substation |  | 0 | 1 | 1 | 2026-07-31 | Scoping | Direct Connection | SPT | Energy Storage System | a0l8e000000TPIWAA4 | PRO-003247 |  | 1
Whitelaw Brae Windfarm | WHITELAW BRAE WINDFARM LIMITED | Whitelaw Brae 'A' and 'B' 33kV Substations |  | 0 | 57 | 57 | 2026-07-31 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005isxQAA | PRO-000341 |  | 57
Whitelee | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Whitelee 275/33kV | 1 | 305 | 0 | 305 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005imeQAA | PRO-000067-1 | WLEE2 | 305 | WLEE2-
Whitelee | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Whitelee 275/33kV | 2 | 0 | 50 | 355 | 2031-05-02 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005imeQAA | PRO-000067-2 | WLEE2 | 0 | WLEE2-
Whitelee | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Whitelee 275/33kV | 3 | 0 | 305 | 660 | 2033-04-25 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005imeQAA | PRO-000067-3 |  | 0
Whitelee | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Whitelee 275/33kV | 4 | 0 | 158 | 818 | 2034-04-27 | Scoping | Direct Connection | SPT | Wind Onshore | a0l4L0000005imeQAA | PRO-000067-4 |  | 0
Whitelee Extension | SCOTTISHPOWER RENEWABLES (UK) LIMITED | Whitelee Extension 275/33kV |  | 206 | 32 | 238 | 2026-12-01 | Built | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l4L0000005imfQAA | PRO-000068 | WLEX2 | 238 | WLEX2-
Whiteleigh Farm | QAIR RENEWABLES UK LIMITED | Pyworthy 400kV Substation |  | 0 | 300 | 300 | 2036-12-06 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iMIQAY | PRO-002385 |  | 0
Whiteminhill Renewable Energy Park | VOLTALIA UK LTD | Mark Hill 275/33kV |  | 0 | 220 | 220 | 2036-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e000000ewwdAAA | PRO-003693 | MAHI1 | 0 | MAHI1-
Whiteside Hill Wind Farm | WHITESIDE HILL WINDFARM (SCOTLAND) LIMITED | Glenglass 132/33kV |  | 27 | 0 | 27 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005irLQAQ | PRO-000267 | GLGL3 | 27 | GLGL3-
Whitson | PIVOTED POWER LLP | Whitson 275kV Substation |  | 0 | 49.9 | 49.9 | 2026-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005ieFQAQ | PRO-001061 | WHSO21 | 49.9 | WHSO21
Whitson BESS | FIELD DEVCO LTD | Whitson 275kV Substation |  | 0 | 150 | 150 | 2037-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f4iOAAQ | PRO-003862 | WHSO21 | 0 | WHSO21
Whitson BESS NP | NORIKER POWER LTD | South Wales East Node A 275kV Substation |  | 0 | 350 | 350 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TP6fAAG | PRO-003102 | WHSO2 | 0 | WHSO21
Wick Moor Drove | BSR APPLICATIONS LIMITED | West Country Connection Node D 400kV Substation |  | 0 | 500 | 500 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Wind Onshore | a0l8e0000012krQAAQ | PRO-004788 |  | 0
Willington | PIVOTED POWER LLP | Willington East 400kV Substation |  | 0 | 57 | 57 | 2026-06-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005islQAA | PRO-000326 | WILE4 | 57 | WILE41
Willington | SSE UTILITY SOLUTIONS LIMITED | Willington 400kV Substation |  | 0 | 600 | 600 | 2029-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iuYQAQ | PRO-002257 | WILE4 | 600 | WILE41
Willington BESS Station | IB VOGT UK LTD | Willington 400kV Substation |  | 0 | 240 | 240 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000exSiAAI | PRO-003727 | WILL1 | 0 | WILL11
Willington East 1 (Tertiary) | ENSO GREEN HOLDINGS LIMITED | Willington East 400kV Substation | 1 | 0 | 49.9 | 49.9 | 2025-06-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ippQAA | PRO-000551-1 | WILE4 | 49.9 | WILE41
Willington East 1 (Tertiary) | ENSO GREEN HOLDINGS LIMITED | Willington East 400kV Substation | 2 | 0 | 7.1 | 57 | 2027-06-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ippQAA | PRO-000551-2 | WILE4 | 7.1 | WILE41
Willington East 2 (Tertiary) | ENSO GREEN HOLDINGS LIMITED | Willington East 400kV Substation | 2 | 0 | 7.1 | 57 | 2027-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ipsQAA | PRO-000548-2 | WILE4 | 7.1 | WILE41
Willington East 2 (Tertiary) | ENSO GREEN HOLDINGS LIMITED | Willington East 400kV Substation | 1 | 0 | 49.9 | 49.9 | 2025-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ipsQAA | PRO-000548-1 | WILE4 | 49.9 | WILE41
Willington Energy Park | BROCKWELL STORAGE & SOLAR LIMITED | Willington 400kV Substation |  | 0 | 500 | 500 | 2028-03-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iYwQAI | PRO-001964 | WILE4 | 500 | WILE41
Willington Green Energy Centre | WILLINGTON GREEN ENERGY LIMITED | Willington 400kV Substation | 1 | 0 | 400 | 400 | 2026-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l4L0000005ikHQAQ | PRO-001797-1 | WILE4 | 400 | WILE41
Willington Green Energy Centre | WILLINGTON GREEN ENERGY LIMITED | Willington 400kV Substation | 2 | 0 | 625 | 1025 | 2029-10-30 | Awaiting Consents | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l4L0000005ikHQAQ | PRO-001797-2 | WILE4 | 625 | WILE41
Willington PV & BESS | WILLINGTON ENERGY PARK LIMITED | Willington East 400kV Substation |  | 0 | 249.9 | 249.9 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e000001HperAAC | PRO-004142 | WILE4 | 0 | WILE41
Wilton | SEMBCORP UTILITIES (UK) LIMITED | Wilton 66kV Substation |  | 141 | 0 | 141 |  | Built | Direct Connection | NGET | CCGT (Combined Cycle Gas Turbine) | a0l4L0000005izeQAA | PRO-000228 | WILT2 | 141 | WILT2A
Windy Rig Wind Farm | WINDY RIG WIND FARM LIMITED | Blackhill 132/33kV |  | 42.8 | 0 | 42.8 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005iloQAA | PRO-000374 | BLAH3 | 42.8 | BLAH3A
Windy Standard II (Brockloch Rig) Wind Farm | BROCKLOCH RIG WINDFARM LIMITED | Dun Hill 132/33kV | 1 | 61.5 | 0 | 61.5 |  | Built | Direct Connection | SPT | Wind Onshore | a0l4L0000005iqjQAA | PRO-000233-1 | DUNH3 | 61.5 | DUNH3-
Windy Standard II (Brockloch Rig) Wind Farm | BROCKLOCH RIG WINDFARM LIMITED | Dun Hill 132/33kV | 2 | 0 | 13.5 | 75 | 2024-06-30 | Consents Approved | Direct Connection | SPT | Wind Onshore | a0l4L0000005iqjQAA | PRO-000233-2 | DUNH3 | 13.5 | DUNH3-
Windy Standard III Wind Farm | Windy Standard III Ltd | Dun Hill 132/33kV | 1 | 0 | 43.5 | 43.5 | 2026-06-01 | Awaiting Consents | Direct Connection | SPT | Wind Onshore | a0l4L0000005iteQAA | PRO-000359-1 | DUNH3 | 43.5 | DUNH3-
Windy Standard III Wind Farm | Windy Standard III Ltd | Dun Hill 132/33kV | 2 | 0 | 42 | 85.5 | 2026-06-01 | Awaiting Consents | Direct Connection | SPT | Wind Onshore | a0l4L0000005iteQAA | PRO-000359-2 | DUNH3 | 42 | DUNH3-
Windy Standard III Wind Farm | Windy Standard III Ltd | Dun Hill 132/33kV | 3 | 0 | 10.5 | 96 | 2026-06-01 | Awaiting Consents | Direct Connection | SPT | Wind Onshore | a0l4L0000005iteQAA | PRO-000359-3 | DUNH3 | 10.5 | DUNH3-
WindyHill BESS2 Facility | ENERGYGRIDPOWER LTD | Windyhill 275/132kV |  | 0 | 200 | 200 | 2025-07-27 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005ib7QAA | PRO-002032 | WIYH1 | 200 | WIYH1-
WindyHill Energy Storage Facility | ENERGYGRIDPOWER LTD | Windyhill 275/132kV |  | 0 | 200 | 200 | 2025-08-27 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005iesQAA | PRO-001696 | WIYH1 | 200 | WIYH1-
Wishaw Energy Storage Facility | ZENOBE WISHAW LIMITED | Wishaw 400/275kV |  | 49.95 | 0 | 49.95 |  | Built | Direct Connection | SPT | Energy Storage System | a0l4L0000005ixRQAQ | PRO-001433 | WISH2 | 49.95 | WISH2-
Woburn Solar Farm | SolarThree Ltd | Dunstable 400kV Substation |  | 0 | 840 | 840 | 2031-10-31 | Scoping | Direct Connection | NGET | PV Array (Photo Voltaic/solar) | a0l8e0000010x0FAAQ | PRO-003033 | SUND4 | 0 | SUND41
Womblehill BESS Farm | RE Projects Development Limited | Womblehill BESS Farm 132kV |  | 0 | 200 | 200 | 2029-12-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l4L0000005itjQAA | PRO-002197 |  | 200
Woodcock Faulds Battery Storage | Woodcock Faulds Battery Storage Limited | Denny North |  | 0 | 200 | 200 | 2029-10-31 | Scoping | Direct Connection | SPT | Demand;Energy Storage System | a0l8e0000010wXLAAY | PRO-002663 | DENN | 200 | DENN1-
Woodcock Hill Wind Farm | ORSTED ONSHORE UK LIMITED | Woodcock Hill WF Substation |  | 0 | 90 | 90 | 2032-10-31 | Scoping | Direct Connection | SHET | Energy Storage System;Wind Onshore | a0l8e000001HxcZAAS | PRO-004282 |  | 0
Woodland Ridge | CUBICO UK DEVELOPMENT LIMITED | Hawick 132kV Substation |  | 0 | 150 | 150 | 2034-07-03 | Scoping | Direct Connection | SPT | Energy Storage System;Wind Onshore | a0lJ9000000PDz2IAG | PRO-005110 |  | 0
Worksop BESS | ARM Cedar Limited | Trent Valley South Connection Node B 400kV Substation. |  | 0 | 480 | 480 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000ewOYAAY | PRO-003657 |  | 0
Worset PV & BESS Park | Worcestershire Solar 1 Limited | Hartmoor 275kV Substation |  | 0 | 37.5 | 37.5 | 2024-06-07 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ieLQAQ | PRO-001055 | HARM2 | 37.5 | HARM21
Wylfa Substation | WYLFA GREEN LIMITED | Wylfa 132kV Substation |  | 0 | 120 | 120 | 2029-06-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005ioDQAQ | PRO-000506 | WYLF1 | 120 | WYLF11
Wymondley | PIVOTED POWER LLP | Wymondley 400kV Substation |  | 0 | 57 | 57 | 2025-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005iOgQAI | PRO-001245 | WYMO4 | 57 | WYMO41
Wymondley | ENSO GREEN HOLDINGS LIMITED | Wymondley 400kV Substation | 3 | 0 | 100 | 400 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iyNQAQ | PRO-002187-3 | WYMO4 | 0 | WYMO41
Wymondley | ENSO GREEN HOLDINGS LIMITED | Wymondley 400kV Substation | 1 | 0 | 200 | 200 | 2031-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iyNQAQ | PRO-002187-1 | WYMO4 | 0 | WYMO41
Wymondley | ENSO GREEN HOLDINGS LIMITED | Wymondley 400kV Substation | 2 | 0 | 100 | 300 | 2032-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iyNQAQ | PRO-002187-2 | WYMO4 | 0 | WYMO41
Wymondley BESS Limited | AGR RENEWABLES LIMITED | Wymondley 400kV Substation |  | 0 | 35.5 | 35.5 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e0000011y2SAAQ | PRO-003496 | WYMO4 | 0 | WYMO41
Wymondley Farm | Wymondley 10 Renewables Ltd | Wymondley 2 400kV Substation |  | 0 | 1000 | 1000 | 2032-10-30 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L000002yQZjQAM | PRO-002552 | WYMO4 | 0 | WYMO41
Wymondley GEC (Ethos Green) | WYMONDLEY GREEN ENERGY CENTRE LTD | Wymondley 400kV Substation |  | 0 | 700 | 700 | 2032-10-30 | Awaiting Consents | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l8e000000f5Y7AAI | PRO-003934 | WYMO4 | 0 | WYMO41
Wymondley High Impact Green Energy Hub (HIGEH) 1 | TELIS ENERGY UK LIMITED | Wymondley 2 400kV Substation |  | 0 | 1000 | 1000 | 2033-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation;Wind Onshore | a0l8e0000010wWrAAI | PRO-002659 | WYMO4 | 0 | WYMO41
Wymondley Solar Farm | AGR SOLAR 4 LIMITED | Wymondley 400kV Substation |  | 0 | 49.995 | 49.995 | 2025-10-31 | Consents Approved | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005igqQAA | PRO-001105 | WYMO4 | 49.995 | WYMO41
Wyseby Hill Energy Farm | WYSEBYHILL ENERGY FARM LIMITED | Wyseby Hill Energy Farm 400kV Substation |  | 0 | 750 | 750 | 2031-10-31 | Scoping | Direct Connection | SPT | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l4L0000005iQSQAY | PRO-001884 |  | 0
Y Bryn Wind Farm | Y BRYN WIND FARM LIMITED | Margam 275kV Substation |  | 0 | 151.2 | 151.2 | 2029-05-10 | Scoping | Direct Connection | NGET | Wind Onshore | a0l4L0000005ib4QAA | PRO-002029 | MAGA2 | 151.2 | MAGA21
Yaxley | CONNECTID 2 LIMITED | North Anglia Connection Node E 400kV Substation |  | 0 | 520 | 520 | 2034-10-31 | Scoping | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l8e000000TPMiAAO | PRO-003272 | YAXL4 | 0 | YAXL41
Yaxley BESS | FIELD DEVCO LTD | North Anglia Connection Node E 400kV Substation |  | 0 | 200 | 200 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f6ABAAY | PRO-003964 | YAXL4 | 0 | YAXL41
Yaxley Farm | 548 UK INVESTMENT HOLDINGS LIMITED | Yaxley 400kV Substation |  | 0 | 200 | 200 | 2032-10-31 | Scoping | Direct Connection | NGET | Energy Storage System;PV Array (Photo Voltaic/solar) | a0l8e0000010wZMAAY | PRO-002688 | YAXL4 | 0 | YAXL41
Yaxley GEC (Ethos Green) | YAXLEY GREEN ENERGY CENTRE LTD | Yaxley 400kV Substation |  | 0 | 450 | 450 | 2031-10-31 | Awaiting Consents | Direct Connection | NGET | Demand;Energy Storage System;PV Array (Photo Voltaic/solar);Reactive Compensation | a0l8e000000f5YCAAY | PRO-003935 | YAXL4 | 0 | YAXL41
Zenobe Blackhillock 300 MW | ZENOBE BLACKHILLOCK LIMITED | Blackhillock 275kV Substation | 1 | 200 | 0 | 200 |  | Built | Direct Connection | SHET | Energy Storage System | a0l4L0000005iNTQAY | PRO-001624-1 | BLHI2 | 200 | BLHI2A
Zenobe Blackhillock 300 MW | ZENOBE BLACKHILLOCK LIMITED | Blackhillock 275kV Substation | 2 | 0 | 100 | 300 | 2026-04-01 | Consents Approved | Direct Connection | SHET | Energy Storage System | a0l4L0000005iNTQAY | PRO-001624-2 | BLHI2 | 100 | BLHI2A
Zenobe Butler's Wood BESS | Zenobe Energy Limited | Butlers Wood 400kV Substation |  | 0 | 330 | 330 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001Hod1AAC | PRO-004085 | TWIN4A | 0 | TWIN4A
Zenobe Coalburn Battery Storage | Zenobe Coalburn Limited | Coalburn 400kV Substation |  | 0 | 200 | 200 | 2026-06-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005j1WQAQ | PRO-001780 | COAL4 | 200 | COAL4-
Zenobe Eccles Battery Storage | Zenobe Eccles Limited | Eccles 132/33kV |  | 0 | 400 | 400 | 2026-04-30 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005ij4QAA | PRO-001779 | ECCL1 | 400 | ECCL1-
Zenobe Energy Kilmarnock South | ZENOBE KILMARNOCK SOUTH LIMITED | Kilmarnock South 400kV Substation |  | 0 | 300 | 300 | 2025-08-29 | Scoping | Direct Connection | SPT | Energy Storage System | a0l4L0000005ieoQAA | PRO-001687 | KILS4 | 300 | KILS4-
Zenobe Hartmoor BESS | Zenobe Energy Limited | Hartmoor 275kV Substation |  | 0 | 300 | 300 | 2035-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000ewx2AAA | PRO-003696 | HARM2 | 0 | HARM21
Zenobe Hawthorn Pit BESS | Zenobe Energy Limited | Hawthorn Pit 400kV Substation |  | 0 | 300 | 300 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001Hod6AAC | PRO-004086 | HAWP41 | 0 | HAWP41
Zenobe Little Horsted BESS | Zenobe Energy Limited | Little Horsted 400kV Substation |  | 0 | 300 | 300 | 2037-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000f8PiAAI | PRO-004032 | LHOR4 | 0 | LHOR4A
Zenobe Necton BESS | Zenobe Energy Limited | Necton 400kV Substation |  | 0 | 300 | 300 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000TPQMAA4 | PRO-003402 | NECT4 | 0 | NECT41
Zenobe New Deer Battery Storage | Zenobe Energy Limited | New Deer 400kV Substation |  | 0 | 200 | 200 | 2029-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l4L0000005ij3QAA | PRO-001778 | NEDE4 | 200 | NEDE4J
Zenobe Norton | Zenobe Energy Limited | Norton 400kV Substation |  | 0 | 150 | 150 | 2031-10-31 | Awaiting Consents | Direct Connection | NGET | Energy Storage System | a0l4L0000005iy8QAA | PRO-001691 | NORT4 | 0 | NORT41
Zenobe Spennymoor BESS | Zenobe Energy Limited | Spennymoor 400kV Substation |  | 0 | 300 | 300 | 2034-10-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000000ewwYAAQ | PRO-003692 | SPEN42 | 0 | SPEN42
Zenobe Stalybridge Project | Zenobe Energy Limited | Stalybridge 275kV Substation |  | 0 | 150 | 150 | 2026-09-30 | Scoping | Direct Connection | NGET | Energy Storage System | a0l4L0000005iuVQAQ | PRO-001940 | STAL2 | 150 | STAL21
Zenobe Yaxley BESS | Zenobe Energy Limited | North Anglia Connection Node E 400kV Substation |  | 0 | 300 | 300 | 2034-10-31 | Scoping | Direct Connection | NGET | Energy Storage System | a0l8e000001HodGAAS | PRO-004088 | YAXL4 | 0 | YAXL41
[23-0225] UPPER GREENFIELDS - 175MW BESS | Lower 48 Energy BESS Limited | New Deer 2 400kV Substation |  | 0 | 175 | 175 | 2033-10-31 | Scoping | Direct Connection | SHET | Energy Storage System | a0l8e000000ewjHAAQ | PRO-003682 | NEDE4 | 0 | NEDE4J

## IC Register
Project Name | Customer Name | Connection Site | Stage | MW Import - Current | MW Export - Current | MW Import - Increase / Decrease | MW Export - Increase / Decrease | MW Import - Total | MW Export - Total | MW Effective From | Project Status | HOST TO | Project Number | Node_Name | MW_Import_Capacity | MW_Export_Capacity | ETYS_Node
Aquind Interconnector | Aquind Limited | Lovedean 400kV Substation |  | 0 | 0 | 2000 | 2075 | 2000 | 2075 | 2030-06-30 | Awaiting Consents | NGET | PRO-000285 | LOVE4 | 2000 | 2075 | LOVE41
Auchencrosh (interconnector CCT) | MOYLE INTERCONNECTOR LIMITED* | Auchencrosh 275kV | 1 | 270 | 500 | 205 | 0 | 475 | 500 | 2022-04-01 | Built | SPT | PRO-001292-1 | AUCH2 | 475 | 500 | AUCH2-
Auchencrosh (interconnector CCT) | MOYLE INTERCONNECTOR LIMITED* | Auchencrosh 275kV | 2 | 475 | 500 | 25 | 0 | 500 | 500 | 2022-08-01 | Built | SPT | PRO-001292-2 | AUCH2 | 25 | 0 | AUCH2-
Britned | BRITNED DEVELOPMENT LIMITED | Grain 400kV Substation |  | 1200 | 1200 | 0 | 0 | 1200 | 1200 |  | Built | NGET | PRO-000280 | GRAI4 | 1200 | 1200 | GRAI41
Celtic MPI | NATIONAL GRID INTERCONNECTOR HOLDINGS LIMITED | Alverdiscott 400kV Substation |  | 0 | 0 | 1500 | 1500 | 1500 | 1500 | 2037-10-31 | Scoping | NGET | PRO-003461 | ALVE4 | 0 | 0 | ALVE41
Continental Link | NATIONAL GRID INTERCONNECTOR HOLDINGS LIMITED | Creyke Beck 400kV Substation |  | 0 | 0 | 1800 | 1800 | 1800 | 1800 | 2027-09-01 | Scoping | NGET | PRO-000977 | CREB4 | 1800 | 1800 | CREB41
Cronos | CRONOS ENERGY LTD | Kemsley 400kV Substation |  | 0 | 0 | 1400 | 1400 | 1400 | 1400 | 2029-10-31 | Scoping | NGET | PRO-000984 | KEMS4 | 1400 | 1400 | KEMS41
East West Interconnector | EIRGRID INTERCONNECTOR DESIGNATED ACTIVITY COMPANY | Deeside 400kV Substation |  | 505 | 585 | 0 | 0 | 505 | 585 |  | Built | NGET | PRO-000284 | CONQ4 | 505 | 585 | CONQ41
ElecLink | ELECLINK LIMITED | Sellindge 400kV Substation |  | 1000 | 1050 | 0 | 0 | 1000 | 1050 |  | Built | NGET | PRO-000286 | SELL4 | 1000 | 1050 | SELL4A
FAB Link Interconnector | FAB LINK LIMITED | Exeter 400kV Substation |  | 0 | 0 | 1250 | 1310 | 1250 | 1310 | 2027-10-01 | Awaiting Consents | NGET | PRO-000281 | EXET4 | 1250 | 1310 | EXET41
GB-EU MPI | Windgrid | Fiddes 400kV Substation |  | 0 | 0 | 1800 | 1800 | 1800 | 1800 | 2033-10-31 | Scoping | SHET | PRO-004398 | FIDD4 | 0 | 0 | FIDD3-
Greenlink | GREENLINK INTERCONNECTOR LIMITED | Pembroke 400kV Substation |  | 504 | 524 | 0 | 0 | 504 | 524 |  | Built | NGET | PRO-000279 | PEMB4 | 504 | 524 | PEMB41
Gridlink Interconnector | GRIDLINK INTERCONNECTOR LIMITED | Kingsnorth 400kV Substation |  | 0 | 0 | 1500 | 1500 | 1500 | 1500 | 2029-03-31 | Scoping | NGET | PRO-000287 | KINO4 | 1500 | 1500 | KINO41
IFA Interconnector | NATIONAL GRID INTERCONNECTORS LIMITED | Sellindge 400kV Substation |  | 1988 | 1988 | 0 | 0 | 1988 | 1988 |  | Built | NGET | PRO-000282 | SELL4 | 1988 | 1988 | SELL4A
IFA2 Interconnector | NATIONAL GRID IFA 2 LIMITED | Chilling 400kV Substation |  | 1100 | 1150 | 0 | 0 | 1100 | 1150 |  | Built | NGET | PRO-000283 | CHIL4 | 1100 | 1150 | CHIL41
Isle of Man Interconnector | MANX UTILITIES | Bispham 132kV Substation |  | 74 | 74 | 0 | 0 | 74 | 74 |  | Built | NGET | PRO-001291 | PEWO2 | 74 | 74 | PEWO2A
Kulizumboo Interconnector | KULIZUMBOO LIMITED | Canterbury North 400kV Substation |  | 0 | 0 | 700 | 700 | 700 | 700 | 2031-04-01 | Scoping | NGET | PRO-001290 | CANT4 | 0 | 0 | CANT41
LionLink (EuroLink) | NATIONAL GRID INTERCONNECTOR HOLDINGS LIMITED | Friston 400kV Substation |  | 0 | 0 | 1600 | 1600 | 1600 | 1600 | 2024-10-30 | Scoping | NGET | PRO-000983 | FRIS4 | 1600 | 1600 | FRIS41
LIRIC Interconnector | TI LIRIC Limited | Hunterston East 400kV |  | 0 | 0 | 730 | 700 | 730 | 700 | 2032-10-31 | Scoping | SPT | PRO-001454 | HUNE4 | 0 | 0 | HUNE4-
Low Carbon Link | LOW CARBON SOLAR PARK 39 LIMITED | Pembroke GSP |  | 0 | 0 | 1400 | 1400 | 1400 | 1400 | 2037-10-31 | Scoping | NGET | PRO-004262 | PEMB4 | 0 | 0 | PEMB41
MARES | Maresconnect Limited | Bodelwyddan 400kV Substation |  | 0 | 0 | 750 | 750 | 750 | 750 | 2028-11-30 | Awaiting Consents | NGET | PRO-000978 | BODE4 | 750 | 750 | BODE41
Nautilus | NATIONAL GRID INTERCONNECTOR HOLDINGS LIMITED | Wallend 400kV Substation |  | 0 | 0 | 1500 | 1500 | 1500 | 1500 | 2029-10-31 | Scoping | NGET | PRO-000976 | WALE4 | 1500 | 1500 | WALE41
Nemo Link | NEMO LINK LIMITED | Richborough 400kV Substation |  | 1020 | 1046 | 0 | 0 | 1020 | 1046 |  | Built | NGET | PRO-000974 | RICH4 | 1020 | 1046 | RICH41
NeuConnect Interconnector | Neuconnect Britain Ltd | Grain West 400kV Substation |  | 0 | 0 | 1400 | 1470 | 1400 | 1470 | 2026-08-01 | Under Construction/Commissioning | NGET | PRO-001288 | WALE4 | 1400 | 1470 | WALE41
NorthConnect | NORTHCONNECT LIMITED | Peterhead 400kV Substation |  | 0 | 0 | 1400 | 1400 | 1400 | 1400 | 2030-03-01 | Scoping | SHET | PRO-001285 | PEHE4 | 1400 | 1400 | PEHE4J
NS Link | NATIONAL GRID NORTH SEA LINK LIMITED | Blyth GSP |  | 1400 | 1480 | 0 | 0 | 1400 | 1480 |  | Built | NGET | PRO-000975 | BLYT4 | 1400 | 1480 | BLYT41
Project Cobalt | GETLINK PROJECTS 2 LIMITED | East Kent Connection Node B 400kV Substation |  | 0 | 0 | 1000 | 1050 | 1000 | 1050 | 2036-10-30 | Scoping | NGET | PRO-004402 | RICH4 | 0 | 0 | RICH41
SENECA | FRONTIER POWER INTERNATIONAL LIMITED | Mablethorpe 400kV Substation |  | 0 | 0 | 1200 | 1254 | 1200 | 1254 | 2031-11-30 | Scoping | NGET | PRO-000981 | MABL4 | 0 | 0
Tarchon | TARCHON ENERGY LIMITED | East Anglia Connection Node 400kV Substation |  | 0 | 0 | 1400 | 1400 | 1400 | 1400 | 2030-10-31 | Scoping | NGET | PRO-001289 |  | 1400 | 1400
Teeside MPI | NATIONAL GRID INTERCONNECTOR HOLDINGS LIMITED | Wearside Connection Node B 400kV Substation |  | 0 | 0 | 1800 | 1800 | 1800 | 1800 | 2033-10-31 | Scoping | NGET | PRO-003462 |  | 0 | 0
The Superconnection | ASC ENERGY LIMITED | Creyke Beck 400kV Substation |  | 0 | 0 | 1000 | 1000 | 1000 | 1000 | 2027-09-01 | Scoping | NGET | PRO-001284 | CREB4 | 1000 | 1000 | CREB41
Viking Link Denmark Interconnector | NATIONAL GRID VIKING LINK LIMITED | Bicker Fen 400kV Substation |  | 1500 | 1500 | 0 | 0 | 1500 | 1500 |  | Built | NGET | PRO-000288 | BICF4 | 1500 | 1500 | BICF41
Western MPI | NATIONAL GRID INTERCONNECTOR HOLDINGS LIMITED | Connah's Quay 400kV Substation |  | 0 | 0 | 1500 | 1500 | 1500 | 1500 | 2037-10-31 | Scoping | NGET | PRO-003463 | CONQ4 | 0 | 0 | CONQ41

## Demand Data
scenario | year | DemandPk | DemandAM | DemandPM | type | Node_Name | Name | Minor Flop | Major Flop | ETYS_Node | GSP
HT | 30 | 185.725 | 58.6005 | 132.39 | C,D,E,H,I,R,Z | ABHA1 | Abham | F6 | F | ABHA11 | ABHA1
HT | 30 | 185.725 | 58.6005 | 132.39 | C,D,E,H,I,R,Z | ABHA1 | Abham | F6 | F | ABHA12 | ABHA1
HT | 30 | 36.475 | 13.093 | 539.247 | C,D,E,H,I,R,Z | ABNE3 | Abernethy | T4 | T | ABNE3- | ABNEP
HT | 30 | 70.291 | 27.193 | 53.215 | C,D,E,H,I,R,Z | ABTH1 | Aberthaw | H2 | H | ABTH11 | ABTH1
HT | 30 | 70.291 | 27.193 | 53.215 | C,D,E,H,I,R,Z | ABTH1 | Aberthaw | H2 | H | ABTH12 | ABTH1
HT | 30 | 70.291 | 27.193 | 53.215 | C,D,E,H,I,R,Z | ABTH1 | Aberthaw | H2 | H | ABTH13 | ABTH1
HT | 30 | 71.721 | 71.721 | 71.721 | T | ALDW2 | Corus Aldwarke | P3 | P | ALDW21 | TMYELT001
HT | 30 | 31.028 | 14.04 | 24.743 | C,D,E,H,I,R,Z | ALNE3 | Alness | T5 | T | ALNE3J | ALNEP
HT | 30 | 4.4135 | 1.0175 | 5.058 | C,D,E,H,I,R,Z | ALST3 | Alpha Steel (Uskmouth) | H2 | H | ALST31 | ALST3
HT | 30 | 4.4135 | 1.0175 | 5.058 | C,D,E,H,I,R,Z | ALST3 | Alpha Steel (Uskmouth) | H2 | H | ALST32 | ALST3
HT | 30 | 312.264 | 91.958 | 268.515 | C,D,E,H,I,R,Z | ALVE1 | Alverdiscott | F6 | F | ALVE11 | ALVE1
HT | 30 | 174.919 | 37.553 | 68.447 | C,D,E,H,I,R,Z | AMEM1 | Amersham Main,Loudwater | A6 | A | AMEM11 | AMEM1
HT | 30 | 47.611 | 13.431 | 18.919 | C,D,E,H,I,R,Z | ARBR3 | Arbroath | T4 | T | ARBR3- | ARBRP
HT | 30 | 0 | 0 | 0 | C,D,E,H,I,R,Z | ARDK3 | Ardkinglas | T3 | T | ARDK3K | ARDKP
HT | 30 | 38.312 | 9.307 | 52.062 | C,D,E,H,I,R,Z | ARMO3 | Ardmore | T1 | T | ARMO3- | ARMOP
HT | 30 | 176.272 | 58.321 | 153.366 | C,D,E,H,I,R,Z | AXMI1 | Axminster,Axminster H | E1 | E | AXMI11 | AXMI1
HT | 30 | 13.1233 | 4.9033 | 7.8017 | C,D,E,H,I,R,Z | AYR- | Ayr | S6 | S | AYR-2Q | AYRR
HT | 30 | 13.1233 | 4.9033 | 7.8017 | C,D,E,H,I,R,Z | AYR- | Ayr | S6 | S | AYR-2R | AYRR
HT | 30 | 13.1233 | 4.9033 | 7.8017 | C,D,E,H,I,R,Z | AYR- | Ayr | S6 | S | AYR-3- | AYRR
HT | 30 | 1.8245 | 1.8245 | 1.8245 | T | BAGA1 | Bathgate (Network Rail) | S5 | S | BAGA1Q | TBAGTD-1
HT | 30 | 1.8245 | 1.8245 | 1.8245 | T | BAGA1 | Bathgate (Network Rail) | S5 | S | BAGA1R | TBAGTD-1
HT | 30 | 39.912 | 16.288 | 27.138 | C,D,E,H,I,R,Z | BAGA3 | Bathgate | S5 | S | BAGA3- | BAGA
HT | 30 | 0 | 0 | 0 | T | BAGB2 | Baglan Energy Park | H1 | H | BAGB21 | TBAGED-1
HT | 30 | 25.036 | 9.295 | 44.143 | C,D,E,H,I,R,Z | BAIN3 | Bainsford | S5 | S | BAIN3- | BAIN
HT | 30 | 170.3493 | 46.319 | 99.5978 | C,D,E,H,I,R,T,Z | BARK1,BARK3 | Barking,Barking NR,Barking West | A1 | A | BARK11 | BARKC1
HT | 30 | 57.9083 | 20.646 | 29.0938 | C,D,E,H,I,R,Z | BARK3 | Barking West | A1 | A | BARK21 | BARKW3
HT | 30 | 57.9083 | 20.646 | 29.0938 | C,D,E,H,I,R,Z | BARK3 | Barking West | A1 | A | BARK22 | BARKW3
HT | 30 | 90.1992 | 52.937 | 61.3847 | C,D,E,H,I,R,T,Z | BARK3,BARK4 | Barking Chnl Tunnel RLink,Barking West | A1 | A | BARK41 | BARKW3
HT | 30 | 2.343 | 1.3832 | 1.9641 | C,D,E,H,I,R,Z | BEAU1 | Beauly | T1 | T | BEAU1J | BEAUP
HT | 30 | 2.343 | 1.3832 | 1.9641 | C,D,E,H,I,R,Z | BEAU1 | Beauly | T1 | T | BEAU1K | BEAUP
HT | 30 | 2.343 | 1.3832 | 1.9641 | C,D,E,H,I,R,Z | BEAU1 | Beauly | T1 | T | BEAU1L | BEAUP
HT | 30 | 2.343 | 1.3832 | 1.9641 | C,D,E,H,I,R,Z | BEAU1 | Beauly | T1 | T | BEAU1M | BEAUP
HT | 30 | 2.343 | 1.3832 | 1.9641 | C,D,E,H,I,R,Z | BEAU1 | Beauly | T1 | T | BEAU1N | BEAUP
HT | 30 | 2.343 | 1.3832 | 1.9641 | C,D,E,H,I,R,Z | BEAU1 | Beauly | T1 | T | BEAU1P | BEAUP
HT | 30 | 2.343 | 1.3832 | 1.9641 | C,D,E,H,I,R,Z | BEAU1 | Beauly | T1 | T | BEAU1Q | BEAUP
HT | 30 | 2.343 | 1.3832 | 1.9641 | C,D,E,H,I,R,Z | BEAU1 | Beauly | T1 | T | BEAU1R | BEAUP
HT | 30 | 2.343 | 1.3832 | 1.9641 | C,D,E,H,I,R,Z | BEAU1 | Beauly | T1 | T | BEAU1S | BEAUP
HT | 30 | 2.343 | 1.3832 | 1.9641 | C,D,E,H,I,R,Z | BEAU1 | Beauly | T1 | T | BEAU1T | BEAUP
HT | 30 | 308.4425 | 94.4695 | 175.428 | C,D,E,H,I,R,Z | BEDD1 | Beddington (_C),Beddington (_J) | A8 | A | BEDD11 | BEDDT1
HT | 30 | 308.4425 | 94.4695 | 175.428 | C,D,E,H,I,R,Z | BEDD1 | Beddington (_C),Beddington (_J) | A8 | A | BEDD12 | BEDDT1
HT | 30 | 0 | 0 | 0 | C,D,E,H,I,R,Z | BERB3 | Berryburn | T1 | T | BERB3- | BERBP
HT | 30 | 26.247 | 21.511 | 32.527 | C,D,E,H,I,R,Z | BERW3 | Berwick | S6 | S | BERW3- | BERW
HT | 30 | 238.8435 | 120.7475 | 171.2155 | C,D,E,H,I,R,T,Z | BESW1 | Berkswell,Berkswell (Rail) | L3 | L | BESW11 | BESW1
HT | 30 | 238.8435 | 120.7475 | 171.2155 | C,D,E,H,I,R,T,Z | BESW1 | Berkswell,Berkswell (Rail) | L3 | L | BESW12 | BESW1
HT | 30 | 0 | 0 | 0 | T | [5 empty] | BEXTRA1
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P8 | P |  | BEXTRA100
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA101
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA102
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A6 | A |  | BEXTRA103
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T2 | T |  | BEXTRA104
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T2 | T |  | BEXTRA105
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA106
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA107
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T2 | T |  | BEXTRA108
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P3 | P |  | BEXTRA109
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L3 | L |  | BEXTRA11
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P6 | P |  | BEXTRA110
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | C6 | C |  | BEXTRA111
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A7 | A |  | BEXTRA112
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P4 | P |  | BEXTRA113
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P8 | P |  | BEXTRA114
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P4 | P |  | BEXTRA115
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P6 | P |  | BEXTRA116
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P8 | P |  | BEXTRA117
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A8 | A |  | BEXTRA118
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | Q6 | Q |  | BEXTRA119
HT | 30 | 0 | 0 | 2.031 | T |  | Grid-connected electrolysis | F6 | F |  | BEXTRA12
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA120
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T4 | T |  | BEXTRA121
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA122
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A8 | A |  | BEXTRA123
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A7 | A |  | BEXTRA124
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T2 | T |  | BEXTRA125
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA126
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T2 | T |  | BEXTRA127
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA128
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA129
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L5 | L |  | BEXTRA13
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA130
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T2 | T |  | BEXTRA131
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA132
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA133
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA134
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A6 | A |  | BEXTRA135
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P5 | P |  | BEXTRA136
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T2 | T |  | BEXTRA137
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA138
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T2 | T |  | BEXTRA139
HT | 30 | 0 | 0 | 6.3422 | T |  | Grid-connected electrolysis | T4 | T |  | BEXTRA14
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA140
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA141
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA142
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA143
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A1 | A |  | BEXTRA144
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA145
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA146
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A8 | A |  | BEXTRA147
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA148
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | N1 | N |  | BEXTRA149
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A6 | A |  | BEXTRA15
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | C2 | C |  | BEXTRA151
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T2 | T |  | BEXTRA152
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A6 | A |  | BEXTRA153
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA154
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA155
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A8 | A |  | BEXTRA156
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A8 | A |  | BEXTRA157
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A7 | A |  | BEXTRA158
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA159
HT | 30 | 0 | 0 | 43.4236 | T |  | Grid-connected electrolysis | T5 | T |  | BEXTRA16
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P3 | P |  | BEXTRA160
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A4 | A |  | BEXTRA161
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A6 | A |  | BEXTRA162
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P3 | P |  | BEXTRA163
HT | 30 | 0 | 0 | 2.665 | T |  | Grid-connected electrolysis | B2 | B |  | BEXTRA164
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA165
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T2 | T |  | BEXTRA166
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P3 | P |  | BEXTRA167
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA168
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA169
HT | 30 | 0 | 0 | 2.6651 | T |  | Grid-connected electrolysis | B2 | B |  | BEXTRA17
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T2 | T |  | BEXTRA170
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | C7 | C |  | BEXTRA171
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A7 | A |  | BEXTRA172
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | Q4 | Q |  | BEXTRA173
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T2 | T |  | BEXTRA174
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T2 | T |  | BEXTRA175
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A1 | A |  | BEXTRA176
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | N1 | N |  | BEXTRA177
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A6 | A |  | BEXTRA178
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA179
HT | 30 | 0 | 0 | 2.6651 | T |  | Grid-connected electrolysis | B3 | B |  | BEXTRA18
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA180
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A1 | A |  | BEXTRA181
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A4 | A |  | BEXTRA182
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T2 | T |  | BEXTRA183
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A7 | A |  | BEXTRA184
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T2 | T |  | BEXTRA185
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A1 | A |  | BEXTRA186
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L2 | L |  | BEXTRA187
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L2 | L |  | BEXTRA188
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L3 | L |  | BEXTRA189
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | N3 | N |  | BEXTRA19
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L5 | L |  | BEXTRA190
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L3 | L |  | BEXTRA191
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L3 | L |  | BEXTRA192
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L3 | L |  | BEXTRA193
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L5 | L |  | BEXTRA194
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L2 | L |  | BEXTRA195
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L3 | L |  | BEXTRA196
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L2 | L |  | BEXTRA197
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L2 | L |  | BEXTRA198
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L5 | L |  | BEXTRA199
HT | 30 | 0 | 0 | 0 | T |  | Hydrogen-SMR-1 | T2 | T |  | BEXTRA2
HT | 30 | 0 | 0 | 39.2359 | T |  | Grid-connected electrolysis | P7 | P |  | BEXTRA20
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L2 | L |  | BEXTRA200
HT | 30 | 277.083 | 277.083 | 277.083 | T |  | Direct Connect for electrified offshore oil and gas platforms (INTOG) | T2 | T |  | BEXTRA201
HT | 30 | 360 | 360 | 360 | T |  | Port Talbot | H6 | H |  | BEXTRA202
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | H2 | H |  | BEXTRA203
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A7 | A |  | BEXTRA204
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | H2 | H |  | BEXTRA205
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | F6 | F |  | BEXTRA206
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A6 | A |  | BEXTRA207
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T4 | T |  | BEXTRA208
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | E1 | E |  | BEXTRA209
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T3 | T |  | BEXTRA21
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A1 | A |  | BEXTRA210
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA211
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA212
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A8 | A |  | BEXTRA213
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA214
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA215
HT | 30 | 0 | 0 | 0.009 | T |  | Grid-connected electrolysis | K4 | K |  | BEXTRA216
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | Q6 | Q |  | BEXTRA217
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA218
HT | 30 | 0 | 0 | 2.665 | T |  | Grid-connected electrolysis | B1 | B |  | BEXTRA219
HT | 30 | 0 | 0 | 325.4044 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA22
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA220
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T4 | T |  | BEXTRA221
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | J8 | J |  | BEXTRA222
HT | 30 | 0 | 0 | 0.651 | T |  | Grid-connected electrolysis | J5 | J |  | BEXTRA223
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | N2 | N |  | BEXTRA224
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A3 | A |  | BEXTRA225
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA226
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T5 | T |  | BEXTRA227
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA228
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T4 | T |  | BEXTRA229
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | E1 | E |  | BEXTRA23
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | J7 | J |  | BEXTRA230
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A7 | A |  | BEXTRA231
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | H2 | H |  | BEXTRA232
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA233
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T3 | T |  | BEXTRA234
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | N2 | N |  | BEXTRA235
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA236
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T5 | T |  | BEXTRA237
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA238
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA239
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | H6 | H |  | BEXTRA24
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T4 | T |  | BEXTRA240
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | E1 | E |  | BEXTRA241
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T3 | T |  | BEXTRA242
HT | 30 | 0 | 0 | 0.651 | T |  | Grid-connected electrolysis | J5 | J |  | BEXTRA243
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA244
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA245
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | M5 | M |  | BEXTRA246
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T4 | T |  | BEXTRA247
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA248
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA249
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | R4 | R |  | BEXTRA25
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA250
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA251
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA252
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA253
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T5 | T |  | BEXTRA254
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L2 | L |  | BEXTRA255
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA256
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA257
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T4 | T |  | BEXTRA258
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA259
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A1 | A |  | BEXTRA26
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T5 | T |  | BEXTRA260
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA261
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA262
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA263
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | D4 | D |  | BEXTRA264
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA265
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA266
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA267
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P1 | P |  | BEXTRA268
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L8 | L |  | BEXTRA269
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | C5 | C |  | BEXTRA27
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA270
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | F6 | F |  | BEXTRA271
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA272
HT | 30 | 0 | 0 | 2.665 | T |  | Grid-connected electrolysis | B2 | B |  | BEXTRA273
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P5 | P |  | BEXTRA274
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P6 | P |  | BEXTRA275
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T2 | T |  | BEXTRA276
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA277
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA278
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | Q8 | Q |  | BEXTRA279
HT | 30 | 0 | 0 | 658.259 | T |  | Grid-connected electrolysis | P1 | P |  | BEXTRA28
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA280
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA281
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA282
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA283
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA284
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A7 | A |  | BEXTRA285
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | J6 | J |  | BEXTRA286
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA287
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A1 | A |  | BEXTRA288
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | Q8 | Q |  | BEXTRA289
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | C4 | C |  | BEXTRA29
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | Q4 | Q |  | BEXTRA290
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | Q4 | Q |  | BEXTRA291
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA292
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | R5 | R |  | BEXTRA293
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | R5 | R |  | BEXTRA294
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA295
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | R6 | R |  | BEXTRA296
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | H6 | H |  | BEXTRA297
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | F6 | F |  | BEXTRA298
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA299
HT | 30 | 0 | 0 | 0 | T |  | Hydrogen-SMR-2 | P6 | P |  | BEXTRA3
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | D4 | D |  | BEXTRA30
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA300
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | G5 | G |  | BEXTRA301
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A7 | A |  | BEXTRA302
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A6 | A |  | BEXTRA303
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA304
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P3 | P |  | BEXTRA305
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA306
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | N4 | N |  | BEXTRA307
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | N4 | N |  | BEXTRA308
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA309
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | B4 | B |  | BEXTRA31
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA310
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T4 | T |  | BEXTRA311
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA312
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA313
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | N1 | N |  | BEXTRA314
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P1 | P |  | BEXTRA315
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P2 | P |  | BEXTRA316
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T5 | T |  | BEXTRA317
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | F6 | F |  | BEXTRA318
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | M4 | M |  | BEXTRA319
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | E7 | E |  | BEXTRA32
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA320
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | N1 | N |  | BEXTRA321
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A6 | A |  | BEXTRA322
HT | 30 | 0 | 0 | 2.665 | T |  | Grid-connected electrolysis | B2 | B |  | BEXTRA323
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T4 | T |  | BEXTRA324
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T4 | T |  | BEXTRA325
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | N6 | N |  | BEXTRA326
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | E1 | E |  | BEXTRA327
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA328
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | G6 | G |  | BEXTRA329
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | C1 | C |  | BEXTRA33
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T4 | T |  | BEXTRA330
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | G6 | G |  | BEXTRA331
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T5 | T |  | BEXTRA332
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA333
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA334
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA335
HT | 30 | 0 | 0 | 2.665 | T |  | Grid-connected electrolysis | B1 | B |  | BEXTRA336
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | C2 | C |  | BEXTRA337
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | Q4 | Q |  | BEXTRA338
HT | 30 | 0 | 0 | 0.651 | T |  | Grid-connected electrolysis | J3 | J |  | BEXTRA339
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | G1 | G |  | BEXTRA34
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | Q4 | Q |  | BEXTRA340
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | R5 | R |  | BEXTRA341
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA342
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | N5 | N |  | BEXTRA343
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA344
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | D5 | D |  | BEXTRA345
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | H6 | H |  | BEXTRA346
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | R4 | R |  | BEXTRA347
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A7 | A |  | BEXTRA348
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P2 | P |  | BEXTRA349
HT | 30 | 0 | 0 | 349.0401 | T |  | Grid-connected electrolysis | T2 | T |  | BEXTRA35
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T3 | T |  | BEXTRA350
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA351
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | H1 | H |  | BEXTRA352
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T1 | T |  | BEXTRA353
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | N1 | N |  | BEXTRA354
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T4 | T |  | BEXTRA355
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | H6 | H |  | BEXTRA356
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L7 | L |  | BEXTRA357
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A1 | A |  | BEXTRA358
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | Q8 | Q |  | BEXTRA359
HT | 30 | 0 | 0 | 151.8021 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA36
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | N4 | N |  | BEXTRA360
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A9 | A |  | BEXTRA361
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | G7 | G |  | BEXTRA362
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | Q2 | Q |  | BEXTRA363
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | G7 | G |  | BEXTRA364
HT | 30 | 0 | 0 | 0.651 | T |  | Grid-connected electrolysis | J3 | J |  | BEXTRA365
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T5 | T |  | BEXTRA366
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L5 | L |  | BEXTRA367
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA368
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA369
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA37
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P1 | P |  | BEXTRA370
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T3 | T |  | BEXTRA371
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | N2 | N |  | BEXTRA372
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA373
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | Q7 | Q |  | BEXTRA374
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T4 | T |  | BEXTRA375
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | M6 | M |  | BEXTRA376
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | N7 | N |  | BEXTRA377
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | R4 | R |  | BEXTRA378
HT | 30 | 0 | 0 | 0.009 | T |  | Grid-connected electrolysis | K5 | K |  | BEXTRA379
HT | 30 | 0 | 0 | 19.9993 | T |  | Grid-connected electrolysis | J4 | J |  | BEXTRA38
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | Q5 | Q |  | BEXTRA380
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | Q5 | Q |  | BEXTRA381
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA382
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | L7 | L |  | BEXTRA383
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA384
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA385
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | D4 | D |  | BEXTRA386
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | E8 | E |  | BEXTRA387
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T3 | T |  | BEXTRA388
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA389
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | N1 | N |  | BEXTRA39
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P3 | P |  | BEXTRA390
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P3 | P |  | BEXTRA391
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T5 | T |  | BEXTRA392
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA393
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | M7 | M |  | BEXTRA394
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T4 | T |  | BEXTRA395
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | Q4 | Q |  | BEXTRA396
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | Q4 | Q |  | BEXTRA397
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | H2 | H |  | BEXTRA398
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | H2 | H |  | BEXTRA399
HT | 30 | 0 | 0 | 0 | T |  | Hydrogen-SMR-3 | N3 | N |  | BEXTRA4
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | C3 | C |  | BEXTRA40
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | H2 | H |  | BEXTRA400
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | R4 | R |  | BEXTRA401
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | J1 | J |  | BEXTRA402
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | Q4 | Q |  | BEXTRA403
HT | 30 | 0 | 0 | 0.009 | T |  | Grid-connected electrolysis | K6 | K |  | BEXTRA404
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A7 | A |  | BEXTRA405
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P3 | P |  | BEXTRA406
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A8 | A |  | BEXTRA407
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | N4 | N |  | BEXTRA408
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA409
HT | 30 | 0 | 0 | 81.8424 | T |  | Grid-connected electrolysis | H1 | H |  | BEXTRA41
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A4 | A |  | BEXTRA410
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P3 | P |  | BEXTRA411
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA412
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | D5 | D |  | BEXTRA413
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA414
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA415
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA416
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA417
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA418
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA419
HT | 30 | 0 | 0 | 3.2608 | T |  | Grid-connected electrolysis | L1 | L |  | BEXTRA42
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S5 | S |  | BEXTRA420
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA421
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA422
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA423
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA424
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T5 | T |  | BEXTRA425
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T2 | T |  | BEXTRA426
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | T5 | T |  | BEXTRA427
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA428
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA429
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | D6 | D |  | BEXTRA43
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA430
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA431
HT | 30 | 0 | 0 | 247.6906 | T |  | Grid-connected electrolysis | Q2 | Q |  | BEXTRA44
HT | 30 | 0 | 0 | 0 | T |  | Hydrogen-SMR-4 | P8 | P |  | BEXTRA5
HT | 30 | 0 | 0 | 0 | T |  | Hydrogen-SMR-5 | C4 | C |  | BEXTRA6
HT | 30 | 0 | 0 | 0 | T |  | Hydrogen-SMR-6 | P4 | P |  | BEXTRA7
HT | 30 | 62.5 | 62.5 | 62.5 | T |  | Parkgate (Rail) | L5 | L |  | BEXTRA77
HT | 30 | 62.5 | 62.5 | 62.5 | T |  | Parkgate (Rail) | L5 | L |  | BEXTRA78
HT | 30 | 0 | 0 | 0 | T |  | Hydrogen-SMR-7 | S6 | S |  | BEXTRA8
HT | 30 | 92.4 | 92.4 | 92.4 | T |  | Dingley Wood 400 (N_Rail) | L3 | L |  | BEXTRA83
HT | 30 | 14 | 14 | 14 | T |  | Hasland (New) (N_Rail) | P3 | P |  | BEXTRA84
HT | 30 | 45 | 45 | 45 | T |  | Kegworth (New) (N_Rail) | L7 | L |  | BEXTRA85
HT | 30 | 0 | 0 | 0.048 | T |  | Grid-connected electrolysis | M6 | M |  | BEXTRA87
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | J1 | J |  | BEXTRA88
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | M8 | M |  | BEXTRA89
HT | 30 | 5 | 5 | 5 | T |  | Hydrogen-SMR-8 | S5 | S |  | BEXTRA9
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A7 | A |  | BEXTRA93
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | C7 | C |  | BEXTRA94
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | N3 | N |  | BEXTRA95
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | P3 | P |  | BEXTRA96
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | S6 | S |  | BEXTRA97
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | A7 | A |  | BEXTRA98
HT | 30 | 0 | 0 | 0 | T |  | Grid-connected electrolysis | N3 | N |  | BEXTRA99
HT | 30 | 168.389 | 88.509 | 232.75 | C,D,E,H,I,R,Z | BICF1 | Bicker Fen | K4 | K | BICF11 | BICF1
HT | 30 | 225.4 | 80.848 | 142.906 | C,D,E,H,I,R,Z | BIRK1 | Birkenhead | N3 | N | BIRK11 | BIRK1
HT | 30 | 641.775 | 180.957 | 382.571 | C,D,E,H,I,R,Z | BISW1 | Bishops Wood | L2 | L | BISW11 | BISW1
HT | 30 | 35.213 | 12.4175 | 29.32 | C,D,E,H,I,R,Z | BLYT1 | Blyth 132kV | Q6 | Q | BLYT1A | BLYTH132
HT | 30 | 35.213 | 12.4175 | 29.32 | C,D,E,H,I,R,Z | BLYT1 | Blyth 132kV | Q6 | Q | BLYT1B | BLYTH132
HT | 30 | 153.423 | 32.158 | 90.123 | C,D,E,H,I,R,Z | BLYT6 | Blyth 66kV | Q6 | Q | BLYT61 | BLYTB1
HT | 30 | 27.97 | 9.04 | 14.166 | C,D,E,H,I,R,Z | BOAG3 | Boat of Garten | T1 | T | BOAG3- | BOAGP
HT | 30 | 444.5125 | 141.443 | 250.946 | C,D,E,H,I,R,Z | BOLN1 | Bolney | B1 | B | BOLN11 | BOLN1
HT | 30 | 444.5125 | 141.443 | 250.946 | C,D,E,H,I,R,Z | BOLN1 | Bolney | B1 | B | BOLN12 | BOLN1
HT | 30 | 57.186 | 23.964 | 38.909 | C,D,E,H,I,R,T,Z | BONN1 | Bonnybridge,Bonnybridge (Network Rail) | S5 | S | BONN1- | BONN
HT | 30 | 145.637 | 56.074 | 107.587 | C,D,E,H,I,R,Z | BOTW1 | Botley Wood | B2 | B | BOTW11 | BOTW1
HT | 30 | 222.076 | 90.71 | 130.864 | C,D,E,H,I,R,Z | BRAI1 | Braintree | J8 | J | BRAI11 | BRAI1
HT | 30 | 27.506 | 12.246 | 18.388 | C,D,E,H,I,R,Z | BRAP3 | Braehead Park | S6 | S | BRAP3- | BRAP
HT | 30 | 212.463 | 62.9125 | 140.1235 | C,D,E,H,I,R,Z | BRAW1 | Bradford West | P1 | P | BRAW11 | BRAW1
HT | 30 | 212.463 | 62.9125 | 140.1235 | C,D,E,H,I,R,Z | BRAW1 | Bradford West | P1 | P | BRAW12 | BRAW1
HT | 30 | 45.933 | 11.419 | 17.884 | C,D,E,H,I,R,Z | BRCW3 | Braco West | T4 | T | BRCW3- | BRACP
HT | 30 | 314.109 | 111.059 | 190.266 | C,D,E,H,I,R,Z | BRED1 | Bredbury | N2 | N | BRED11 | BRED1
HT | 30 | 418.533 | 106.5855 | 240.3095 | C,D,E,H,I,R,Z | BRFO1 | Bramford,Clacton | J5 | J | BRFO11 | BRFO1
HT | 30 | 418.533 | 106.5855 | 240.3095 | C,D,E,H,I,R,Z | BRFO1 | Bramford,Clacton | J5 | J | BRFO12 | BRFO1
HT | 30 | 29.723 | 13.617 | 20.222 | C,D,E,H,I,R,Z | BRID3 | Bridge of Dun | T4 | T | BRID3- | BRIDP
HT | 30 | 417.946 | 215.402 | 300.724 | C,D,E,H,I,R,T,Z | BRIM1 | Brimsdown,Brimsdown 132 (Data_centre) | A3 | A | BRIM11 | BRIM1
HT | 30 | 6.2777 | 6.2777 | 6.2777 | T | BRIN1 | BOC Brinsworth Supply | P3 | P | BRIN21 | MTEMP
HT | 30 | 6.2777 | 6.2777 | 6.2777 | T | BRIN1 | BOC Brinsworth Supply | P3 | P | BRIN22 | MTEMP
HT | 30 | 6.2777 | 6.2777 | 6.2777 | T | BRIN1 | BOC Brinsworth Supply | P3 | P | BRIN41 | MTEMP
HT | 30 | 98.2703 | 36.2255 | 57.905 | C,D,E,H,I,R,Z | BRLE1 | Bramley | B4 | B | BRLE11 | BRLE1
HT | 30 | 98.2703 | 36.2255 | 57.905 | C,D,E,H,I,R,Z | BRLE1 | Bramley | B4 | B | BRLE12 | BRLE1
HT | 30 | 98.2703 | 36.2255 | 57.905 | C,D,E,H,I,R,Z | BRLE1 | Bramley | B4 | B | BRLE13 | BRLE1
HT | 30 | 98.2703 | 36.2255 | 57.905 | C,D,E,H,I,R,Z | BRLE1 | Bramley | B4 | B | BRLE14 | BRLE1
HT | 30 | 98.2703 | 36.2255 | 57.905 | C,D,E,H,I,R,Z | BRLE1 | Bramley | B4 | B | BRLE1A | BRLE1
HT | 30 | 98.2703 | 36.2255 | 57.905 | C,D,E,H,I,R,Z | BRLE1 | Bramley | B4 | B | BRLE1B | BRLE1
HT | 30 | 68 | 68 | 68 | T | BRLE4 | Bramley 400 (N_Rail) | B4 | B | BRLE41 | BEXTRA82
HT | 30 | 13.088 | 7.583 | 11.016 | C,D,E,H,I,R,Z | BROA3 | Broadford | T1 | T | BROA3- | BROAP
HT | 30 | 8.667 | 3.718 | 5.505 | C,D,E,H,I,R,Z | BROR3 | Brora | T5 | T | BROR3- | BRORP
HT | 30 | 46.181 | 18.26 | 29.574 | C,D,E,H,I,R,Z | BROX3 | Broxburn | S6 | S | BROX3- | BROX
HT | 30 | 193.34 | 83.519 | 193.129 | C,D,E,H,I,R,Z | BRWA1 | Bridgewater | E7 | E | BRWA11 | BRWA1
HT | 30 | 48.078 | 17.001 | 24.155 | C,D,E,H,I,R,Z | BUMU3 | Burghmuir | T4 | T | BUMU3- | BUMUP
HT | 30 | 334.62 | 114.629 | 256.153 | C,D,E,H,I,R,Z | BURW1 | Burwell Main | J7 | J | BURW11 | BURM1
HT | 30 | 204.298 | 53.486 | 110.818 | C,D,E,H,I,R,Z | BUSH1 | Bushbury | L2 | L | BUSH11 | BUSH1
HT | 30 | 294.528 | 99.483 | 182.324 | C,D,E,H,I,R,Z | BUST1 | Bustleholme | L3 | L | BUST11 | BUST1
HT | 30 | 8.997 | 4.732 | 7.389 | C,D,E,H,I,R,Z | CAAD3 | Carradale | T3 | T | CAAD3- | CAADP
HT | 30 | 8.997 | 4.732 | 7.389 | C,D,E,H,I,R,Z | CAAD3 | Carradale | T3 | T | CAAD3J | CAADP
HT | 30 | 0 | 0 | 0 | C,D,E,H,I,R,Z | CAFA5 | Carsfad | S6 | S | CAFA5R | CAFA
HT | 30 | 118.6085 | 21.2155 | 99.8205 | C,D,E,H,I,R,Z | CANT1 | Canterbury | C7 | C | CANT13 | CANTN1
HT | 30 | 118.6085 | 21.2155 | 99.8205 | C,D,E,H,I,R,Z | CANT1 | Canterbury | C7 | C | CANT14 | CANTN1
HT | 30 | 109.092 | 42.8813 | 60.2277 | C,D,E,H,I,R,Z | CAPE1 | Capenhurst | N3 | N | CAPE11 | CAPEA1
HT | 30 | 109.092 | 42.8813 | 60.2277 | C,D,E,H,I,R,Z | CAPE1 | Capenhurst | N3 | N | CAPE1A | CAPEA1
HT | 30 | 109.092 | 42.8813 | 60.2277 | C,D,E,H,I,R,Z | CAPE1 | Capenhurst | N3 | N | CAPE1B | CAPEA1
HT | 30 | 301.988 | 203.993 | 260.813 | C,D,E,H,I,R,T,Z | CARE1 | Cardiff Airport 132 (Data_centre),Cardiff East | H2 | H | CARE11 | BEXTRA63
HT | 30 | 183.3705 | 66.5675 | 109.4855 | C,D,E,H,I,R,Z | CARR1 | Carrington | N2 | N | CARR11 | CARR1
HT | 30 | 183.3705 | 66.5675 | 109.4855 | C,D,E,H,I,R,Z | CARR1 | Carrington | N2 | N | CARR12 | CARR1
HT | 30 | 2.136 | 0.756 | 1.679 | C,D,E,H,I,R,Z | CASS3 | Cassley | T5 | T | CASS3- | CASSP
HT | 30 | 14.877 | 5.991 | 9.683 | C,D,E,H,I,R,Z | CATY3 | Carntyne | S6 | S | CATY3- | CATY
HT | 30 | 3.386 | 2.106 | 3.078 | C,D,E,H,I,R,Z | CEAN5 | Ceannacroc | T1 | T | CEAN5- | CEANP
HT | 30 | 298.5535 | 102.0675 | 188.1965 | C,D,E,H,I,R,Z | CELL1 | Cellarhead | L5 | L | CELL11 | CELL1
HT | 30 | 298.5535 | 102.0675 | 188.1965 | C,D,E,H,I,R,Z | CELL1 | Cellarhead | L5 | L | CELL12 | CELL1
HT | 30 | 2.559 | 2.559 | 2.559 | T | CHAP1 | Chapelcross Directs,Ecclefechan (Network Rail) | S6 | S | CHAP1- | TCHAPD-1
HT | 30 | 22.8236 | 11.6023 | 17.8344 | C,D,E,H,I,R,Z | CHAP3 | Chapelcross | S6 | S | CHAP3- | CHAP
HT | 30 | 24.533 | 8.326 | 12.059 | C,D,E,H,I,R,Z | CHAR3 | Charleston | T4 | T | CHAR3- | CHARP
HT | 30 | 31.219 | 9.3025 | 14.12 | C,D,E,H,I,R,Z | CHAS3 | Charlotte Street | S6 | S | CHAS3A | CHAS
HT | 30 | 31.219 | 9.3025 | 14.12 | C,D,E,H,I,R,Z | CHAS3 | Charlotte Street | S6 | S | CHAS3C | CHAS
HT | 30 | 97.756 | 29.85 | 65.373 | C,D,E,H,I,R,Z | CHIC1 | Chickerell | E1 | E | CHIC11 | CHIC1
HT | 30 | 83.041 | 27.5103 | 47.311 | C,D,E,H,I,R,Z | CHSI1 | Chessington | A8 | A | CHSI11 | CHSI1
HT | 30 | 83.041 | 27.5103 | 47.311 | C,D,E,H,I,R,Z | CHSI1 | Chessington | A8 | A | CHSI1A | CHSI1
HT | 30 | 83.041 | 27.5103 | 47.311 | C,D,E,H,I,R,Z | CHSI1 | Chessington | A8 | A | CHSI1B | CHSI1
HT | 30 | 290.767 | 97.2525 | 198.9465 | C,D,E,H,I,R,Z | CHTE1 | Chesterfield | P3 | P | CHTE11 | CHTE1
HT | 30 | 290.767 | 97.2525 | 198.9465 | C,D,E,H,I,R,Z | CHTE1 | Chesterfield | P3 | P | CHTE12 | CHTE1
HT | 30 | 330.6125 | 161.6165 | 206.101 | C,D,E,H,I,R,Z | CITR1 | City Road | A7 | A | CITR11 | CITR1
HT | 30 | 330.6125 | 161.6165 | 206.101 | C,D,E,H,I,R,Z | CITR1 | City Road | A7 | A | CITR12 | CITR1
HT | 30 | 4.272 | 0.199 | 0.491 | C,D,E,H,I,R,Z | CLAC5 | Clachan | T3 | T | CLAC5J | CLACP
HT | 30 | 28.385 | 10.722 | 14.959 | C,D,E,H,I,R,Z | CLAY3 | Clayhills | T2 | T | CLAY3- | CLAYP
HT | 30 | 38.402 | 11.638 | 17.582 | C,D,E,H,I,R,Z | CLYM3 | Clyde’s Mill | S6 | S | CLYM3A | CLYM
HT | 30 | 38.402 | 11.638 | 17.582 | C,D,E,H,I,R,Z | CLYM3 | Clyde’s Mill | S6 | S | CLYM3B | CLYM
HT | 30 | 63.58 | 22.226 | 33.84 | C,D,E,H,I,R,Z | COAT3 | Coatbridge | S6 | S | COAT3- | COAT
HT | 30 | 38.863 | 18.436 | 29.218 | C,D,E,H,I,R,Z | COCK3 | Cockenzie | S6 | S | COCK3- | COCK
HT | 30 | 80.517 | 37.8947 | 74.935 | C,D,E,H,I,R,Z | CONQ1 | Connah's Quay | M5 | M | CONQ11 | CONQA1
HT | 30 | 80.517 | 37.8947 | 74.935 | C,D,E,H,I,R,Z | CONQ1 | Connah's Quay | M5 | M | CONQ12 | CONQA1
HT | 30 | 80.517 | 37.8947 | 74.935 | C,D,E,H,I,R,Z | CONQ1 | Connah's Quay | M5 | M | CONQ13 | CONQA1
HT | 30 | 31.707 | 8.797 | 14.713 | C,D,E,H,I,R,Z | COUA3 | Coupar Angus | T4 | T | COUA3- | COUAP
HT | 30 | 252.624 | 74.5025 | 153.4165 | C,D,E,H,I,R,Z | COVE1 | Coventry | L3 | L | COVE11 | COVE1
HT | 30 | 252.624 | 74.5025 | 153.4165 | C,D,E,H,I,R,Z | COVE1 | Coventry | L3 | L | COVE12 | COVE1
HT | 30 | 295.289 | 110.9755 | 188.16 | C,D,E,H,I,R,Z | COWL1 | Cowley | D6 | D | COWL11 | COWL1
HT | 30 | 295.289 | 110.9755 | 188.16 | C,D,E,H,I,R,Z | COWL1 | Cowley | D6 | D | COWL12 | COWL1
HT | 30 | 41.165 | 20.046 | 33.784 | C,D,E,H,I,R,Z | COYL3 | Coylton | S6 | S | COYL3- | COYL
HT | 30 | 25.404 | 15.078 | 22.125 | C,D,E,H,I,R,Z | CRAI3 | Craigiebuckler | T2 | T | CRAI3- | CRAIP
HT | 30 | 269.1595 | 76.181 | 164.791 | C,D,E,H,I,R,Z | CREB1 | Creyke Beck | P8 | P | CREB11 | CREB1
HT | 30 | 269.1595 | 76.181 | 164.791 | C,D,E,H,I,R,Z | CREB1 | Creyke Beck | P8 | P | CREB12 | CREB1
HT | 30 | 22.357 | 8.579 | 13.9725 | C,D,E,H,I,R,Z | CROO3 | Crookston A,Crookston B | S6 | S | CROO3J | GEXTRA10
HT | 30 | 22.357 | 8.579 | 13.9725 | C,D,E,H,I,R,Z | CROO3 | Crookston A,Crookston B | S6 | S | CROO3K | GEXTRA10
HT | 30 | 0 | 0 | 0 | T | CULJ3 | UKAEA Culham Jet | D6 | D | CULJ31 | THYELT002
HT | 30 | 0 | 0 | 0 | T | CULJ3 | UKAEA Culham Jet | D6 | D | CULJ32 | THYELT002
HT | 30 | 0 | 0 | 0 | T | CULJ3 | UKAEA Culham Jet | D6 | D | CULJ33 | THYELT002
HT | 30 | 48.708 | 15.407 | 25.048 | C,D,E,H,I,R,Z | CUMB3 | Cumbernauld | S5 | S | CUMB3- | CUMB
HT | 30 | 49.764 | 20.628 | 35.313 | C,D,E,H,I,R,Z | CUPA3 | Cupar | S5 | S | CUPA3- | CUPA
HT | 30 | 10.297 | 4.36 | 7.38 | C,D,E,H,I,R,Z | CURR5 | Currie | S6 | S | CURR5- | CURR
HT | 30 | 0 | 0 | 0 | C,D,E,H,I,R,Z | DALL3 | Dallas | T1 | T | DALL2- | DALLP
HT | 30 | 27.337 | 12.119 | 18.219 | C,D,E,H,I,R,Z | DALM3 | Dalmarnock | S6 | S | DALM3- | DALM3
HT | 30 | 1.511 | 1.511 | 1.511 | T | DEVM1 | Port Glasgow (Network Rail) | S6 | S | DEVM1- | TPORGD-1
HT | 30 | 26.268 | 9.02 | 13.625 | C,D,E,H,I,R,Z | DEVM3 | Devol Moor | S6 | S | DEVM3- | DEVM
HT | 30 | 53.834 | 28.952 | 44.135 | C,D,E,H,I,R,Z | DEVO3 | Devonside | S5 | S | DEVO3- | DEVO
HT | 30 | 66.927 | 24.434 | 36.21 | C,D,E,H,I,R,Z | DEWP3 | Dewar Place | S6 | S | DEWP3- | DEWP
HT | 30 | 436.695 | 436.695 | 436.695 | T | DIDC4 | Didcot - Foxhall 1,Didcot - Foxhall 2,Didcot A (Data_centre),Didcot B (Data_centre) | D6 | D | DIDC41 | BEXTRA69
HT | 30 | 2.209 | 1.1318 | 1.5695 | C,D,E,H,I,R,Z | DOUN3 | Dounreay | T5 | T | DOUN3- | DOUNP
HT | 30 | 2.209 | 1.1318 | 1.5695 | C,D,E,H,I,R,Z | DOUN3 | Dounreay | T5 | T | DOUN3W | DOUNP
HT | 30 | 2.209 | 1.1318 | 1.5695 | C,D,E,H,I,R,Z | DOUN3 | Dounreay | T5 | T | DOUN3X | DOUNP
HT | 30 | 2.209 | 1.1318 | 1.5695 | C,D,E,H,I,R,Z | DOUN3 | Dounreay | T5 | T | DOUN3Y | DOUNP
HT | 30 | 205.961 | 78.057 | 154.455 | C,D,E,H,I,R,Z | DRAK1 | Drakelow | L2 | L | DRAK11 | DRAK1
HT | 30 | 114.844 | 59.09 | 85.476 | C,D,E,H,I,R,Z | DRAX1 | Drax | P4 | P | DRAX11 | DRAX1
HT | 30 | 15.51 | 8.405 | 12.563 | C,D,E,H,I,R,Z | DRCR3 | Drumcross | S5 | S | DRCR3- | DRCR
HT | 30 | 65.677 | 20.546 | 31.669 | C,D,E,H,I,R,Z | DRUM3 | Drumchapel | S5 | S | DRUM3- | DRUM
HT | 30 | 0.001 | 0 | 0 | C,D,E,H,I,R,Z | DUBE3 | Dunbeath | T5 | T | DUBE3- | DUBEP
HT | 30 | 47.525 | 15.887 | 22.282 | C,D,E,H,I,R,Z | DUDH3 | Dudhope | T4 | T |  | DUDHP
HT | 30 | 7.689 | 3.324 | 5.11 | C,D,E,H,I,R,Z | DUGR3 | Dunvegan | T1 | T | DUGR3- | DUGRP
HT | 30 | 21.5943 | 9.6 | 14.9503 | C,D,E,H,I,R,Z | DUMF3 | Dumfries 11,Dumfries 33,Dumfries ICI | S6 | S | DUMF3A | GEXTRA1
HT | 30 | 21.5943 | 9.6 | 14.9503 | C,D,E,H,I,R,Z | DUMF3 | Dumfries 11,Dumfries 33,Dumfries ICI | S6 | S | DUMF3B | GEXTRA1
HT | 30 | 21.5943 | 9.6 | 14.9503 | C,D,E,H,I,R,Z | DUMF3 | Dumfries 11,Dumfries 33,Dumfries ICI | S6 | S | DUMF3I | GEXTRA1
HT | 30 | 13.891 | 7.5335 | 11.8105 | C,D,E,H,I,R,Z | DUNB3 | Dunbar A,Dunbar B | S6 | S | DUNB3A | DUNBA
HT | 30 | 13.891 | 7.5335 | 11.8105 | C,D,E,H,I,R,Z | DUNB3 | Dunbar A,Dunbar B | S6 | S | DUNB3B | DUNBA
HT | 30 | 29.176 | 11.438 | 18.023 | C,D,E,H,I,R,Z | DUNF3 | Dunfermline | S5 | S | DUNF3- | DUNF
HT | 30 | 20.339 | 8.234 | 11.81 | C,D,E,H,I,R,Z | DUNO3 | Dunoon | S5 | S | DUNO3- | DUNOP
HT | 30 | 36.771 | 15.421 | 22.647 | C,D,E,H,I,R,Z | DYCE3 | Dyce | T2 | T | DYCE3- | DYCEP
HT | 30 | 218.337 | 78.384 | 127.338 | C,D,E,H,I,R,Z | EALI6 | Ealing | A7 | A | EALI61 | EALI6
HT | 30 | 116.8125 | 37.0515 | 148.813 | C,D,E,H,I,R,Z | EASO1 | Eaton Socon | J4 | J | EASO11 | EASO1
HT | 30 | 116.8125 | 37.0515 | 148.813 | C,D,E,H,I,R,Z | EASO1 | Eaton Socon | J4 | J | EASO12 | EASO1
HT | 30 | 0 | 0 | 0 | C,D,E,H,I,R,Z | EAST5 | Earlstoun | S6 | S | EAST5- | EAST
HT | 30 | 11.61 | 2.7525 | 4.784 | C,D,E,H,I,R,Z | ECCL3 | Eccles | S6 | S | ECCL3- | ECCL
HT | 30 | 11.61 | 2.7525 | 4.784 | C,D,E,H,I,R,Z | ECCL3 | Eccles | S6 | S | ECCL3V | ECCL
HT | 30 | 239.0525 | 65.027 | 134.4735 | C,D,E,H,I,R,Z | ECLA1 | East Claydon | D4 | D | ECLA11 | ECLA1
HT | 30 | 239.0525 | 65.027 | 134.4735 | C,D,E,H,I,R,Z | ECLA1 | East Claydon | D4 | D | ECLA12 | ECLA1
HT | 30 | 125 | 125 | 125 | T | ECLA4 | Quainton (new) (Rail) | A6 | A | ECLA41 | BEXTRA76
HT | 30 | 81.904 | 27.53 | 44.01 | C,D,E,H,I,R,Z | EERH3 | Easterhouse | S6 | S | EERH3- | EERH
HT | 30 | 20.417 | 6.287 | 9.4665 | C,D,E,H,I,R,Z | EKIL3 | East Kilbride | S6 | S | EKIL3A | EKIL
HT | 30 | 20.417 | 6.287 | 9.4665 | C,D,E,H,I,R,Z | EKIL3 | East Kilbride | S6 | S | EKIL3B | EKIL
HT | 30 | 10.9375 | 4.5745 | 6.7255 | C,D,E,H,I,R,Z | EKIS3 | East Kilbride South | S6 | S | EKIS3A | EKIS
HT | 30 | 10.9375 | 4.5745 | 6.7255 | C,D,E,H,I,R,Z | EKIS3 | East Kilbride South | S6 | S | EKIS3B | EKIS
HT | 30 | 27.01 | 11.567 | 17.447 | C,D,E,H,I,R,Z | ELDE3 | Elderslie | S6 | S | ELDE3- | ELDE
HT | 30 | 49.944 | 21.793 | 30.603 | C,D,E,H,I,R,Z | ELGI3 | Elgin | T1 | T | ELGI3- | ELGIP
HT | 30 | 170.9435 | 53.6225 | 105.828 | C,D,E,H,I,R,Z | ELLA1 | Elland | P1 | P | ELLA11 | ELLA1
HT | 30 | 170.9435 | 53.6225 | 105.828 | C,D,E,H,I,R,Z | ELLA1 | Elland | P1 | P | ELLA12 | ELLA1
HT | 30 | 232.0877 | 118.1493 | 162.9343 | C,D,E,H,I,R,T,Z | ELST1 | Bushey NR,Elstree,Elstree 132 (Data_centre) | A6 | A | ELST11 | BEXTRA70
HT | 30 | 232.0877 | 118.1493 | 162.9343 | C,D,E,H,I,R,T,Z | ELST1 | Bushey NR,Elstree,Elstree 132 (Data_centre) | A6 | A | ELST12 | BEXTRA70
HT | 30 | 232.0877 | 118.1493 | 162.9343 | C,D,E,H,I,R,T,Z | ELST1 | Bushey NR,Elstree,Elstree 132 (Data_centre) | A6 | A | ELST13 | BEXTRA70
HT | 30 | 5.6355 | 5.6355 | 5.6355 | T | ELST2 | Elstree NR | A6 | A | ELST21 | TELSTR-1
HT | 30 | 5.6355 | 5.6355 | 5.6355 | T | ELST2 | Elstree NR | A6 | A | ELST22 | TELSTR-1
HT | 30 | 2.7355 | 2.7355 | 2.7355 | T | ELVA2 | Elvanfoot (Network Rail) | S6 | S | ELVA2Q | TELVAD-1
HT | 30 | 2.7355 | 2.7355 | 2.7355 | T | ELVA2 | Elvanfoot (Network Rail) | S6 | S | ELVA2R | TELVAD-1
HT | 30 | 526.886 | 172.819 | 310.742 | C,D,E,H,I,R,Z | ENDE1 | Enderby | L8 | L | ENDE11 | ENDE1
HT | 30 | 17.941 | 9.248 | 14.407 | C,D,E,H,I,R,Z | ERSK3 | Erskine | S6 | S | ERSK3- | ERSK
HT | 30 | 317.185 | 106.825 | 214.215 | C,D,E,H,I,R,Z | EXET1 | Exeter | F6 | F | EXET11 | EXET1
HT | 30 | 1.752 | 0.476 | 0.863 | C,D,E,H,I,R,Z | FASN3 | Fasnakyle | T1 | T | FASN3- | FASNP
HT | 30 | 1.051 | 0.4144 | 0.6524 | C,D,E,H,I,R,Z | FAUG3 | Fort Augustus | T1 | T | FAUG3- | FAUGP
HT | 30 | 1.051 | 0.4144 | 0.6524 | C,D,E,H,I,R,Z | FAUG3 | Fort Augustus | T1 | T | FAUG3W | FAUGP
HT | 30 | 1.051 | 0.4144 | 0.6524 | C,D,E,H,I,R,Z | FAUG3 | Fort Augustus | T1 | T | FAUG3X | FAUGP
HT | 30 | 1.051 | 0.4144 | 0.6524 | C,D,E,H,I,R,Z | FAUG3 | Fort Augustus | T1 | T | FAUG3Y | FAUGP
HT | 30 | 1.051 | 0.4144 | 0.6524 | C,D,E,H,I,R,Z | FAUG3 | Fort Augustus | T1 | T | FAUG3Z | FAUGP
HT | 30 | 219.291 | 130.312 | 173.475 | C,D,E,H,I,R,Z | FAWL1 | Fawley | B2 | B | FAWL11 | FAWL1
HT | 30 | 529.773 | 174.983 | 361.955 | C,D,E,H,I,R,Z | FECK6 | Feckenham | L3 | L | FECK61 | FECK6
HT | 30 | 380.165 | 84.363 | 209.462 | C,D,E,H,I,R,Z | FERR6 | Ferrybridge A,Ferrybridge B | P5,P6 | P | FERR61 | FERRA2
HT | 30 | 0 | 0 | 0 | C,D,E,H,I,R,Z | FETT3 | Fetteresso | T2 | T | FETT3S | FETTP
HT | 30 | 21.374 | 7.681 | 12.873 | C,D,E,H,I,R,Z | FIDD3 | Fiddes | T2 | T | FIDD3- | FIDDP
HT | 30 | 181.9995 | 68.8655 | 314.735 | C,D,E,H,I,R,Z | FIDF1 | Fiddlers Ferry | N1 | N | FIDF11 | FIDF1
HT | 30 | 181.9995 | 68.8655 | 314.735 | C,D,E,H,I,R,Z | FIDF1 | Fiddlers Ferry | N1 | N | FIDF12 | FIDF1
HT | 30 | 19.598 | 15.543 | 23.028 | C,D,E,H,I,R,Z | FINN3 | Finnieston | S5 | S | FINN3- | FINN
HT | 30 | 397.886 | 144.471 | 267.0525 | C,D,E,H,I,R,Z | FLEE1 | Fleet | B3 | B | FLEE11 | FLEE1
HT | 30 | 397.886 | 144.471 | 267.0525 | C,D,E,H,I,R,Z | FLEE1 | Fleet | B3 | B | FLEE12 | FLEE1
HT | 30 | 11.6943 | 8.8313 | 7.9613 | C,D,E,H,I,R,Z | FOUR1 | Fourstones | Q8 | Q | FOUR21 | FOUR1
HT | 30 | 11.6943 | 8.8313 | 7.9613 | C,D,E,H,I,R,Z | FOUR1 | Fourstones | Q8 | Q | FOUR31 | FOUR1
HT | 30 | 11.6943 | 8.8313 | 7.9613 | C,D,E,H,I,R,Z | FOUR1 | Fourstones | Q8 | Q | FOUR71 | FOUR1
HT | 30 | 19.486 | 8.007 | 11.268 | C,D,E,H,I,R,Z | FRAS3 | Fraserburgh | T2 | T | FRAS3- | FRASP
HT | 30 | 362.25 | 120.544 | 238.532 | C,D,E,H,I,R,Z | FROD1 | Frodsham | N3 | N | FROD11 | FROD1
HT | 30 | 63.5935 | 63.5935 | 63.5935 | T | FROD2 | Castner Kellner,Frodsham NR | N3 | N | FROD21 | TCASKD-1
HT | 30 | 63.5935 | 63.5935 | 63.5935 | T | FROD2 | Castner Kellner,Frodsham NR | N3 | N | FROD22 | TCASKD-1
HT | 30 | 33.842 | 14.155 | 20.88 | C,D,E,H,I,R,Z | FWIL3 | Fort William | T1 | T | FWIL3- | FWILP
HT | 30 | 32.861 | 13.476 | 21.276 | C,D,E,H,I,R,Z | GALA3 | Galashiels | S6 | S | GALA3- | GALA
HT | 30 | 0 | 0 | 0 | C,D,E,H,I,R,Z |  | Finstown | T5 | T |  | GEXTRA14
HT | 30 | 7.4846 | 2.5844 | 4.677 | C,D,E,H,I,R,Z |  | Lesmahagow | S6 | S |  | GEXTRA15
HT | 30 | 30.8815 | 8.8625 | 14.0455 | C,D,E,H,I,R,Z | GIFF3 | Giffnock | S6 | S | GIFF3A | GIFF
HT | 30 | 30.8815 | 8.8625 | 14.0455 | C,D,E,H,I,R,Z | GIFF3 | Giffnock | S6 | S | GIFF3B | GIFF
HT | 30 | 0 | 0 | 0 | C,D,E,H,I,R,Z | GLFA3 | Glenfarclas | T1 | T | GLFA3- | GLEFP
HT | 30 | 0 | 0 | 0 | C,D,E,H,I,R,Z | GLLE5 | Glenlee | S6 | S | GLLE5- | GLLE
HT | 30 | 17.467 | 9.179 | 14.603 | C,D,E,H,I,R,Z | GLLU3 | Glenluce | S6 | S | GLLU3- | GLLU
HT | 30 | 23.401 | 8.152 | 12.481 | C,D,E,H,I,R,Z | GLNI3 | Glenniston | S5 | S | GLNI3- | GLNI
HT | 30 | 12.3815 | 6.739 | 10.2195 | C,D,E,H,I,R,Z | GLRO3 | Glenrothes | S5 | S | GLRO3A | GLRO
HT | 30 | 12.3815 | 6.739 | 10.2195 | C,D,E,H,I,R,Z | GLRO3 | Glenrothes | S5 | S | GLRO3B | GLRO
HT | 30 | 24.233 | 14.232 | 21.048 | C,D,E,H,I,R,Z | GORG3 | Gorgie | S6 | S | GORG3- | GORG
HT | 30 | 32.812 | 16.961 | 25.615 | C,D,E,H,I,R,Z | GOVA3 | Govan | S6 | S | GOVA3- | GOVA
HT | 30 | 13.1 | 13.1 | 13.1 | T | GRAI4 | Grain LNG Terminal | C3 | C | GRAI41 | TGLNG
HT | 30 | 373.6855 | 95.038 | 231.6785 | C,D,E,H,I,R,Z | GREN1 | Grendon | J6 | J | GREN11 | GREN1
HT | 30 | 373.6855 | 95.038 | 231.6785 | C,D,E,H,I,R,Z | GREN1 | Grendon | J6 | J | GREN12 | GREN1
HT | 30 | 122.9075 | 49.807 | 83.0535 | C,D,E,H,I,R,Z | GRIW1 | Grimsby West | P7 | P | GRIW11 | GRIW1
HT | 30 | 122.9075 | 49.807 | 83.0535 | C,D,E,H,I,R,Z | GRIW1 | Grimsby West | P7 | P | GRIW12 | GRIW1
HT | 30 | 67.375 | 55.388 | 62.022 | C,D,E,H,I,R,T,Z | GRMO3 | Grangemouth A,Grangemouth B (BP),Grangemouth C | S6 | S | GRMO3A | GEXTRA4
HT | 30 | 67.375 | 55.388 | 62.022 | C,D,E,H,I,R,T,Z | GRMO3 | Grangemouth A,Grangemouth B (BP),Grangemouth C | S6 | S | GRMO3C | GEXTRA4
HT | 30 | 7.485 | 7.485 | 7.485 | T | GRTO6 | BS Grangetown Supply | Q2 | Q | GRTO61 | MGRTO
HT | 30 | 19.86 | 4.792 | 8.429 | C,D,E,H,I,R,Z | GRUB3 | Grudie Bridge | T1 | T | GRUB3- | GRUBP
HT | 30 | 313.187 | 102.099 | 181.872 | C,D,E,H,I,R,Z | HACK1 | Hackney 132kV,Hackney 66kV | A1 | A | HACK11 | HACK1
HT | 30 | 31.523 | 11.887 | 18.388 | C,D,E,H,I,R,Z | HAGR3 | Haggs Road | S6 | S | HAGR3- | HAGR
HT | 30 | 463.694 | 98.771 | 275.35 | C,D,E,H,I,R,Z | HARG1 | Harker | Q8 | Q | HARG11 | HARK1
HT | 30 | 21.537 | 92.135 | 105.539 | C,D,E,H,I,R,T,Z | HARK1 | Harker NR,Robin Rigg | Q8 | Q | HARK13 | RRIG
HT | 30 | 123.267 | 43.652 | 78.296 | C,D,E,H,I,R,Z | HARM6 | Hart Moor | Q4 | Q | HARM61 | HARM6
HT | 30 | 19.277 | 11.67 | 18.12 | C,D,E,H,I,R,Z | HAWI3 | Hawick | S6 | S | HAWI3- | HAWI
HT | 30 | 94.163 | 32.069 | 71.021 | C,D,E,H,I,R,Z | HAWP6 | Hawthorn Pit | Q4 | Q | HAWP61 | HAWP6
HT | 30 | 13.963 | 6.395 | 9.561 | C,D,E,H,I,R,Z | HELE3 | Helensburgh | S5 | S | HELE3- | HELE
HT | 30 | 134.395 | 165.823 | 156.903 | C,D,E,H,I,R,Z | HEYS1 | Heysham (Barrow WF),Heysham (NGET),Ormonde | R5 | R | HEYS11 | HEYS1
HT | 30 | 0 | 0 | 0 | T | HINP2 | HPC construction supply | E7 | E | HINP21 | THPC-CES
HT | 30 | 0 | 0 | 0 | T | HINP2 | HPC construction supply | E7 | E | HINP22 | THPC-CES
HT | 30 | 3.46 | 2.067 | 3.039 | C,D,E,H,I,R,Z | HUNF3 | Hunterston Farm | S6 | S | HUNF3- | HUER
HT | 30 | 87.4057 | 27.5173 | 50.7867 | C,D,E,H,I,R,Z | HURS1 | Hurst | A8 | A | HURS1B | HURS1
HT | 30 | 87.4057 | 27.5173 | 50.7867 | C,D,E,H,I,R,Z | HURS1 | Hurst | A8 | A | HURS1C | HURS1
HT | 30 | 87.4057 | 27.5173 | 50.7867 | C,D,E,H,I,R,Z | HURS1 | Hurst | A8 | A | HURS1D | HURS1
HT | 30 | 203.734 | 31.796 | 73.121 | C,D,E,H,I,R,T,Z | HUTT1 | Hutton,Oxenholme NR | R6 | R | HUTT11 | HUTT1
HT | 30 | 24.971 | 23.265 | 24.244 | C,D,E,H,I,R,Z | IMPP3 | Imperial Park | H6 | H | IMPP31 | IMPK1
HT | 30 | 0 | 0 | 0 | T | IMPP4 | Imperial Park 1,Imperial Park 2 | H6 | H | IMPP41 | TIMPRK-1
HT | 30 | 516.171 | 146.823 | 320.77 | C,D,E,H,I,R,Z | INDQ1 | Indian Queens | F6 | F | INDQ11 | INDQ1
HT | 30 | 39.544 | 16.169 | 24.064 | C,D,E,H,I,R,Z | INKE3 | Inverkeithing | S5 | S | INKE3- | INKE
HT | 30 | 70.72 | 19.696 | 27.53 | C,D,E,H,I,R,Z | INNE3 | Inverness | T1 | T | INNE3- | INNEP
HT | 30 | 1.7265 | 1.7265 | 1.7265 | T | INWI1 | Innerwick (Network Rail) | S6 | S | INWI1Q | TINWID-1
HT | 30 | 1.7265 | 1.7265 | 1.7265 | T | INWI1 | Innerwick (Network Rail) | S6 | S | INWI1R | TINWID-1
HT | 30 | 247.339 | 73.994 | 150.9873 | C,D,E,H,I,R,Z | IROA1 | Camblesforth,Iron Acton | G5,P4 | G,P | IROA11 | CAMB01
HT | 30 | 247.339 | 73.994 | 150.9873 | C,D,E,H,I,R,Z | IROA1 | Camblesforth,Iron Acton | G5,P4 | G,P | IROA12 | CAMB01
HT | 30 | 247.339 | 73.994 | 150.9873 | C,D,E,H,I,R,Z | IROA1 | Camblesforth,Iron Acton | G5,P4 | G,P | IROA13 | CAMB01
HT | 30 | 76.3847 | 20.7503 | 34.975 | C,D,E,H,I,R,Z | IRON1 | Ironbridge | L5 | L | IRON11 | IRONB1
HT | 30 | 76.3847 | 20.7503 | 34.975 | C,D,E,H,I,R,Z | IRON1 | Ironbridge | L5 | L | IRON12 | IRONB1
HT | 30 | 76.3847 | 20.7503 | 34.975 | C,D,E,H,I,R,Z | IRON1 | Ironbridge | L5 | L | IRON13 | IRONB1
HT | 30 | 140.738 | 50.245 | 81.086 | C,D,E,H,I,R,Z | ISLI1 | Islington | A7 | A | ISLI11 | ISLI1
HT | 30 | 882.46 | 628.396 | 740.925 | C,D,E,H,I,R,T,Z | IVER1 | Iver 132kV,Iver 66kV,Iver B 132 (Data_centre) | A6 | A | IVER11 | BEXTRA65
HT | 30 | 40.466 | 15.29 | 27.024 | C,D,E,H,I,R,Z | JOHN3 | Johnstone | S6 | S | JOHN3- | JOHN
HT | 30 | 45.553 | 12.841 | 26.41 | C,D,E,H,I,R,Z | JORD3 | Jordanthorpe | P3 | P | JORD31 | JORD3
HT | 30 | 20.0063 | 13.4693 | 20.6953 | C,D,E,H,I,R,Z | KAIM3 | Kaimes | S6 | S | KAIM3- | KAIM
HT | 30 | 20.0063 | 13.4693 | 20.6953 | C,D,E,H,I,R,Z | KAIM3 | Kaimes | S6 | S | KAIM3A | KAIM
HT | 30 | 20.0063 | 13.4693 | 20.6953 | C,D,E,H,I,R,Z | KAIM3 | Kaimes | S6 | S | KAIM3B | KAIM
HT | 30 | 320.357 | 140.645 | 302.523 | C,D,E,H,I,R,Z | KEAD1 | Keadby | P8 | P | KEAD11 | KEAD1
HT | 30 | 644.992 | 215.271 | 381.604 | C,D,E,H,I,R,Z | KEAR1 | Kearsley 132kV,Kearsley 33kV | N4 | N | KEAR11 | KEAR1
HT | 30 | 19.6501 | 8.4303 | 12.4888 | C,D,E,H,I,R,Z | KEIT3 | Keith | T1 | T | KEIT3- | KEITP
HT | 30 | 19.6501 | 8.4303 | 12.4888 | C,D,E,H,I,R,Z | KEIT3 | Keith | T1 | T | KEIT3A | KEITP
HT | 30 | 130.218 | 5.835 | 91.784 | C,D,E,H,I,R,Z | KEMS1 | Kemsley | C3 | C | KEMS11 | KEMS1
HT | 30 | 0 | 0 | 0 | T | KENG4 | Kensal Green Crossrail | A7 | A | KENG41 | TKSGND-1
HT | 30 | 0 | 0 | 0 | C,D,E,H,I,R,Z | KEOO5 | Kendoon | S6 | S | KEOO5- | KEOO
HT | 30 | 262.242 | 60.402 | 156.268 | C,D,E,H,I,R,Z | KIBY1 | Kirkby (_D),Kirkby (_G) | N1 | N | KIBY11 | KIBY1
HT | 30 | 81.22 | 20.816 | 32.701 | C,D,E,H,I,R,Z | KIER3 | Killermont | S5 | S | KIER3- | KIER
HT | 30 | 7.764 | 2.12 | 4.661 | C,D,E,H,I,R,Z | KIIN3 | Killin | T4 | T | KIIN3- | KIINP
HT | 30 | 23.7 | 10.925 | 16.511 | C,D,E,H,I,R,Z | KILB3 | Kilbowie 11,Kilbowie 33 | S5 | S | KILB3- | GEXTRA6
HT | 30 | 2.903 | 2.377 | 3.378 | C,D,E,H,I,R,Z | KILO3 | Kinlochleven | T1 | T | KILO3- | KINLP
HT | 30 | 10.0877 | 4.2253 | 6.3923 | C,D,E,H,I,R,Z | KILS3 | Kilmarnock South | S6 | S | KILS3- | KILS
HT | 30 | 10.0877 | 4.2253 | 6.3923 | C,D,E,H,I,R,Z | KILS3 | Kilmarnock South | S6 | S | KILS3U | KILS
HT | 30 | 10.0877 | 4.2253 | 6.3923 | C,D,E,H,I,R,Z | KILS3 | Kilmarnock South | S6 | S | KILS3X | KILS
HT | 30 | 63.155 | 27.049 | 40.765 | C,D,E,H,I,R,Z | KILT3 | Kilmarnock Town | S6 | S | KILT3A | KILT
HT | 30 | 30.968 | 15.57 | 22.894 | C,D,E,H,I,R,Z | KILW3 | Kilwinning | S6 | S | KILW3- | KILW
HT | 30 | 220.897 | 79.883 | 133.392 | C,D,E,H,I,R,Z | KINO1 | Kingsnorth | C2 | C | KINO11 | KINO1
HT | 30 | 20.6329 | 6.6114 | 9.5343 | C,D,E,H,I,R,Z | KINT3 | Kintore | T2 | T | KINT3- | KINTP
HT | 30 | 20.6329 | 6.6114 | 9.5343 | C,D,E,H,I,R,Z | KINT3 | Kintore | T2 | T | KINT3W | KINTP
HT | 30 | 20.6329 | 6.6114 | 9.5343 | C,D,E,H,I,R,Z | KINT3 | Kintore | T2 | T | KINT3Y | KINTP
HT | 30 | 240.414 | 85.1 | 141.082 | C,D,E,H,I,R,Z | KIRK1 | Kirkstall B | P1 | P | KIRK11 | KIRKB1
HT | 30 | 331.884 | 112.738 | 201.045 | C,D,E,H,I,R,Z | KITW1 | Kitwell | L2 | L | KITW11 | KITW1
HT | 30 | 176.147 | 47.409 | 100.643 | C,D,E,H,I,R,Z | KNAR1 | Knaresborough | P2 | P | KNAR11 | KNAR
HT | 30 | 166.942 | 63.709 | 139.049 | C,D,E,H,I,R,Z | LACK6 | Lackenby | Q2 | Q | LACK61 | LACK6
HT | 30 | 2.2 | 0.861 | 1.699 | C,D,E,H,I,R,Z | LAIR3 | Lairg | T5 | T | LAIR3- | LAIRP
HT | 30 | 258.916 | 111.841 | 167.707 | C,D,E,H,I,R,Z | LALE1 | Laleham | A6 | A | LALE11 | LALE1SG003
HT | 30 | 28 | 28 | 28 | T | LALE2 | Laleham 275 (N_Rail) | A6 | A | LALE21 | BEXTRA86
HT | 30 | 385.049 | 111.33 | 217.73 | C,D,E,H,I,R,Z | LAND1 | Landulph | F6 | F | LAND11 | LAND1
HT | 30 | 327.131 | 96.991 | 237.263 | C,D,E,H,I,R,Z | LEGA1 | Legacy | M4 | M | LEGA11 | LEGA1
HT | 30 | 15.7475 | 15.7475 | 15.7475 | T | LEIB4 | LEIGHTON BUZZARD NR | D4 | D | LEIB4A | TLBUZRTK
HT | 30 | 15.7475 | 15.7475 | 15.7475 | T | LEIB4 | LEIGHTON BUZZARD NR | D4 | D | LEIB4B | TLBUZRTK
HT | 30 | 385.09 | 130.253 | 246.091 | C,D,E,H,I,R,Z | LEMR1 | Hams Hall | L3 | L | LEMR11 | HAMHC1
HT | 30 | 38.867 | 15.167 | 23.902 | C,D,E,H,I,R,Z | LEVE3 | Leven | S5 | S | LEVE3- | LEVE
HT | 30 | 64.61 | 22.083 | 37.293 | C,D,E,H,I,R,Z | LING3 | Livingston East | S6 | S | LING3- | LING
HT | 30 | 50.0894 | 17.2956 | 31.3 | C,D,E,H,I,R,Z | LINM3 | Linnmill | S6 | S | LINM3- | LINM
HT | 30 | 363.156 | 128.994 | 223.477 | C,D,E,H,I,R,Z | LISD1 | Lister Drive | N1 | N | LISD11 | LISD1
HT | 30 | 183.343 | 54.535 | 94.955 | C,D,E,H,I,R,Z | LITT1 | Littlebrook (_C),Littlebrook (_J) | A8 | A | LITT11 | LITTC
HT | 30 | 158.4785 | 61.8465 | 94.858 | C,D,E,H,I,R,Z | LODR6 | Lodge Road | A7 | A | LODR61 | LODR6
HT | 30 | 158.4785 | 61.8465 | 94.858 | C,D,E,H,I,R,Z | LODR6 | Lodge Road | A7 | A | LODR62 | LODR6
HT | 30 | 272.5185 | 99.1445 | 188.9715 | C,D,E,H,I,R,Z | LOVE1 | Lovedean | B2 | B | LOVE11 | LOVE1
HT | 30 | 272.5185 | 99.1445 | 188.9715 | C,D,E,H,I,R,Z | LOVE1 | Lovedean | B2 | B | LOVE12 | LOVE1
HT | 30 | 41.036 | 14.024 | 21.569 | C,D,E,H,I,R,Z | LUNA3 | Lunanhead | T4 | T | LUNA3- | LUNAP
HT | 30 | 25.631 | 8.175 | 11.957 | C,D,E,H,I,R,Z | LYND3 | Lyndhurst | T4 | T | LYND3- | LYNDP
HT | 30 | 117.746 | 29.515 | 55.994 | C,D,E,H,I,R,Z | MACC3 | Macclesfield | N6 | N | MACC31 | MACC3
HT | 30 | 21.722 | 8.946 | 12.713 | C,D,E,H,I,R,Z | MACD3 | Macduff | T1 | T | MACD3- | MACDP
HT | 30 | 62.401 | 56.312 | 164.735 | C,D,E,H,I,R,Z | MAGA6 | Margam | H1 | H | MAGA21 | MAGA6
HT | 30 | 711.165 | 229.409 | 449.074 | C,D,E,H,I,R,Z | MANN1 | Mannington | E1 | E | MANN11 | MANN1
HT | 30 | 19.138 | 9.976 | 17.488 | C,D,E,H,I,R,Z | MAYB3 | Maybole | S6 | S | MAYB3- | MAYB
HT | 30 | 675.937 | 172.958 | 448.536 | C,D,E,H,I,R,Z | MELK1 | Melksham | G6 | G | MELK11 | MELK1
HT | 30 | 0 | 0 | 0 | T | MELK4 | Thingley Junction 1,Thingley Junction 2 | G6 | G | MELK41 | TTHNJD-1
HT | 30 | 49.771 | 17.174 | 25.273 | C,D,E,H,I,R,Z | MILC3 | Milton of Craigie | T4 | T | MILC3- | MILCP
HT | 30 | 99.617 | 37.772 | 62.0595 | C,D,E,H,I,R,Z | MILH1 | Mill Hill | A6 | A | MILH11 | MILH1
HT | 30 | 99.617 | 37.772 | 62.0595 | C,D,E,H,I,R,Z | MILH1 | Mill Hill | A6 | A | MILH12 | MILH1
HT | 30 | 194.035 | 50.964 | 133.576 | C,D,E,H,I,R,Z | MITY1 | Minety | G6 | G | MITY11 | MITY1
HT | 30 | 194.035 | 50.964 | 133.576 | C,D,E,H,I,R,Z | MITY1 | Minety | G6 | G | MITY12 | MITY1
HT | 30 | 8.2637 | 4.2008 | 6.4573 | C,D,E,H,I,R,Z | MOFF1 | Moffat | S6 | S | MOFF1- | GEXTRA16
HT | 30 | 8.2637 | 4.2008 | 6.4573 | C,D,E,H,I,R,Z | MOFF1 | Moffat | S6 | S | MOFF1A | GEXTRA16
HT | 30 | 16.6745 | 16.6745 | 16.6745 | T | MOSM1 | Mossmoran Exxon,Mossmorran Shell | S5 | S | MOSM1A | TEXMOSSD-1
HT | 30 | 16.6745 | 16.6745 | 16.6745 | T | MOSM1 | Mossmoran Exxon,Mossmorran Shell | S5 | S | MOSM1B | TEXMOSSD-1
HT | 30 | 2.5417 | 0.63625 | 1.1755 | C,D,E,H,I,R,Z | MYBS3 | Mybster | T5 | T | MYBS3J | MYBSP
HT | 30 | 2.5417 | 0.63625 | 1.1755 | C,D,E,H,I,R,Z | MYBS3 | Mybster | T5 | T | MYBS3K | MYBSP
HT | 30 | 2.5417 | 0.63625 | 1.1755 | C,D,E,H,I,R,Z | MYBS3 | Mybster | T5 | T | MYBS3M | MYBSP
HT | 30 | 2.5417 | 0.63625 | 1.1755 | C,D,E,H,I,R,Z | MYBS3 | Mybster | T5 | T | MYBS3N | MYBSP
HT | 30 | 35.507 | 17.365 | 25.226 | C,D,E,H,I,R,Z | NAIR3 | Nairn | T1 | T | NAIR3- | NAIRP
HT | 30 | 90.844 | 33.306 | 54.792 | C,D,E,H,I,R,Z | NEAR3 | Newarthill | S6 | S | NEAR3- | NEAR
HT | 30 | 203.3915 | 66.087 | 116.3165 | C,D,E,H,I,R,Z | NECH1 | Nechells | L3 | L | NECH11 | NECE1
HT | 30 | 203.3915 | 66.087 | 116.3165 | C,D,E,H,I,R,Z | NECH1 | Nechells | L3 | L | NECH12 | NECE1
HT | 30 | 80.435 | 25.04 | 46.672 | C,D,E,H,I,R,Z | NEEP3 | Neepsend | P3 | P | NEEP31 | NEEP3
HT | 30 | 11.125 | 2.016 | 4.473 | C,D,E,H,I,R,Z | NETS3 | Newton Stewart | S6 | S | NETS3- | NETS
HT | 30 | 0 | 0 | 0 | T | NEWX2 | New Cross 1,New Cross 2 | A4 | A | NEWX21 | TNWCRS-1
HT | 30 | 203.001 | 66.051 | 112.392 | C,D,E,H,I,R,Z | NEWX6 | New Cross | A4 | A | NEWX61 | NEWX6
HT | 30 | 203.001 | 66.051 | 112.392 | C,D,E,H,I,R,Z | NEWX6 | New Cross | A4 | A | NEWX62 | NEWX6
HT | 30 | 237.868 | 71.7565 | 133.132 | C,D,E,H,I,R,Z | NFLE1 | Northfleet East | C2 | C | NFLE11 | NFLE
HT | 30 | 237.868 | 71.7565 | 133.132 | C,D,E,H,I,R,Z | NFLE1 | Northfleet East | C2 | C | NFLE12 | NFLE
HT | 30 | 305.035 | 216.791 | 245.327 | C,D,E,H,I,R,T,Z | NHYD6 | North Hyde,North Hyde 66 (Data_centre) | A6 | A | NHYD61 | BEXTRA67
HT | 30 | 237.8595 | 67.236 | 151.1325 | C,D,E,H,I,R,Z | NINF1 | Ninfield | B1 | B | NINF11 | NINF1
HT | 30 | 237.8595 | 67.236 | 151.1325 | C,D,E,H,I,R,Z | NINF1 | Ninfield | B1 | B | NINF12 | NINF1
HT | 30 | 59.131 | 16.293 | 30.34 | C,D,E,H,I,R,Z | NORL3 | Norton Lees | P3 | P | NORL31 | NORL3
HT | 30 | 163.881 | 96.5232 | 112.9633 | C,D,E,H,I,R,Z | NORM1 | Norwich Main,Sheringham Shoal | J3 | J | NORM11 | NORM1
HT | 30 | 163.881 | 96.5232 | 112.9633 | C,D,E,H,I,R,Z | NORM1 | Norwich Main,Sheringham Shoal | J3 | J | NORM12 | NORM1
HT | 30 | 163.881 | 96.5232 | 112.9633 | C,D,E,H,I,R,Z | NORM1 | Norwich Main,Sheringham Shoal | J3 | J | NORM1A | NORM1
HT | 30 | 163.881 | 96.5232 | 112.9633 | C,D,E,H,I,R,Z | NORM1 | Norwich Main,Sheringham Shoal | J3 | J | NORM1B | NORM1
HT | 30 | 470.27 | 131.847 | 284.188 | C,D,E,H,I,R,Z | NORT1 | Norton | Q4 | Q | NORT11 | NORT1
HT | 30 | 377.139 | 125.351 | 230.958 | C,D,E,H,I,R,Z | NURS1 | Nursling | B2 | B | NURS11 | NURS1
HT | 30 | 128.986 | 45.647 | 72.515 | C,D,E,H,I,R,Z | OCKH1 | Ocker Hill | L2 | L | OCKH11 | OCKH1
HT | 30 | 25.14 | 8.573 | 15.3475 | C,D,E,H,I,R,Z | OFFE3 | Offerton | Q4 | Q | OFFE31 | OFFE3
HT | 30 | 25.14 | 8.573 | 15.3475 | C,D,E,H,I,R,Z | OFFE3 | Offerton | Q4 | Q | OFFE32 | OFFE3
HT | 30 | 111.911 | 33.701 | 60.734 | C,D,E,H,I,R,Z | OLDB1 | Oldbury | L2 | L | OLDB11 | OLDB1
HT | 30 | 0 | 0 | 0 | C,D,E,H,I,R,Z | ORRI1 | Orrin | T1 | T | ORRI1Q | ORRIP
HT | 30 | 0 | 0 | 0 | C,D,E,H,I,R,Z | ORRI1 | Orrin | T1 | T | ORRI1R | ORRIP
HT | 30 | 0 | 0 | 0 | C,D,E,H,I,R,Z | ORRI1 | Orrin | T1 | T | ORRI1S | ORRIP
HT | 30 | 0 | 0 | 0 | C,D,E,H,I,R,Z | ORRI1 | Orrin | T1 | T | ORRI1T | ORRIP
HT | 30 | 308.607 | 102.642 | 201.597 | C,D,E,H,I,R,Z | OSBA1 | Osbaldwick | P6 | P | OSBA11 | OSBA1
HT | 30 | 242.649 | 89.826 | 161.348 | C,D,E,H,I,R,Z | PADI1 | Padiham | N5 | N | PADI11 | PADIB1
HT | 30 | 5.0925 | 5.0925 | 5.0925 | T | PAFB4 | Patford Bridge NR | L3 | L | PAFB4A | TPATBRTK
HT | 30 | 5.0925 | 5.0925 | 5.0925 | T | PAFB4 | Patford Bridge NR | L3 | L | PAFB4B | TPATBRTK
HT | 30 | 26.799 | 10.896 | 16.387 | C,D,E,H,I,R,Z | PAIS3 | Paisley | S6 | S | PAIS3- | PAIS
HT | 30 | 17.951 | 13.21 | 20.044 | C,D,E,H,I,R,Z | PART3 | Partick | S5 | S | PART3- | PART
HT | 30 | 24.35 | 8.568 | 11.936 | C,D,E,H,I,R,Z | PEHG3 | Peterhead Grange | T2 | T | PEHG3- | PEHGP
HT | 30 | 8.617 | 4.158 | 6.536 | C,D,E,H,I,R,Z | PEHS5 | Peterhead Shell | T2 | T | PEHS5- | PEHSP
HT | 30 | 160.769 | 39.1595 | 102.504 | C,D,E,H,I,R,Z | PELH1 | Pelham | D5 | D | PELH11 | PELH1
HT | 30 | 160.769 | 39.1595 | 102.504 | C,D,E,H,I,R,Z | PELH1 | Pelham | D5 | D | PELH12 | PELH1
HT | 30 | 157.307 | 75.832 | 129.193 | C,D,E,H,I,R,Z | PEMB1 | Pembroke | H6 | H | PEMB11 | PEMB1
HT | 30 | 352.455 | 146.126 | 223.638 | C,D,E,H,I,R,Z | PENE1 | Penwortham East | R4 | R | PENE11 | PENE1
HT | 30 | 271.21 | 87.418 | 162.869 | C,D,E,H,I,R,Z | PENN1 | Penn | L1 | L | PENN11 | PENN1
HT | 30 | 120.333 | 3.748 | 66.477 | C,D,E,H,I,R,Z | PENT1 | Pentir | M6 | M | PENT11 | PENT1
HT | 30 | 307.476 | 37.415 | 151.093 | C,D,E,H,I,R,Z | PENW1 | Penwortham West | R4 | R | PENW11 | PENW1
HT | 30 | 44.211 | 15.068 | 22.345 | C,D,E,H,I,R,Z | PERS3 | Persley | T2 | T | PERS3- | PERSP
HT | 30 | 23.8585 | 9.83 | 15.12 | C,D,E,H,I,R,Z | PITS3 | Pitsmoor | P3 | P | PITS31 | PITS3
HT | 30 | 23.8585 | 9.83 | 15.12 | C,D,E,H,I,R,Z | PITS3 | Pitsmoor | P3 | P | PITS32 | PITS3
HT | 30 | 95.138 | 35.948 | 52.244 | C,D,E,H,I,R,T,Z | POOB3 | Portobello,Portobello (Network Rail) | S6 | S | POOB3- | POOB
HT | 30 | 51.211 | 20.683 | 35.61 | C,D,E,H,I,R,T,Z | POPP3 | Poppleton,Poppleton NR | P2 | P | POPP31 | POPP3
HT | 30 | 11.4905 | 5.6875 | 8.439 | C,D,E,H,I,R,Z | PORA3 | Port Ann | T3 | T | PORA1S | PORAP
HT | 30 | 11.4905 | 5.6875 | 8.439 | C,D,E,H,I,R,Z | PORA3 | Port Ann | T3 | T | PORA1U | PORAP
HT | 30 | 29.571 | 13.517 | 20.934 | C,D,E,H,I,R,Z | PORD3 | Port Dundas | S5 | S | PORD3- | PORD
HT | 30 | 0 | 0 | 0 | T | PUDM4 | Pudding Mill Lane 1,Pudding Mill Lane 2 | A1 | A | PUDM41 | TPUDMD-1
HT | 30 | 107.235 | 32.304 | 99.111 | C,D,E,H,I,R,Z | PYLE1 | Pyle | H1 | H | PYLE11 | PYLE1
HT | 30 | 0.511 | 0.033 | 0.181 | C,D,E,H,I,R,Z | QUOI5 | Quoich | T1 | T | QUOI5- | QUOIP
HT | 30 | 173.355 | 69.5725 | 112.8855 | C,D,E,H,I,R,Z | RAIN1 | Rainhill | N1 | N | RAIN11 | RAIN1
HT | 30 | 173.355 | 69.5725 | 112.8855 | C,D,E,H,I,R,Z | RAIN1 | Rainhill | N1 | N | RAIN12 | RAIN1
HT | 30 | 4.505 | 1.088 | 2.69 | C,D,E,H,I,R,Z | RANN3 | Rannoch | T4 | T | RANN3Q | RANNP
HT | 30 | 248.509 | 82.757 | 175.786 | C,D,E,H,I,R,Z | RASS1 | Rassau | H6 | H | RASS11 | RASS1
HT | 30 | 241.315 | 85.576 | 151.3445 | C,D,E,H,I,R,Z | RATS1 | Ratcliffe | L7 | L | RATS11 | RATS1
HT | 30 | 241.315 | 85.576 | 151.3445 | C,D,E,H,I,R,Z | RATS1 | Ratcliffe | L7 | L | RATS12 | RATS1
HT | 30 | 1.3985 | 0.303 | 0.7935 | C,D,E,H,I,R,Z | RAVE3 | Ravenscraig | S6 | S | RAVE3S | RAVE
HT | 30 | 1.3985 | 0.303 | 0.7935 | C,D,E,H,I,R,Z | RAVE3 | Ravenscraig | S6 | S | RAVE3T | RAVE
HT | 30 | 587.603 | 126.072 | 318.76 | C,D,E,H,I,R,Z | RAYL1 | Rayleigh | C5 | C | RAYL41 | RAYL1
HT | 30 | 63.596 | 20.568 | 37.359 | C,D,E,H,I,R,Z | REBR3 | Redbridge | A1 | A | REBR31 | REBR3
HT | 30 | 63.596 | 20.568 | 37.359 | C,D,E,H,I,R,Z | REBR3 | Redbridge | A1 | A | REBR32 | REBR3
HT | 30 | 27.325 | 33.007 | 48.951 | C,D,E,H,I,R,Z | REDH3 | Redhouse | S5 | S | REDH3- | REDH
HT | 30 | 44.632 | 22.314 | 31.508 | C,D,E,H,I,R,Z | REDM3 | Redmoss | T2 | T | REDM3- | REDMP
HT | 30 | 31.388 | 25.743 | 54.191 | C,D,E,H,I,R,Z | RICH1 | Richborough | C7 | C | RICH11 | RICHJ
HT | 30 | 116.3235 | 19.9655 | 67.528 | C,D,E,H,I,R,Z | ROCH1 | Rochdale | N4 | N | ROCH11 | ROCH1
HT | 30 | 116.3235 | 19.9655 | 67.528 | C,D,E,H,I,R,Z | ROCH1 | Rochdale | N4 | N | ROCH12 | ROCH1
HT | 30 | 24.52 | 9.6341 | 14.1694 | C,D,E,H,I,R,Z | ROTI3 | Rothienorman | T2 | T | ROTI3- | ROTI3
HT | 30 | 219.718 | 77.52 | 131.017 | C,D,E,H,I,R,T,Z | RUGE1 | Brereton NR,Rugeley | L5 | L | RUGE11 | RUGEB1
HT | 30 | 133.3123 | 61.973 | 83.6813 | C,D,E,H,I,R,Z | RYEH1 | Rye House | A9 | A | RYEH11 | RYEH1
HT | 30 | 133.3123 | 61.973 | 83.6813 | C,D,E,H,I,R,Z | RYEH1 | Rye House | A9 | A | RYEH12 | RYEH1
HT | 30 | 133.3123 | 61.973 | 83.6813 | C,D,E,H,I,R,Z | RYEH1 | Rye House | A9 | A | RYEH13 | RYEH1
HT | 30 | 0.913 | 0.913 | 0.913 | T | RYHA4 | Essendine 1,Essendine 2 | J7 | J | RYHA4A | TRYHAD-1
HT | 30 | 0.913 | 0.913 | 0.913 | T | RYHA4 | Essendine 1,Essendine 2 | J7 | J | RYHA4B | TRYHAD-1
HT | 30 | 25.4595 | 12.409 | 17.9355 | C,D,E,H,I,R,T,Z | SACO3 | Saltcoats / South Beach (Network Rail),Saltcoats A,Saltcoats B | S6 | S | SACO3J | GEXTRA8
HT | 30 | 25.4595 | 12.409 | 17.9355 | C,D,E,H,I,R,T,Z | SACO3 | Saltcoats / South Beach (Network Rail),Saltcoats A,Saltcoats B | S6 | S | SACO3K | GEXTRA8
HT | 30 | 77.115 | 47.361 | 70.629 | C,D,E,H,I,R,Z | SAEN1 | Saltend North | P8 | P | SAEN11 | SALT1
HT | 30 | 112.869 | 37.924 | 25.999 | C,D,E,H,I,R,Z | SAFO1 | Sandford | G7 | G | SAFO11 | SAFO1
HT | 30 | 222.078 | 112.003 | 125.917 | C,D,E,H,I,R,Z | SALH1 | Saltholme | Q2 | Q | SALH11 | SALH1
HT | 30 | 34.414 | 14.85 | 22.131 | C,D,E,H,I,R,Z | SANX3 | St Andrews Cross | S6 | S | SANX3- | SANX
HT | 30 | 29.149 | 9.085 | 19.95 | C,D,E,H,I,R,Z | SASA3 | St. Asaph | M6 | M | SASA11 | SASA
HT | 30 | 311.572 | 87.326 | 174.201 | C,D,E,H,I,R,Z | SEAB1 | Seabank | G7 | G | SEAB11 | SEAB1
HT | 30 | 49.8277 | 18.1937 | 37.7483 | C,D,E,H,I,R,Z | SELL1 | Sellindge | C4 | C | SELL11 | SELL1
HT | 30 | 49.8277 | 18.1937 | 37.7483 | C,D,E,H,I,R,Z | SELL1 | Sellindge | C4 | C | SELL12 | SELL1
HT | 30 | 49.8277 | 18.1937 | 37.7483 | C,D,E,H,I,R,Z | SELL1 | Sellindge | C4 | C | SELL13 | SELL1
HT | 30 | 2.9592 | 2.9592 | 2.9592 | T | SELL4 | Sellindge NR | C4 | C | SELL4A | TSELL-1
HT | 30 | 2.9592 | 2.9592 | 2.9592 | T | SELL4 | Sellindge NR | C4 | C | SELL4B | TSELL-1
HT | 30 | 2.9592 | 2.9592 | 2.9592 | T | SELL4 | Sellindge NR | C4 | C | SELL4C | TSELL-1
HT | 30 | 2.9592 | 2.9592 | 2.9592 | T | SELL4 | Sellindge NR | C4 | C | SELL4D | TSELL-1
HT | 30 | 2.9592 | 2.9592 | 2.9592 | T | SELL4 | Sellindge NR | C4 | C | SELL4E | TSELL-1
HT | 30 | 2.9592 | 2.9592 | 2.9592 | T | SELL4 | Sellindge NR | C4 | C | SELL4F | TSELL-1
HT | 30 | 7.4525 | 5.5415 | 6.1445 | C,D,E,H,I,R,T,Z | SFEG1 | St Fergus Gas Terminal,St. Fergus Mobil | T2 | T | SFEG1Q | SFEGP
HT | 30 | 7.4525 | 5.5415 | 6.1445 | C,D,E,H,I,R,T,Z | SFEG1 | St Fergus Gas Terminal,St. Fergus Mobil | T2 | T | SFEG1R | SFEGP
HT | 30 | 2.38 | 0.78 | 1.424 | C,D,E,H,I,R,Z | SFIL1 | St Fillans | T4 | T | SFIL1Q | SFILP
HT | 30 | 91.281 | 29.554 | 44.214 | C,D,E,H,I,R,Z | SHEC3 | Sheffield City | P3 | P | SHEC31 | SHEC3
HT | 30 | 2.413 | 0.925 | 1.881 | C,D,E,H,I,R,Z | SHIN3 | Shin | T5 | T | SHIN3- | SHINP
HT | 30 | 107.145 | 50.627 | 126.616 | C,D,E,H,I,R,Z | SHRE1 | Shrewsbury | L5 | L | SHRE11 | SHRW1
HT | 30 | 32.2015 | 10.6775 | 15.8665 | C,D,E,H,I,R,Z | SHRU3 | Shrubhill | S6 | S | SHRU3A | SHRU
HT | 30 | 32.2015 | 10.6775 | 15.8665 | C,D,E,H,I,R,Z | SHRU3 | Shrubhill | S6 | S | SHRU3B | SHRU
HT | 30 | 96.3 | 38.14 | 57.744 | C,D,E,H,I,R,Z | SIGH3 | Sighthill | S6 | S | SIGH3A | SIGH
HT | 30 | 10.761 | 10.761 | 10.761 | T | SING4 | Singlewell NR | C2 | C | SING41 | TSINGL1
HT | 30 | 206.1303 | 90.2773 | 130.7703 | C,D,E,H,I,R,Z | SJOW1 | St John's Wood | A7 | A | SJOW11 | SJOW1
HT | 30 | 206.1303 | 90.2773 | 130.7703 | C,D,E,H,I,R,Z | SJOW1 | St John's Wood | A7 | A | SJOW12 | SJOW1
HT | 30 | 206.1303 | 90.2773 | 130.7703 | C,D,E,H,I,R,Z | SJOW1 | St John's Wood | A7 | A | SJOW13 | SJOW1
HT | 30 | 546.229 | 185.073 | 321.847 | C,D,E,H,I,R,Z | SKLG1 | Skelton Grange | P1 | P | SKLG11 | SKLGB1
HT | 30 | 0.26808 | 0.068308 | 0.13754 | C,D,E,H,I,R,Z | SLOY1 | Sloy | T3 | T | SLOY1A | SLOYP
HT | 30 | 0.26808 | 0.068308 | 0.13754 | C,D,E,H,I,R,Z | SLOY1 | Sloy | T3 | T | SLOY1B | SLOYP
HT | 30 | 0.26808 | 0.068308 | 0.13754 | C,D,E,H,I,R,Z | SLOY1 | Sloy | T3 | T | SLOY1C | SLOYP
HT | 30 | 0.26808 | 0.068308 | 0.13754 | C,D,E,H,I,R,Z | SLOY1 | Sloy | T3 | T | SLOY1D | SLOYP
HT | 30 | 0.26808 | 0.068308 | 0.13754 | C,D,E,H,I,R,Z | SLOY1 | Sloy | T3 | T | SLOY1E | SLOYP
HT | 30 | 0.26808 | 0.068308 | 0.13754 | C,D,E,H,I,R,Z | SLOY1 | Sloy | T3 | T | SLOY1F | SLOYP
HT | 30 | 0.26808 | 0.068308 | 0.13754 | C,D,E,H,I,R,Z | SLOY1 | Sloy | T3 | T | SLOY1J | SLOYP
HT | 30 | 0.26808 | 0.068308 | 0.13754 | C,D,E,H,I,R,Z | SLOY1 | Sloy | T3 | T | SLOY1K | SLOYP
HT | 30 | 0.26808 | 0.068308 | 0.13754 | C,D,E,H,I,R,Z | SLOY1 | Sloy | T3 | T | SLOY1L | SLOYP
HT | 30 | 0.26808 | 0.068308 | 0.13754 | C,D,E,H,I,R,Z | SLOY1 | Sloy | T3 | T | SLOY1M | SLOYP
HT | 30 | 0.26808 | 0.068308 | 0.13754 | C,D,E,H,I,R,Z | SLOY1 | Sloy | T3 | T | SLOY1N | SLOYP
HT | 30 | 0.26808 | 0.068308 | 0.13754 | C,D,E,H,I,R,Z | SLOY1 | Sloy | T3 | T | SLOY1P | SLOYP
HT | 30 | 0.26808 | 0.068308 | 0.13754 | C,D,E,H,I,R,Z | SLOY1 | Sloy | T3 | T | SLOY1T | SLOYP
HT | 30 | 181.892 | 70.9505 | 111.1555 | C,D,E,H,I,R,Z | SMAN1 | South Manchester | N2 | N | SMAN11 | SMAN1
HT | 30 | 181.892 | 70.9505 | 111.1555 | C,D,E,H,I,R,Z | SMAN1 | South Manchester | N2 | N | SMAN12 | SMAN1
HT | 30 | 26.271 | 14.603 | 22.139 | C,D,E,H,I,R,Z | SPAV3 | Spango Valley | S6 | S | SPAV3- | SPAV
HT | 30 | 277.631 | 63.873 | 148.742 | C,D,E,H,I,R,Z | SPEN1 | Spennymoor | Q7 | Q | SPEN11 | SPEN1
HT | 30 | 70.598 | 14.592 | 32.855 | C,D,E,H,I,R,Z | SSHI3 | South Shields | Q4 | Q | SSHI31 | SSHI3
HT | 30 | 158.606 | 23.536 | 85.318 | C,D,E,H,I,R,Z | STAH1 | Stanah | R4 | R | STAH11 | STAH1
HT | 30 | 366.811 | 147.437 | 236.553 | C,D,E,H,I,R,Z | STAL1 | Stalybridge | N7 | N | STAL11 | STAL1
HT | 30 | 0 | 0 | 0 | T | STAL2 | Stalybridge | N7 | N | STAL21 | TSTBRD-1
HT | 30 | 149.0175 | 48.771 | 119.388 | C,D,E,H,I,R,T,Z | STAY1 | Staythorpe,Staythorpe 132 (N_Rail) | K5 | K | STAY41 | BEXTRA80
HT | 30 | 149.0175 | 48.771 | 119.388 | C,D,E,H,I,R,T,Z | STAY1 | Staythorpe,Staythorpe 132 (N_Rail) | K5 | K | STAY4A | BEXTRA80
HT | 30 | 242.109 | 80.549 | 133.481 | C,D,E,H,I,R,Z | STEN1 | Stella North | Q5 | Q | STEN11 | STEN1
HT | 30 | 195.022 | 86.484 | 156 | C,D,E,H,I,R,Z | STES1 | Stella South | Q5 | Q | STES11 | STES1
HT | 30 | 28.305 | 11.2485 | 16.618 | C,D,E,H,I,R,Z | STHA3 | Strathaven | S6 | S | STHA3- | STHA
HT | 30 | 28.305 | 11.2485 | 16.618 | C,D,E,H,I,R,Z | STHA3 | Strathaven | S6 | S | STHA3V | STHA
HT | 30 | 48.462 | 31.164 | 46.229 | C,D,E,H,I,R,Z | STIR3 | Stirling | S5 | S | STIR3- | STIR
HT | 30 | 41.265 | 15.529 | 25.604 | C,D,E,H,I,R,Z | STLE3 | Strathleven | S5 | S | STLE3S | STLE
HT | 30 | 173.434 | 55.566 | 121.588 | C,D,E,H,I,R,Z | STOB1 | Stoke Bardolph | L7 | L | STOB11 | SBAR
HT | 30 | 16.968 | 5.925 | 8.98 | C,D,E,H,I,R,Z | STRI3 | Strichen | T2 | T | STRI3- | STRIP
HT | 30 | 633.287 | 177.51 | 382.672 | C,D,E,H,I,R,Z | SUND1 | Sundon | D4 | D | SUND11 | SUND1
HT | 30 | 0 | 0 | 0 | T | SUND4 | Sundon 1,Sundon 2 | D4 | D | SUND41 | TSNDND-1
HT | 30 | 0 | 0 | 0 | T | SUND4 | Sundon 1,Sundon 2 | D4 | D | SUND42 | TSNDND-1
HT | 30 | 317.902 | 86.1145 | 247.544 | C,D,E,H,I,R,Z | SWAN1 | Swansea North | H6 | H | SWAN11 | SWAN1
HT | 30 | 317.902 | 86.1145 | 247.544 | C,D,E,H,I,R,Z | SWAN1 | Swansea North | H6 | H | SWAN12 | SWAN1
HT | 30 | 22.101 | 3.88 | 8.789 | C,D,E,H,I,R,Z | TARL3 | Tarland | T2 | T | TARL3- | TARLP
HT | 30 | 184.383 | 49.457 | 100.177 | C,D,E,H,I,R,Z | TAUN1 | Taunton | E8 | E | TAUN11 | TAUN1
HT | 30 | 36.977 | 12.598 | 18.774 | C,D,E,H,I,R,Z | TAYN3 | Taynuilt | T3 | T | TAYN3- | TAYNP
HT | 30 | 5.128 | 5.128 | 5.128 | T |  | Dalreoch (Network Rail) | S5 | S |  | TDALRD-1
HT | 30 | 8.984 | 8.984 | 8.984 | T |  | Eglington Street (Network Rail) | S6 | S |  | TEGLSD-1
HT | 30 | 21.014 | 8.862 | 13.432 | C,D,E,H,I,R,Z | TELR3 | Telford Road | S6 | S | TELR3- | TELR
HT | 30 | 10.759 | 3.019 | 4.392 | C,D,E,H,I,R,Z | TEMP3 | Templeborough | P3 | P | TEMP31 | TEMP3
HT | 30 | 143.106 | 29.444 | 122.561 | C,D,E,H,I,R,Z | THOM6 | Thorpe Marsh | P6 | P | THOM61 | THOM6
HT | 30 | 223.243 | 62.439 | 125.016 | C,D,E,H,I,R,Z | THUR6 | Thurcroft | P3 | P | THUR61 | THUR6
HT | 30 | 37.752 | 20.551 | 29.35 | C,D,E,H,I,R,Z | THUS3 | Thurso | T5 | T | THUS3- | THSOP
HT | 30 | 56.9153 | 15.3175 | 32.4725 | C,D,E,H,I,R,Z | TILB1 | Tilbury | C1 | C | TILB11 | TILBB1
HT | 30 | 56.9153 | 15.3175 | 32.4725 | C,D,E,H,I,R,Z | TILB1 | Tilbury | C1 | C | TILB12 | TILBB1
HT | 30 | 56.9153 | 15.3175 | 32.4725 | C,D,E,H,I,R,Z | TILB1 | Tilbury | C1 | C | TILB13 | TILBB1
HT | 30 | 56.9153 | 15.3175 | 32.4725 | C,D,E,H,I,R,Z | TILB1 | Tilbury | C1 | C | TILB14 | TILBB1
HT | 30 | 21.242 | 21.242 | 21.242 | T | TINP3 | Tinsley Park Steelworks | P3 | P | TINP31 | TTINSD-1
HT | 30 | 21.242 | 21.242 | 21.242 | T | TINP3 | Tinsley Park Steelworks | P3 | P | TINP32 | TTINSD-1
HT | 30 | 18.647 | 18.647 | 18.647 | T |  | Long Buckby Wharf NR | L3 | L |  | TLONGB-RTK
HT | 30 | 2.735 | 2.735 | 2.735 | T | MARM1 | Marshall Meadows (Network Rail) | S6 | S |  | TMARMD-1
HT | 30 | 20.484 | 20.484 | 20.484 | T |  | Meadowhead (Caledonian Paper) | S6 | S |  | TMEADD-1
HT | 30 | 8.12 | 8.12 | 8.12 | T | TODP6 | BS Tod Point Supply | Q2 | Q | TODP61 | TTODSD-1
HT | 30 | 1.7694 | 0.649 | 1.2402 | C,D,E,H,I,R,Z | TONG | Tongland | S6 | S | TONG1- | TONG
HT | 30 | 1.7694 | 0.649 | 1.2402 | C,D,E,H,I,R,Z | TONG | Tongland | S6 | S | TONG1Q | TONG
HT | 30 | 1.7694 | 0.649 | 1.2402 | C,D,E,H,I,R,Z | TONG | Tongland | S6 | S | TONG1R | TONG
HT | 30 | 1.7694 | 0.649 | 1.2402 | C,D,E,H,I,R,Z | TONG | Tongland | S6 | S | TONG3- | TONG
HT | 30 | 1.7694 | 0.649 | 1.2402 | C,D,E,H,I,R,Z | TONG | Tongland | S6 | S | TONG5- | TONG
HT | 30 | 171.426 | 49.5025 | 92.865 | C,D,E,H,I,R,Z | TOTT1 | Tottenham | A1 | A | TOTT11 | TOTT1
HT | 30 | 171.426 | 49.5025 | 92.865 | C,D,E,H,I,R,Z | TOTT1 | Tottenham | A1 | A | TOTT12 | TOTT1
HT | 30 | 4.066 | 4.066 | 4.066 | T |  | Carntyne / Parkhead (Network Rail) | S6 | S |  | TPARHD-1
HT | 30 | 2.966 | 2.966 | 2.966 | T |  | Ravenscraig B (BSC) | S6 | S |  | TRAVED-1
HT | 30 | 114.423 | 63.81 | 132.199 | C,D,E,H,I,R,Z | TRAW1 | Trawsfynydd | M7 | M | TRAW11 | TRAW1
HT | 30 | 66.116 | 66.116 | 66.116 | T | TREM2 | ASW Tremorfa | H2 | H | TREM21 | TKYELT003
HT | 30 | 25 | 25 | 25 | T |  | St Fergus Compressor | T2 | T |  | TSFGSD-1
HT | 30 | 21 | 21 | 21 | T |  | St Fergus Compressor | T2 | T |  | TSFGSD-2
HT | 30 | 7.8135 | 2.861 | 5.292 | C,D,E,H,I,R,Z | TUMB | Tummel Bridge | T4 | T | TUMB1Q | TUMBP
HT | 30 | 7.8135 | 2.861 | 5.292 | C,D,E,H,I,R,Z | TUMB | Tummel Bridge | T4 | T | TUMB1R | TUMBP
HT | 30 | 25 | 25 | 25 | T |  | MOD Harestanes Whistlefield | S5 | S |  | TWHISTLD-1
HT | 30 | 212.215 | 59.307 | 118.061 | C,D,E,H,I,R,Z | TYNE1 | Tynemouth 1,Tynemouth 2 | Q4 | Q | TYNE11 | TYNE1
HT | 30 | 271.873 | 90.202 | 202.647 | C,D,E,H,I,R,Z | UPPB1 | Upper Boat 132kV,Upper Boat 33kV | H2 | H | UPPB11 | UPPB1
HT | 30 | 44 | 44 | 44 | T | UPPB2 | Upper Boat 275 (Rail) | H2 | H | UPPB21 | BEXTRA79
HT | 30 | 44 | 44 | 44 | T | UPPB2 | Upper Boat 275 (Rail) | H2 | H | UPPB22 | BEXTRA79
HT | 30 | 127.201 | 65.0395 | 129.443 | C,D,E,H,I,R,T,Z | USKM1 | Llanwern Steelworks,Uskmouth | H2 | H | USKM11 | TLLWSD-1
HT | 30 | 127.201 | 65.0395 | 129.443 | C,D,E,H,I,R,T,Z | USKM1 | Llanwern Steelworks,Uskmouth | H2 | H | USKM12 | TLLWSD-1
HT | 30 | 35.738 | 118.144 | 71.718 | C,D,E,H,I,R,Z | MIDD4 | Walney 2 | R4 | R |  | WABO
HT | 30 | 425.59 | 160.901 | 257.395 | C,D,E,H,I,R,Z | WALH1 | Walham | G1 | G | WALH41 | WALH1
HT | 30 | 756.841 | 225.004 | 560.701 | C,D,E,H,I,R,Z | WALP1 | Walpole (_A),Walpole (_B) | J1 | J | WALP11 | WALP1
HT | 30 | 100 | 100 | 100 | T | WALX2 | Waltham Cross 275 (Data_centre) | A3 | A | WALX2A | BEXTRA64
HT | 30 | 284.583 | 74.639 | 146.783 | C,D,E,H,I,R,Z | WARL1 | Warley | C6 | C | WARL11 | WARL1
HT | 30 | 75.692 | 32.8835 | 46.0345 | C,D,E,H,I,R,Z | WASF1 | Washway Farm | N1 | N | WASF1A | WASF1
HT | 30 | 75.692 | 32.8835 | 46.0345 | C,D,E,H,I,R,Z | WASF1 | Washway Farm | N1 | N | WASF1B | WASF1
HT | 30 | 131.869 | 52.439 | 93.645 | C,D,E,H,I,R,Z | WATS1 | Watford South | A6 | A | WATS11 | WATFS1
HT | 30 | 131.869 | 52.439 | 93.645 | C,D,E,H,I,R,Z | WATS1 | Watford South | A6 | A | WATS12 | WATFS1
HT | 30 | 62.5 | 62.5 | 62.5 | T | WATS2 | Ickenham (new) (Rail) | D4 | D | WATS21 | BEXTRA75
HT | 30 | 62.5 | 62.5 | 62.5 | T | WATS2 | Ickenham (new) (Rail) | D4 | D | WATS22 | BEXTRA75
HT | 30 | 221.357 | 73.265 | 135.132 | C,D,E,H,I,R,Z | WBOL6 | West Boldon | Q4 | Q | WBOL61 | WBOL6
HT | 30 | 117.7335 | 29.7525 | 56.101 | C,D,E,H,I,R,Z | WBUR1 | West Burton | K6 | K | WBUR11 | WBUR1
HT | 30 | 117.7335 | 29.7525 | 56.101 | C,D,E,H,I,R,Z | WBUR1 | West Burton | K6 | K | WBUR12 | WBUR1
HT | 30 | 5.3563 | 2.207 | 3.4855 | C,D,E,H,I,R,Z | WFIE | Westfield | S5 | S | WFIE1A | WFIE
HT | 30 | 5.3563 | 2.207 | 3.4855 | C,D,E,H,I,R,Z | WFIE | Westfield | S5 | S | WFIE1B | WFIE
HT | 30 | 5.3563 | 2.207 | 3.4855 | C,D,E,H,I,R,Z | WFIE | Westfield | S5 | S | WFIE2- | WFIE
HT | 30 | 5.3563 | 2.207 | 3.4855 | C,D,E,H,I,R,Z | WFIE | Westfield | S5 | S | WFIE3- | WFIE
HT | 30 | 20.6237 | 7.335 | 10.8253 | C,D,E,H,I,R,Z | WGEO | West George Street | S5 | S | WGEO2Q | WGEO
HT | 30 | 20.6237 | 7.335 | 10.8253 | C,D,E,H,I,R,Z | WGEO | West George Street | S5 | S | WGEO2R | WGEO
HT | 30 | 20.6237 | 7.335 | 10.8253 | C,D,E,H,I,R,Z | WGEO | West George Street | S5 | S | WGEO3- | WGEO
HT | 30 | 210.194 | 108.463 | 152.149 | C,D,E,H,I,R,Z | WHAM1 | West Ham | A1 | A | WHAM11 | WHAM1
HT | 30 | 210.194 | 108.463 | 152.149 | C,D,E,H,I,R,Z | WHAM1 | West Ham | A1 | A | WHAM12 | WHAM1
HT | 30 | 281.142 | 99.959 | 180.478 | C,D,E,H,I,R,Z | WHGA1 | Whitegate | N4 | N | WHGA11 | WHGA1
HT | 30 | 20.817 | 6.8173 | 10.2123 | C,D,E,H,I,R,Z | WHHO | Whitehouse | S6 | S | WHHO2Q | WHHO
HT | 30 | 20.817 | 6.8173 | 10.2123 | C,D,E,H,I,R,Z | WHHO | Whitehouse | S6 | S | WHHO2R | WHHO
HT | 30 | 20.817 | 6.8173 | 10.2123 | C,D,E,H,I,R,Z | WHHO | Whitehouse | S6 | S | WHHO3- | WHHO
HT | 30 | 21.011 | 7.17 | 7.395 | C,D,E,H,I,R,Z | WIBA3 | Wincobank | P3 | P | WIBA31 | WIBA3
HT | 30 | 170.512 | 44.708 | 87.182 | C,D,E,H,I,R,Z | WIEN1 | Willenhall | L2 | L | WIEN11 | WIEN1
HT | 30 | 239.3575 | 103.064 | 172.926 | C,D,E,H,I,R,Z | WILL1 | Willington | L5 | L | WILL11 | WILL1
HT | 30 | 239.3575 | 103.064 | 172.926 | C,D,E,H,I,R,Z | WILL1 | Willington | L5 | L | WILL12 | WILL1
HT | 30 | 0.575 | 0.575 | 0.575 | T | WILT2 | ETOL - Wilton Site | Q2 | Q | WILT2A | TWILCT-1
HT | 30 | 0.575 | 0.575 | 0.575 | T | WILT2 | ETOL - Wilton Site | Q2 | Q | WILT2B | TWILCT-1
HT | 30 | 0.575 | 0.575 | 0.575 | T | WILT2 | ETOL - Wilton Site | Q2 | Q | WILT2C | TWILCT-1
HT | 30 | 0.575 | 0.575 | 0.575 | T | WILT2 | ETOL - Wilton Site | Q2 | Q | WILT2D | TWILCT-1
HT | 30 | 660.618 | 232.316 | 398.28 | C,D,E,H,I,R,Z | WIMB1 | Wimbledon North,Wimbledon South | A4 | A | WIMB11 | WIMBN1
HT | 30 | 7.4805 | 2.5663 | 3.5957 | C,D,E,H,I,R,Z | WIOW | Willowdale | T2 | T | WIOW1- | WIOWP
HT | 30 | 7.4805 | 2.5663 | 3.5957 | C,D,E,H,I,R,Z | WIOW | Willowdale | T2 | T | WIOW1Q | WIOWP
HT | 30 | 7.4805 | 2.5663 | 3.5957 | C,D,E,H,I,R,Z | WIOW | Willowdale | T2 | T | WIOW1R | WIOWP
HT | 30 | 7.4805 | 2.5663 | 3.5957 | C,D,E,H,I,R,Z | WIOW | Willowdale | T2 | T | WIOW3- | WIOWP
HT | 30 | 330.577 | 121.608 | 187.039 | C,D,E,H,I,R,Z | WISD1 | Wesley Avenue (Willesden),Willesden 132kV,Willesden 66kV | A7 | A | WISD11 | WESAH
HT | 30 | 175.04 | 81.865 | 118.441 | C,D,E,H,I,R,T,Z | WISD6 | Acton Lane 22kV,Acton Lane 66kV,Canal Bank,Greenford,LU Acton Lane Supply,Perivale | A7 | A | WISD61 | ACTL2
HT | 30 | 9.1767 | 2.8919 | 4.3471 | C,D,E,H,I,R,Z | WISH | Wishaw | S6 | S | WISH1- | WISH
HT | 30 | 17.1297 | 10.8449 | 12.3001 | C,D,E,H,I,R,T,Z | WISH,WISH2 | Gowkthrapple (Network Rail),Wishaw | S6 | S | WISH2- | TGOWKD-1
HT | 30 | 9.1767 | 2.8919 | 4.3471 | C,D,E,H,I,R,Z | WISH | Wishaw | S6 | S | WISH3- | WISH
HT | 30 | 9.1767 | 2.8919 | 4.3471 | C,D,E,H,I,R,Z | WISH | Wishaw | S6 | S | WISH3S | WISH
HT | 30 | 9.1767 | 2.8919 | 4.3471 | C,D,E,H,I,R,Z | WISH | Wishaw | S6 | S | WISH3T | WISH
HT | 30 | 9.1767 | 2.8919 | 4.3471 | C,D,E,H,I,R,Z | WISH | Wishaw | S6 | S | WISH3W | WISH
HT | 30 | 9.1767 | 2.8919 | 4.3471 | C,D,E,H,I,R,Z | WISH | Wishaw | S6 | S | WISH4- | WISH
HT | 30 | 295.8065 | 105.2545 | 173.908 | C,D,E,H,I,R,Z | WMEL1 | West Melton | P3 | P | WMEL11 | WMEL1
HT | 30 | 295.8065 | 105.2545 | 173.908 | C,D,E,H,I,R,Z | WMEL1 | West Melton | P3 | P | WMEL12 | WMEL1
HT | 30 | 12.3563 | 4.438 | 6.43 | C,D,E,H,I,R,Z | WOHI | Woodhill | T2 | T | WOHI1Q | WOHIP
HT | 30 | 12.3563 | 4.438 | 6.43 | C,D,E,H,I,R,Z | WOHI | Woodhill | T2 | T | WOHI1R | WOHIP
HT | 30 | 12.3563 | 4.438 | 6.43 | C,D,E,H,I,R,Z | WOHI | Woodhill | T2 | T | WOHI3- | WOHIP
HT | 30 | 64.005 | 31.997 | 38.954 | C,D,E,H,I,R,Z | WTHU3 | West Thurrock | A1 | A | WTHU31 | WTHU31
HT | 30 | 193.28 | 66.7495 | 123.302 | C,D,E,H,I,R,Z | WWEY1 | West Weybridge | A8 | A | WWEY11 | WWEY1
HT | 30 | 193.28 | 66.7495 | 123.302 | C,D,E,H,I,R,Z | WWEY1 | West Weybridge | A8 | A | WWEY12 | WWEY1
HT | 30 | 53.682 | 15.563 | 47.857 | C,D,E,H,I,R,T,Z | WYLF1 | Anglesey Aluminium Demand,Wylfa | M8 | M | WYLF11 | TANGLD-1
HT | 30 | 256.85 | 83.865 | 121.225 | C,D,E,H,I,R,Z | WYMO1 | Wymondley | D5 | D | WYMO11 | WYMOM1
HT | 30 | 24.244 | 24.244 | 24.244 | T | WYMO4 | Correy's Mill NR,Wymondley 400 (N_Rail) | D5 | D | WYMO41 | BEXTRA81
HT | 30 | 210 | 210 | 210 |  |  | Prosperity Parc, Anglesey (Manual Addition) |  |  | WYLF11 | Wylfa 132kV
HT | 30 | 1800 | 1800 | 1800 |  |  | New West London Data Centres (Manual Addition) |  |  | UXBR41 | Uxbridge Moor 400kV (New)
HT | 30 | 300 | 300 | 300 |  |  | Microsoft Data Centres (Manual Addition) |  |  | EGGB41 | Eggborough 400kV
HT | 30 | 300 | 300 | 300 |  |  | Capenhurst_TractDataCentre (Manual Addition) |  |  | CAPE21 | Capenhurst
HT | 30 | 300 | 300 | 300 |  |  | Daines_TractDataCentre (Manual Addition) |  |  | DAIN41 | Daines
HT | 30 | 300 | 300 | 300 |  |  | Frodsham_TractDataCentre (Manual Addition) |  |  | FROD41 | Frodsham
HT | 30 | 300 | 300 | 300 |  |  | EatonSocon_TractDataCentre (Manual Addition) |  |  | EASO41 | Eaton Socon
HT | 30 | 300 | 300 | 300 |  |  | Pelham_TractDataCentre (Manual Addition) |  |  | PELH41 | Pelham
HT | 30 | 300 | 300 | 300 |  |  | Sundon_TractDataCentre (Manual Addition) |  |  | SUND41 | Sundon
HT | 30 | 300 | 300 | 300 |  |  | Brinsworth_TractDataCentre (Manual Addition) |  |  | BRIN41 | Brinsworth
HT | 30 | 300 | 300 | 300 |  |  | Eggborough_TractDataCentre (Manual Addition) |  |  | EGGB41 | Eggborough
HT | 30 | 300 | 300 | 300 |  |  | Thornton_TractDataCentre (Manual Addition) |  |  | THTO41 | Thornton

## Intra_HVDC
Interconnector Name | Existing | Planned from year | Node 1 | Node 2 | Type | Rated Voltage (kV) | Length(km) | Metallic Return | Winter Rating (MVA) | Spring Rating (MVA) | Summer Rating (MVA) | Autumn Rating (MVA) | Node 1 MVAr Gen | Node 1 MVAr Abs | Node 2 MVAr Gen | Node 2 MVAr Abs | Year | Status
Caithness Moray Shetland Multi-Terminal Link - Terminal 1 | Yes | Existing | SPIT2K | Central DC Substation | VSC | ±320 | 31 | No | 800 | 800 | 800 | 800 | 263 | 263 |  |  |  | Existing
Caithness Moray Shetland Multi-Terminal Link - Terminal 2 | Yes | Existing | BLHI4R | Central DC Substation | VSC | ±320 | 136 | No | 1200 | 1200 | 1200 | 1200 | 394 | 394 |  |  |  | Existing
PSDC HVDC Link | No | 2030 | BANN4R | LOSD4R | VSC | ±525 | 145 | Yes | 2000 | 2000 | 2000 | 2000 | 657 | 657 | 657 | 657 | 2030 | Addition
Western Isles HVDC Link | No | 2030 | LEWI4R | FNLN4R | VSC | ±525 | 170 | No | 1800 | 1800 | 1800 | 1800 | 592 | 592 | 592 | 592 | 2030 | Addition
Caithness Moray Shetland Multi-Terminal Link - Terminal 3 | Yes | Existing | KERG1J | Central DC Substation | VSC | ±320 | 269 | No | 600 | 600 | 600 | 600 | 197 | 197 |  |  |  | Existing
Western HVDC Link | Yes | Existing | FLIB41 | HUCS4- | LCC | ±600 | 422 | No | 2250 | 2250 | 2250 | 2250 | 1712 | 705 | 688 | 1946 |  | Existing
Eastern Green Link 2 | No | 2029 | DRAX41 | PEHE4- | VSC | ±525 | 505 | No | 2000 | 2000 | 2000 | 2000 | 657 | 657 | 657 | 657 | 2029 | Addition
Eastern HVDC Link 1 | No | 2029 | BRNX4A | HAWP41 | VSC | ±525 | 193 | No | 2000 | 2000 | 2000 | 2000 | 660 | 660 | 657 | 657 | 2029 | Addition